## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1010-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1010-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1010-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1010-4_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1010-4_0_2_node_31 | 0.4 | n |  | TRUE
5 | bus_LV_1010-4_0_2_node_20 | 0.4 | n |  | TRUE
6 | bus_LV_1010-4_0_2_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_1010-4_0_2_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_1010-4_0_2_node_41 | 0.4 | n |  | TRUE
9 | bus_LV_1010-4_0_2_node_42 | 0.4 | n |  | TRUE
10 | bus_LV_1010-4_0_2_node_45 | 0.4 | n |  | TRUE
11 | bus_LV_1010-4_0_2_node_46 | 0.4 | n |  | TRUE
12 | bus_LV_1010-4_0_2_node_56 | 0.4 | n |  | TRUE
13 | bus_LV_1010-4_0_2_node_102 | 0.4 | n |  | TRUE
14 | bus_LV_1010-4_0_2_node_47 | 0.4 | n |  | TRUE
15 | bus_LV_1010-4_0_2_node_48 | 0.4 | n |  | TRUE
16 | bus_LV_1010-4_0_2_node_49 | 0.4 | n |  | TRUE
17 | bus_LV_1010-4_0_2_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_1010-4_0_2_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_1010-4_0_2_node_53 | 0.4 | n |  | TRUE
20 | bus_LV_1010-4_0_2_node_86 | 0.4 | n |  | TRUE
21 | bus_LV_1010-4_0_2_node_52 | 0.4 | n |  | TRUE
22 | bus_LV_1010-4_0_2_node_63 | 0.4 | n |  | TRUE
23 | bus_LV_1010-4_0_2_node_59 | 0.4 | n |  | TRUE
24 | bus_LV_1010-4_0_2_node_326 | 0.4 | n |  | TRUE
25 | bus_LV_1010-4_0_2_node_54 | 0.4 | n |  | TRUE
26 | bus_LV_1010-4_0_2_node_101 | 0.4 | n |  | TRUE
27 | bus_LV_1010-4_0_2_node_88 | 0.4 | n |  | TRUE
28 | bus_LV_1010-4_0_2_node_55 | 0.4 | n |  | TRUE
29 | bus_LV_1010-4_0_2_node_85 | 0.4 | n |  | TRUE
30 | bus_LV_1010-4_0_2_node_57 | 0.4 | n |  | TRUE
31 | bus_LV_1010-4_0_2_node_100 | 0.4 | n |  | TRUE
32 | bus_LV_1010-4_0_2_node_58 | 0.4 | n |  | TRUE
33 | bus_LV_1010-4_0_2_node_60 | 0.4 | n |  | TRUE
34 | bus_LV_1010-4_0_2_node_61 | 0.4 | n |  | TRUE
35 | bus_LV_1010-4_0_2_node_62 | 0.4 | n |  | TRUE
36 | bus_LV_1010-4_0_2_node_321 | 0.4 | n |  | TRUE
37 | bus_LV_1010-4_0_2_node_440 | 0.4 | n |  | TRUE
38 | bus_LV_1010-4_0_2_node_258 | 0.4 | n |  | TRUE
39 | bus_LV_1010-4_0_2_node_325 | 0.4 | n |  | TRUE
40 | bus_LV_1010-4_0_2_node_64 | 0.4 | n |  | TRUE
41 | bus_LV_1010-4_0_2_node_65 | 0.4 | n |  | TRUE
42 | bus_LV_1010-4_0_2_node_66 | 0.4 | n |  | TRUE
43 | bus_LV_1010-4_0_2_node_83 | 0.4 | n |  | TRUE
44 | bus_LV_1010-4_0_2_node_212 | 0.4 | n |  | TRUE
45 | bus_LV_1010-4_0_2_node_84 | 0.4 | n |  | TRUE
46 | bus_LV_1010-4_0_2_node_87 | 0.4 | n |  | TRUE
47 | bus_LV_1010-4_0_2_node_304 | 0.4 | n |  | TRUE
48 | bus_LV_1010-4_0_2_node_147 | 0.4 | n |  | TRUE
49 | bus_LV_1010-4_0_2_node_148 | 0.4 | n |  | TRUE
50 | bus_LV_1010-4_0_2_node_149 | 0.4 | n |  | TRUE
51 | bus_LV_1010-4_0_2_node_150 | 0.4 | n |  | TRUE
52 | bus_LV_1010-4_0_2_node_151 | 0.4 | n |  | TRUE
53 | bus_LV_1010-4_0_2_node_152 | 0.4 | n |  | TRUE
54 | bus_LV_1010-4_0_2_node_153 | 0.4 | n |  | TRUE
55 | bus_LV_1010-4_0_2_node_154 | 0.4 | n |  | TRUE
56 | bus_LV_1010-4_0_2_node_155 | 0.4 | n |  | TRUE
57 | bus_LV_1010-4_0_2_node_232 | 0.4 | n |  | TRUE
58 | bus_LV_1010-4_0_2_node_266 | 0.4 | n |  | TRUE
59 | bus_LV_1010-4_0_2_node_281 | 0.4 | n |  | TRUE
60 | bus_LV_1010-4_0_2_node_280 | 0.4 | n |  | TRUE
61 | bus_LV_1010-4_0_2_node_175 | 0.4 | n |  | TRUE
62 | bus_LV_1010-4_0_2_node_176 | 0.4 | n |  | TRUE
63 | bus_LV_1010-4_0_2_node_177 | 0.4 | n |  | TRUE
64 | bus_LV_1010-4_0_2_node_178 | 0.4 | n |  | TRUE
65 | bus_LV_1010-4_0_2_node_330 | 0.4 | n |  | TRUE
66 | bus_LV_1010-4_0_2_node_331 | 0.4 | n |  | TRUE
67 | bus_LV_1010-4_0_2_node_246 | 0.4 | n |  | TRUE
68 | bus_LV_1010-4_0_2_node_179 | 0.4 | n |  | TRUE
69 | bus_LV_1010-4_0_2_node_298 | 0.4 | n |  | TRUE
70 | bus_LV_1010-4_0_2_node_249 | 0.4 | n |  | TRUE
71 | bus_LV_1010-4_0_2_node_297 | 0.4 | n |  | TRUE
72 | bus_LV_1010-4_0_2_node_186 | 0.4 | n |  | TRUE
73 | bus_LV_1010-4_0_2_node_254 | 0.4 | n |  | TRUE
74 | bus_LV_1010-4_0_2_node_278 | 0.4 | n |  | TRUE
75 | bus_LV_1010-4_0_2_node_214 | 0.4 | n |  | TRUE
76 | bus_LV_1010-4_0_2_node_308 | 0.4 | n |  | TRUE
77 | bus_LV_1010-4_0_2_node_245 | 0.4 | n |  | TRUE
78 | bus_LV_1010-4_0_2_node_310 | 0.4 | n |  | TRUE
79 | bus_LV_1010-4_0_2_node_247 | 0.4 | n |  | TRUE
80 | bus_LV_1010-4_0_2_node_248 | 0.4 | n |  | TRUE
81 | bus_LV_1010-4_0_2_node_251 | 0.4 | n |  | TRUE
82 | bus_LV_1010-4_0_2_node_252 | 0.4 | n |  | TRUE
83 | bus_LV_1010-4_0_2_node_253 | 0.4 | n |  | TRUE
84 | bus_LV_1010-4_0_2_node_255 | 0.4 | n |  | TRUE
85 | bus_LV_1010-4_0_2_node_256 | 0.4 | n |  | TRUE
86 | bus_LV_1010-4_0_2_node_257 | 0.4 | n |  | TRUE
87 | bus_LV_1010-4_0_2_node_259 | 0.4 | n |  | TRUE
88 | bus_LV_1010-4_0_2_node_327 | 0.4 | n |  | TRUE
89 | bus_LV_1010-4_0_2_node_324 | 0.4 | n |  | TRUE
90 | bus_LV_1010-4_0_2_node_261 | 0.4 | n |  | TRUE
91 | bus_LV_1010-4_0_2_node_262 | 0.4 | n |  | TRUE
92 | bus_LV_1010-4_0_2_node_263 | 0.4 | n |  | TRUE
93 | bus_LV_1010-4_0_2_node_264 | 0.4 | n |  | TRUE
94 | bus_LV_1010-4_0_2_node_301 | 0.4 | n |  | TRUE
95 | bus_LV_1010-4_0_2_node_265 | 0.4 | n |  | TRUE
96 | bus_LV_1010-4_0_2_node_267 | 0.4 | n |  | TRUE
97 | bus_LV_1010-4_0_2_node_268 | 0.4 | n |  | TRUE
98 | bus_LV_1010-4_0_2_node_273 | 0.4 | n |  | TRUE
99 | bus_LV_1010-4_0_2_node_275 | 0.4 | n |  | TRUE
100 | bus_LV_1010-4_0_2_node_411 | 0.4 | n |  | TRUE
101 | bus_LV_1010-4_0_2_node_410 | 0.4 | n |  | TRUE
102 | bus_LV_1010-4_0_2_node_279 | 0.4 | n |  | TRUE
103 | bus_LV_1010-4_0_2_node_299 | 0.4 | n |  | TRUE
104 | bus_LV_1010-4_0_2_node_300 | 0.4 | n |  | TRUE
105 | bus_LV_1010-4_0_2_node_302 | 0.4 | n |  | TRUE
106 | bus_LV_1010-4_0_2_node_433 | 0.4 | n |  | TRUE
107 | bus_LV_1010-4_0_2_node_303 | 0.4 | n |  | TRUE
108 | bus_LV_1010-4_0_2_node_305 | 0.4 | n |  | TRUE
109 | bus_LV_1010-4_0_2_node_306 | 0.4 | n |  | TRUE
110 | bus_LV_1010-4_0_2_node_307 | 0.4 | n |  | TRUE
111 | bus_LV_1010-4_0_2_node_320 | 0.4 | n |  | TRUE
112 | bus_LV_1010-4_0_2_node_322 | 0.4 | n |  | TRUE
113 | bus_LV_1010-4_0_2_node_323 | 0.4 | n |  | TRUE
114 | bus_LV_1010-4_0_2_node_328 | 0.4 | n |  | TRUE
115 | bus_LV_1010-4_0_2_node_346 | 0.4 | n |  | TRUE
116 | bus_LV_1010-4_0_2_node_345 | 0.4 | n |  | TRUE
117 | bus_LV_1010-4_0_2_node_409 | 0.4 | n |  | TRUE
118 | bus_LV_1010-4_0_2_node_412 | 0.4 | n |  | TRUE
119 | bus_LV_1010-4_0_2_node_439 | 0.4 | n |  | TRUE
120 | bus_LV_1010-4_0_2_node_432 | 0.4 | n |  | TRUE
121 | bus_MV_0_node_245 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1010-4_0_2_load_0 | 0 | 0.00013313 | 3.3365e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1010-4_0_2_load_1 | 1 | 3.774e-05 | 9.4585e-06 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1010-4_0_2_load_4 | 3 | 4.6795e-05 | 1.1728e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1010-4_0_2_load_20 | 5 | 8.4508e-05 | 2.118e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1010-4_0_2_load_41 | 8 | 0.00010125 | 2.5377e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1010-4_0_2_load_42 | 9 | 0.00031855 | 7.9835e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1010-4_0_2_load_46 | 11 | 0.00015681 | 3.9301e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1010-4_0_2_load_56 | 12 | 0.00013293 | 3.3315e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1010-4_0_2_load_47 | 14 | 4.9579e-05 | 1.2426e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1010-4_0_2_load_48 | 15 | 0.00022824 | 5.7203e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1010-4_0_2_load_49 | 16 | 7.712e-05 | 1.9328e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1010-4_0_2_load_51 | 18 | 0.0001494 | 3.7443e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1010-4_0_2_load_86 | 20 | 4.9448e-05 | 1.2393e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1010-4_0_2_load_59 | 23 | 0.0002159 | 5.4109e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1010-4_0_2_load_326 | 24 | 0.0004074 | 0.0001021 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1010-4_0_2_load_101 | 26 | 0.00022742 | 5.6996e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1010-4_0_2_load_55 | 28 | 3.9807e-05 | 9.9766e-06 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1010-4_0_2_load_85 | 29 | 0.00027008 | 6.7688e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1010-4_0_2_load_100 | 31 | 9.5607e-05 | 2.3961e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1010-4_0_2_load_58 | 32 | 5.4763e-05 | 1.3725e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1010-4_0_2_load_60 | 33 | 0.00016063 | 4.0258e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1010-4_0_2_load_321 | 36 | 0.00027925 | 6.9988e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1010-4_0_2_load_440 | 37 | 0.00046593 | 0.00011677 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1010-4_0_2_load_325 | 39 | 0.00015916 | 3.9889e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1010-4_0_2_load_64 | 40 | 0.00010565 | 2.6477e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1010-4_0_2_load_65 | 41 | 0.00010977 | 2.751e-05 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1010-4_0_2_load_66 | 42 | 0.0001146 | 2.872e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1010-4_0_2_load_212 | 44 | 0.00034816 | 8.7256e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1010-4_0_2_load_84 | 45 | 6.4019e-05 | 1.6045e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1010-4_0_2_load_87 | 46 | 0.00023382 | 5.8601e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1010-4_0_2_load_147 | 48 | 0.00035537 | 8.9064e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1010-4_0_2_load_148 | 49 | 0.00015306 | 3.8359e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1010-4_0_2_load_150 | 51 | 9.3825e-05 | 2.3515e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1010-4_0_2_load_151 | 52 | 0.00024743 | 6.2011e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1010-4_0_2_load_152 | 53 | 0.00034396 | 8.6204e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1010-4_0_2_load_153 | 54 | 0.00077849 | 0.00019511 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1010-4_0_2_load_154 | 55 | 0.00049113 | 0.00012309 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1010-4_0_2_load_232 | 57 | 0.00014549 | 3.6462e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1010-4_0_2_load_266 | 58 | 9.1078e-05 | 2.2826e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1010-4_0_2_load_175 | 61 | 0.00017753 | 4.4494e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1010-4_0_2_load_331 | 66 | 0.00025244 | 6.3268e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1010-4_0_2_load_246 | 67 | 0.00029332 | 7.3512e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1010-4_0_2_load_298 | 69 | 0.00034487 | 8.6432e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1010-4_0_2_load_297 | 71 | 5.8547e-05 | 1.4673e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1010-4_0_2_load_278 | 74 | 0.00051847 | 0.00012994 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1010-4_0_2_load_214 | 75 | 0.00028556 | 7.1568e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1010-4_0_2_load_308 | 76 | 0.00011866 | 2.9739e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1010-4_0_2_load_245 | 77 | 0.00030056 | 7.5327e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1010-4_0_2_load_310 | 78 | 0.00032142 | 8.0554e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1010-4_0_2_load_247 | 79 | 4.9915e-05 | 1.251e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1010-4_0_2_load_248 | 80 | 0.00039412 | 9.8777e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1010-4_0_2_load_251 | 81 | 0.00025498 | 6.3903e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1010-4_0_2_load_252 | 82 | 8.7855e-05 | 2.2018e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1010-4_0_2_load_253 | 83 | 0.00027899 | 6.9922e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1010-4_0_2_load_256 | 85 | 0.00065029 | 0.00016298 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1010-4_0_2_load_257 | 86 | 0.00022521 | 5.6444e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1010-4_0_2_load_327 | 88 | 5.6958e-05 | 1.4275e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1010-4_0_2_load_324 | 89 | 0.00010848 | 2.7187e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1010-4_0_2_load_261 | 90 | 0.0001003 | 2.5138e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1010-4_0_2_load_262 | 91 | 0.00010106 | 2.5327e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1010-4_0_2_load_263 | 92 | 0.0002064 | 5.1729e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1010-4_0_2_load_264 | 93 | 0.00036577 | 9.1671e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1010-4_0_2_load_301 | 94 | 9.5531e-05 | 2.3942e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1010-4_0_2_load_265 | 95 | 0.00018615 | 4.6654e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1010-4_0_2_load_267 | 96 | 3.1411e-05 | 7.8722e-06 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1010-4_0_2_load_268 | 97 | 0.0003171 | 7.9473e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1010-4_0_2_load_273 | 98 | 0.00040642 | 0.00010186 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1010-4_0_2_load_411 | 100 | 0.00071889 | 0.00018017 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1010-4_0_2_load_410 | 101 | 0.00017274 | 4.3292e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1010-4_0_2_load_279 | 102 | 0.00026535 | 6.6502e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1010-4_0_2_load_299 | 103 | 0.00011407 | 2.8588e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1010-4_0_2_load_300 | 104 | 0.00010029 | 2.5135e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1010-4_0_2_load_302 | 105 | 8.3582e-05 | 2.0947e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1010-4_0_2_load_433 | 106 | 8.3834e-05 | 2.1011e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1010-4_0_2_load_303 | 107 | 0.00012121 | 3.0379e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1010-4_0_2_load_306 | 109 | 5.4531e-05 | 1.3667e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1010-4_0_2_load_307 | 110 | 8.3206e-05 | 2.0854e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1010-4_0_2_load_320 | 111 | 0.00012689 | 3.1803e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1010-4_0_2_load_322 | 112 | 0.00010814 | 2.7103e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1010-4_0_2_load_323 | 113 | 7.8016e-05 | 1.9553e-05 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1010-4_0_2_load_328 | 114 | 0.00032297 | 8.0944e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1010-4_0_2_load_346 | 115 | 4.4412e-05 | 1.1131e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1010-4_0_2_load_345 | 116 | 0.00040561 | 0.00010166 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1010-4_0_2_load_409 | 117 | 0.00022391 | 5.6117e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1010-4_0_2_load_412 | 118 | 0.00018308 | 4.5883e-05 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1010-4_0_2_load_439 | 119 | 6.2266e-05 | 1.5605e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1010-4_0_2_load_432 | 120 | 3.8774e-05 | 9.7176e-06 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 77 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1010-4_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.16445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1010-4_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.026546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1010-4_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.26343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1010-4_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.18575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1010-4_0_2_line_4 | NAYY 4x150 SE | 4 | 6 | 0.45203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1010-4_0_2_line_5 | NAYY 4x150 SE | 4 | 7 | 0.55429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1010-4_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.38075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1010-4_0_2_line_7 | NAYY 4x150 SE | 6 | 9 | 0.062808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1010-4_0_2_line_8 | NAYY 4x150 SE | 7 | 10 | 0.14814 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1010-4_0_2_line_9 | NAYY 4x150 SE | 7 | 11 | 0.24986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1010-4_0_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.042266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1010-4_0_2_line_11 | NAYY 4x150 SE | 10 | 12 | 0.038501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1010-4_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.016137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1010-4_0_2_line_13 | NAYY 4x150 SE | 12 | 28 | 0.15992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1010-4_0_2_line_14 | NAYY 4x150 SE | 13 | 40 | 0.12582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1010-4_0_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.029146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1010-4_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0057056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1010-4_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.079637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1010-4_0_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.11671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1010-4_0_2_line_19 | NAYY 4x150 SE | 17 | 19 | 0.12492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1010-4_0_2_line_20 | NAYY 4x150 SE | 18 | 20 | 0.025102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1010-4_0_2_line_21 | NAYY 4x150 SE | 19 | 24 | 0.017598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1010-4_0_2_line_22 | NAYY 4x150 SE | 19 | 22 | 0.04876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1010-4_0_2_line_23 | NAYY 4x150 SE | 20 | 46 | 0.0022851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1010-4_0_2_line_24 | NAYY 4x150 SE | 21 | 22 | 0.17825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1010-4_0_2_line_25 | NAYY 4x150 SE | 21 | 23 | 0.042771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1010-4_0_2_line_26 | NAYY 4x150 SE | 22 | 38 | 0.006841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1010-4_0_2_line_27 | NAYY 4x150 SE | 22 | 39 | 0.02473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1010-4_0_2_line_28 | NAYY 4x150 SE | 23 | 32 | 0.10977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1010-4_0_2_line_29 | NAYY 4x150 SE | 24 | 110 | 0.030621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1010-4_0_2_line_30 | NAYY 4x150 SE | 25 | 26 | 0.056162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1010-4_0_2_line_31 | NAYY 4x150 SE | 25 | 27 | 0.085899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1010-4_0_2_line_32 | NAYY 4x150 SE | 26 | 47 | 0.010734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1010-4_0_2_line_33 | NAYY 4x150 SE | 27 | 30 | 0.046114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1010-4_0_2_line_34 | NAYY 4x150 SE | 27 | 46 | 0.1297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1010-4_0_2_line_35 | NAYY 4x150 SE | 28 | 29 | 0.24187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1010-4_0_2_line_36 | NAYY 4x150 SE | 29 | 45 | 0.027408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1010-4_0_2_line_37 | NAYY 4x150 SE | 30 | 31 | 0.017944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1010-4_0_2_line_38 | NAYY 4x150 SE | 32 | 33 | 0.017606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1010-4_0_2_line_39 | NAYY 4x150 SE | 34 | 35 | 0.057159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1010-4_0_2_line_40 | NAYY 4x150 SE | 34 | 36 | 0.12214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1010-4_0_2_line_41 | NAYY 4x150 SE | 35 | 37 | 0.045117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1010-4_0_2_line_42 | NAYY 4x150 SE | 36 | 111 | 0.029684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1010-4_0_2_line_43 | NAYY 4x150 SE | 38 | 89 | 0.13997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1010-4_0_2_line_44 | NAYY 4x150 SE | 39 | 87 | 0.012136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1010-4_0_2_line_45 | NAYY 4x150 SE | 40 | 41 | 0.057715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1010-4_0_2_line_46 | NAYY 4x150 SE | 41 | 42 | 0.003412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1010-4_0_2_line_47 | NAYY 4x150 SE | 43 | 44 | 0.20621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1010-4_0_2_line_48 | NAYY 4x150 SE | 43 | 45 | 0.25517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1010-4_0_2_line_49 | NAYY 4x150 SE | 44 | 75 | 0.040532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1010-4_0_2_line_50 | NAYY 4x150 SE | 47 | 59 | 0.056144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1010-4_0_2_line_51 | NAYY 4x150 SE | 47 | 107 | 0.033744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1010-4_0_2_line_52 | NAYY 4x150 SE | 48 | 49 | 0.0084344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1010-4_0_2_line_53 | NAYY 4x150 SE | 48 | 50 | 0.036301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1010-4_0_2_line_54 | NAYY 4x150 SE | 49 | 51 | 0.0040745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1010-4_0_2_line_55 | NAYY 4x150 SE | 50 | 52 | 0.04316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1010-4_0_2_line_56 | NAYY 4x150 SE | 50 | 53 | 0.0035149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1010-4_0_2_line_57 | NAYY 4x150 SE | 51 | 54 | 0.030793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1010-4_0_2_line_58 | NAYY 4x150 SE | 52 | 55 | 0.091326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1010-4_0_2_line_59 | NAYY 4x150 SE | 53 | 56 | 0.023412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1010-4_0_2_line_60 | NAYY 4x150 SE | 54 | 57 | 0.010669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1010-4_0_2_line_61 | NAYY 4x150 SE | 55 | 58 | 0.00034459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1010-4_0_2_line_62 | NAYY 4x150 SE | 56 | 59 | 0.21314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1010-4_0_2_line_63 | NAYY 4x150 SE | 56 | 60 | 0.084694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1010-4_0_2_line_64 | NAYY 4x150 SE | 57 | 77 | 0.025832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1010-4_0_2_line_65 | NAYY 4x150 SE | 60 | 71 | 0.088277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1010-4_0_2_line_66 | NAYY 4x150 SE | 60 | 97 | 0.23438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1010-4_0_2_line_67 | NAYY 4x150 SE | 61 | 62 | 0.020175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1010-4_0_2_line_68 | NAYY 4x150 SE | 62 | 63 | 0.013327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1010-4_0_2_line_69 | NAYY 4x150 SE | 62 | 64 | 0.004258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1010-4_0_2_line_70 | NAYY 4x150 SE | 63 | 65 | 0.074133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1010-4_0_2_line_71 | NAYY 4x150 SE | 63 | 66 | 0.081285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1010-4_0_2_line_72 | NAYY 4x150 SE | 64 | 67 | 0.2074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1010-4_0_2_line_73 | NAYY 4x150 SE | 65 | 115 | 0.14391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1010-4_0_2_line_74 | NAYY 4x150 SE | 66 | 116 | 0.016538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1010-4_0_2_line_75 | NAYY 4x150 SE | 67 | 79 | 0.0024037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1010-4_0_2_line_76 | NAYY 4x150 SE | 68 | 69 | 0.17299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1010-4_0_2_line_77 | NAYY 4x150 SE | 68 | 70 | 0.004945 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1010-4_0_2_line_78 | NAYY 4x150 SE | 68 | 71 | 0.075137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1010-4_0_2_line_79 | NAYY 4x150 SE | 69 | 103 | 0.010474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1010-4_0_2_line_80 | NAYY 4x150 SE | 70 | 80 | 0.024633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1010-4_0_2_line_81 | NAYY 4x150 SE | 72 | 73 | 0.15912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1010-4_0_2_line_82 | NAYY 4x150 SE | 72 | 74 | 0.02561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1010-4_0_2_line_83 | NAYY 4x150 SE | 73 | 85 | 0.041969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1010-4_0_2_line_84 | NAYY 4x150 SE | 73 | 82 | 0.22149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1010-4_0_2_line_85 | NAYY 4x150 SE | 74 | 102 | 0.029813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1010-4_0_2_line_86 | NAYY 4x150 SE | 75 | 76 | 0.013968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1010-4_0_2_line_87 | NAYY 4x150 SE | 76 | 109 | 0.019681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1010-4_0_2_line_88 | NAYY 4x150 SE | 77 | 78 | 0.029254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1010-4_0_2_line_89 | NAYY 4x150 SE | 79 | 80 | 0.028336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1010-4_0_2_line_90 | NAYY 4x150 SE | 81 | 82 | 0.078012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1010-4_0_2_line_91 | NAYY 4x150 SE | 81 | 83 | 0.032977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1010-4_0_2_line_92 | NAYY 4x150 SE | 83 | 84 | 0.08745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1010-4_0_2_line_93 | NAYY 4x150 SE | 84 | 86 | 0.18295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1010-4_0_2_line_94 | NAYY 4x150 SE | 84 | 87 | 0.015613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1010-4_0_2_line_95 | NAYY 4x150 SE | 86 | 88 | 0.1233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1010-4_0_2_line_96 | NAYY 4x150 SE | 88 | 114 | 0.021955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1010-4_0_2_line_97 | NAYY 4x150 SE | 89 | 113 | 0.038958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1010-4_0_2_line_98 | NAYY 4x150 SE | 90 | 91 | 0.076695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1010-4_0_2_line_99 | NAYY 4x150 SE | 90 | 92 | 0.16816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1010-4_0_2_line_100 | NAYY 4x150 SE | 91 | 93 | 0.0046076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1010-4_0_2_line_101 | NAYY 4x150 SE | 92 | 94 | 0.3509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1010-4_0_2_line_102 | NAYY 4x150 SE | 93 | 95 | 0.0094289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1010-4_0_2_line_103 | NAYY 4x150 SE | 94 | 105 | 0.17201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1010-4_0_2_line_104 | NAYY 4x150 SE | 95 | 96 | 0.53586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1010-4_0_2_line_105 | NAYY 4x150 SE | 96 | 97 | 0.01322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1010-4_0_2_line_106 | NAYY 4x150 SE | 98 | 99 | 0.017982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1010-4_0_2_line_107 | NAYY 4x150 SE | 99 | 100 | 0.035708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1010-4_0_2_line_108 | NAYY 4x150 SE | 99 | 101 | 0.036715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1010-4_0_2_line_109 | NAYY 4x150 SE | 100 | 118 | 0.059851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1010-4_0_2_line_110 | NAYY 4x150 SE | 101 | 117 | 0.10607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1010-4_0_2_line_111 | NAYY 4x150 SE | 103 | 104 | 0.17651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1010-4_0_2_line_112 | NAYY 4x150 SE | 105 | 106 | 0.30623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1010-4_0_2_line_113 | NAYY 4x150 SE | 106 | 120 | 0.0053571 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1010-4_0_2_line_114 | NAYY 4x150 SE | 107 | 108 | 0.035421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1010-4_0_2_line_115 | NAYY 4x150 SE | 108 | 109 | 0.26869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1010-4_0_2_line_116 | NAYY 4x150 SE | 111 | 112 | 0.022534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1010-4_0_2_line_117 | NAYY 4x150 SE | 112 | 113 | 0.051111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1010-4_0_2_line_118 | NAYY 4x150 SE | 118 | 119 | 1.2317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1010-4_0_2_line_119 | NAYY 4x150 SE | 119 | 120 | 0.84534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1010-4_0_2_trafo_245 | 0.25 MVA 20/0.4 kV | 121 | 77 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54 | x55 | y55 | x56 | y56 | x57 | y57 | x58 | y58 | x59 | y59 | x60 | y60 | x61 | y61
0 | 2634963.2595 | 1190557.0188 | 2634951.5266 | 1190577.3378 | 2634942.1579 | 1190591.3129 | 2634918.7846 | 1190608.8639 | 2634890.4152 | 1190614.9576 | 2634865.5589 | 1190612.2226 | 2634831.4657 | 1190589.606
1 | 2634809.3443 | 1190574.9312 | 2634831.4657 | 1190589.606
2 | 2634809.3443 | 1190574.9312 | 2634794.1884 | 1190574.5208 | 2634775.9949 | 1190587.7557 | 2634758.2669 | 1190621.9491 | 2634756.6628 | 1190638.2152 | 2634763.6418 | 1190658.8446 | 2634776.7444 | 1190681.9219 | 2634806.459 | 1190706.6856 | 2634858.6803 | 1190772.375
3 | 2634905.7482 | 1190948.7048 | 2634906.6037 | 1190920.9614 | 2634903.5887 | 1190891.439 | 2634873.3331 | 1190817.0783 | 2634866.1958 | 1190781.8289 | 2634858.6803 | 1190772.375
4 | 2634905.7482 | 1190948.7048 | 2634903.2774 | 1190951.4029 | 2634901.7616 | 1190955.0739 | 2634900.0328 | 1190961.2894 | 2634898.1125 | 1190971.5726 | 2634896.7611 | 1190975.8337 | 2634894.6754 | 1190980.4797 | 2634889.8683 | 1190988.9785 | 2634879.0056 | 1191005.6576 | 2634875.2201 | 1191010.2492 | 2634872.6719 | 1191011.8463 | 2634870.0607 | 1191012.4759 | 2634867.2502 | 1191011.9926 | 2634864.2202 | 1191009.9072 | 2634862.7245 | 1191007.5083 | 2634862.2046 | 1191003.8366 | 2634862.7335 | 1191000.7269 | 2634865.3754 | 1190996.1398 | 2634872.932 | 1190986.8121 | 2634876.7373 | 1190980.1306 | 2634878.2244 | 1190973.5357 | 2634878.739 | 1190967.6466 | 2634877.8252 | 1190960.9043 | 2634874.7947 | 1190949.7362 | 2634870.4508 | 1190937.6044 | 2634863.8627 | 1190924.6146 | 2634853.8521 | 1190907.5361 | 2634844.1664 | 1190892.2604 | 2634834.3503 | 1190878.4181 | 2634825.9066 | 1190868.5192 | 2634814.965 | 1190858.0945 | 2634803.8908 | 1190849.4922 | 2634791.4858 | 1190841.6048 | 2634778.0615 | 1190834.6009 | 2634765.1911 | 1190828.056 | 2634756.9368 | 1190823.5946 | 2634749.8607 | 1190818.4286 | 2634724.9096 | 1190795.3493 | 2634697.9124 | 1190772.7251 | 2634693.0075 | 1190769.1615 | 2634687.6243 | 1190766.5623 | 2634679.3773 | 1190763.4351 | 2634662.96 | 1190758.4263 | 2634652.5224 | 1190755.6867
5 | 2635168.4582 | 1191016.9219 | 2635165.9491 | 1191014.4392 | 2635161.6966 | 1191012.8134 | 2635156.9582 | 1191012.1519 | 2635129.5373 | 1191012.8025 | 2635124.1118 | 1191012.2927 | 2635118.1019 | 1191011.3125 | 2635112.6714 | 1191009.0572 | 2635107.5894 | 1191005.8702 | 2635101.6198 | 1191000.6213 | 2635090.335 | 1190987.7371 | 2635086.3672 | 1190984.3787 | 2635083.379 | 1190982.9827 | 2635079.4282 | 1190981.9034 | 2635074.0849 | 1190981.6832 | 2635069.5127 | 1190982.5569 | 2635065.3313 | 1190984.4223 | 2635061.2234 | 1190988.0558 | 2635059.1371 | 1190991.4899 | 2635055.1209 | 1191002.8948 | 2635052.2215 | 1191016.2962 | 2635048.5508 | 1191036.43 | 2635045.9814 | 1191046.8428 | 2635043.9069 | 1191053.4899 | 2635040.5937 | 1191062.0307 | 2635028.8422 | 1191085.9304 | 2635018.1721 | 1191106.1345 | 2635011.4847 | 1191116.7456 | 2635006.0254 | 1191124.6291 | 2634999.921 | 1191132.0197 | 2634996.4208 | 1191136.057 | 2634993.4057 | 1191139.2856 | 2634990.6334 | 1191141.3927 | 2634986.7999 | 1191142.4487 | 2634983.7053 | 1191142.3083 | 2634980.4027 | 1191141.2329 | 2634977.6927 | 1191139.216 | 2634975.864 | 1191136.4149 | 2634975.2882 | 1191133.1876 | 2634975.5133 | 1191129.8872 | 2634977.0835 | 1191126.0276 | 2634979.5421 | 1191122.7957 | 2634986.7209 | 1191116.8233 | 2634989.7796 | 1191113.9729 | 2634992.527 | 1191109.5977 | 2634995.0935 | 1191103.565 | 2634996.8276 | 1191096.4491 | 2634997.6815 | 1191088.6165 | 2634997.3591 | 1191079.8543 | 2634994.5565 | 1191054.5354 | 2634990.2851 | 1191030.0528 | 2634986.9968 | 1191017.3712 | 2634981.0219 | 1190999.9602 | 2634976.4628 | 1190989.4724 | 2634956.4097 | 1190963.5192 | 2634953.1395 | 1190960.7986 | 2634948.1436 | 1190958.5238 | 2634922.7337 | 1190948.9816 | 2634916.4837 | 1190947.3332 | 2634912.5601 | 1190946.8323 | 2634908.73 | 1190947.288 | 2634905.7482 | 1190948.7048
6 | 2634652.5224 | 1190755.6867 | 2634394.7446 | 1191035.9056
7 | 2634652.5224 | 1190755.6867 | 2634646.1782 | 1190753.1486 | 2634641.3065 | 1190750.4301 | 2634636.7055 | 1190747.0573 | 2634632.0903 | 1190742.1613 | 2634627.512 | 1190736.1761 | 2634610.7638 | 1190710.7729
8 | 2635168.4582 | 1191016.9219 | 2635171.3389 | 1191014.5375 | 2635179.7424 | 1191010.3957 | 2635188.853 | 1191007.8701 | 2635212.8043 | 1191003.4306 | 2635226.8508 | 1191001.7011 | 2635232.3389 | 1191001.9446 | 2635237.5715 | 1191002.8536 | 2635242.3554 | 1191004.8606 | 2635247.1548 | 1191008.1128 | 2635250.6648 | 1191011.5353 | 2635254.2029 | 1191016.6478 | 2635257.1706 | 1191022.8019 | 2635273.4828 | 1191067.4776
9 | 2635168.4582 | 1191016.9219 | 2635165.7029 | 1191020.0074 | 2635160.4845 | 1191029.6709 | 2635151.7662 | 1191051.098 | 2635144.06 | 1191068.9514 | 2635140.1439 | 1191076.2768 | 2635131.8334 | 1191089.3018 | 2635095.0554 | 1191142.4372 | 2635087.0544 | 1191154.7081 | 2635081.0019 | 1191164.9338 | 2635074.4019 | 1191178.836 | 2635050.6181 | 1191235.947
10 | 2634578.8985 | 1190684.8633 | 2634579.2446 | 1190685.2255 | 2634586.0879 | 1190691.157 | 2634590.0014 | 1190693.4475 | 2634595.4777 | 1190695.7915 | 2634600.6133 | 1190697.7 | 2634602.3762 | 1190698.744 | 2634603.9902 | 1190700.4987 | 2634610.7638 | 1190710.7729
11 | 2635273.4828 | 1191067.4776 | 2635264.1087 | 1191077.1943 | 2635260.0088 | 1191080.7499 | 2635255.3892 | 1191083.2352 | 2635248.2241 | 1191085.5387 | 2635241.5556 | 1191086.8735
12 | 2635044.4143 | 1191250.8439 | 2635050.6181 | 1191235.947
13 | 2635244.7347 | 1191197.9164 | 2635244.1053 | 1191195.9631 | 2635228.8831 | 1191178.5864 | 2635216.4322 | 1191154.0666 | 2635197.4562 | 1191105.9736 | 2635196.4945 | 1191100.9653 | 2635197.0786 | 1191097.578 | 2635198.6025 | 1191095.1412 | 2635201.6394 | 1191093.4247 | 2635217.5099 | 1191088.771 | 2635240.3466 | 1191087.1155 | 2635241.5556 | 1191086.8735
14 | 2635044.4143 | 1191250.8439 | 2635128.2839 | 1191344.6314
15 | 2635228.9635 | 1190450.0182 | 2635255.9924 | 1190460.9241
16 | 2635223.6724 | 1190447.8833 | 2635228.9635 | 1190450.0182
17 | 2635322.0753 | 1190503.2034 | 2635290.3018 | 1190474.7676 | 2635255.9924 | 1190460.9241
18 | 2635322.0753 | 1190503.2034 | 2635318.409 | 1190510.7414 | 2635313.9745 | 1190521.8324 | 2635311.6709 | 1190534.9037 | 2635318.3139 | 1190617.7524
19 | 2635322.0753 | 1190503.2034 | 2635334.026 | 1190488.5771 | 2635337.0291 | 1190484.8928 | 2635358.1745 | 1190457.5472 | 2635379.6464 | 1190430.4704 | 2635396.9325 | 1190403.3578
20 | 2635318.3139 | 1190617.7524 | 2635320.3201 | 1190642.7742
21 | 2635396.9325 | 1190403.3578 | 2635402.6241 | 1190411.8293 | 2635405.0504 | 1190418.8115
22 | 2635396.9325 | 1190403.3578 | 2635407.2425 | 1190378.7054 | 2635416.9006 | 1190362.4426 | 2635418.5026 | 1190359.7395
23 | 2635320.3201 | 1190642.7742 | 2635320.5028 | 1190645.052
24 | 2635278.2687 | 1190283.2712 | 2635322.6645 | 1190270.0811 | 2635327.2696 | 1190276.6451 | 2635335.5447 | 1190287.9889 | 2635343.5129 | 1190297.063 | 2635351.6847 | 1190305.2378 | 2635360.6737 | 1190313.1729 | 2635418.5026 | 1190359.7395
25 | 2635278.2687 | 1190283.2712 | 2635262.1411 | 1190287.1895 | 2635237.2629 | 1190295.3237
26 | 2635418.5026 | 1190359.7395 | 2635420.9499 | 1190353.3505
27 | 2635418.5026 | 1190359.7395 | 2635437.0085 | 1190376.1432
28 | 2635133.4328 | 1190328.967 | 2635188.6289 | 1190316.5733 | 2635199.1802 | 1190313.0111 | 2635208.821 | 1190308.6876 | 2635220.1543 | 1190303.129 | 2635230.8785 | 1190297.4112 | 2635237.2629 | 1190295.3237
29 | 2635405.0504 | 1190418.8115 | 2635409.8668 | 1190432.6723 | 2635414.0546 | 1190448.0602
30 | 2635407.0945 | 1190736.5644 | 2635411.2823 | 1190733.6654 | 2635414.7464 | 1190730.662 | 2635423.2969 | 1190719.8067 | 2635433.2088 | 1190704.368 | 2635436.4869 | 1190703.1646 | 2635440.995 | 1190701.557 | 2635446.3 | 1190704.4455
31 | 2635407.0945 | 1190736.5644 | 2635394.7753 | 1190740.038 | 2635391.5559 | 1190741.6309 | 2635386.6492 | 1190744.9037 | 2635378.5196 | 1190751.6483 | 2635370.0789 | 1190758.1353 | 2635360.73 | 1190763.483 | 2635347.4901 | 1190769.2414 | 2635330.8689 | 1190774.335
32 | 2635456.5437 | 1190701.2377 | 2635446.3 | 1190704.4455
33 | 2635334.4177 | 1190820.303 | 2635330.8689 | 1190774.335
34 | 2635330.8689 | 1190774.335 | 2635320.5028 | 1190645.052
35 | 2635244.7347 | 1191197.9164 | 2635385.7846 | 1191394.3986
36 | 2635410.5924 | 1191400.1141 | 2635407.5094 | 1191397.6576 | 2635396.7763 | 1191392.2913 | 2635395.4297 | 1191391.8053 | 2635393.8131 | 1191391.8736 | 2635385.7846 | 1191394.3986
37 | 2635334.4177 | 1190820.303 | 2635348.7027 | 1190831.2153
38 | 2635116.2542 | 1190332.8243 | 2635133.4328 | 1190328.967
39 | 2635203.057 | 1190020.4984 | 2635199.7407 | 1190009.9844 | 2635198.2895 | 1190003.8837 | 2635214.7713 | 1189999.5003 | 2635226.1197 | 1189996.6655 | 2635231.8484 | 1189996.3434 | 2635237.2153 | 1189996.6084
40 | 2635203.057 | 1190020.4984 | 2635213.4353 | 1190046.4622 | 2635256.225 | 1190130.3579
41 | 2635237.2153 | 1189996.6084 | 2635245.9309 | 1190004.4639 | 2635250.2326 | 1190008.2135 | 2635253.0154 | 1190012.1875 | 2635253.4531 | 1190016.8482 | 2635252.8516 | 1190020.58 | 2635250.4963 | 1190023.0119 | 2635240.081 | 1190026.6748
42 | 2635269.5373 | 1190156.8888 | 2635257.9204 | 1190133.6819 | 2635256.225 | 1190130.3579
43 | 2635420.9499 | 1190353.3505 | 2635352.5704 | 1190298.5728 | 2635332.4544 | 1190275.4083 | 2635324.5483 | 1190263.5442 | 2635321.0571 | 1190257.0033
44 | 2635446.0906 | 1190384.1936 | 2635437.0085 | 1190376.1432
45 | 2635128.2839 | 1191344.6314 | 2635123.2123 | 1191377.6071 | 2635121.2286 | 1191385.6554 | 2635117.8631 | 1191395.3409 | 2635115.0603 | 1191400.429
46 | 2635115.0603 | 1191400.429 | 2635113.414 | 1191403.4176
47 | 2635616.6426 | 1191249.6057 | 2635613.6368 | 1191246.0748 | 2635545.6412 | 1191075.9791 | 2635533.9869 | 1191061.7575
48 | 2635616.6426 | 1191249.6057 | 2635410.5924 | 1191400.1141
49 | 2635541.0888 | 1191031.3259 | 2635526.0832 | 1191044.1459 | 2635525.2263 | 1191051.0668 | 2635533.9869 | 1191061.7575
50 | 2635456.5437 | 1190701.2377 | 2635483.7034 | 1190672.8609 | 2635496.8962 | 1190662.2333
51 | 2635456.5437 | 1190701.2377 | 2635474.0569 | 1190730.0811
52 | 2635695.5424 | 1190595.1219 | 2635691.261 | 1190587.8548
53 | 2635695.9483 | 1190627.7302 | 2635702.031 | 1190619.0951 | 2635702.9809 | 1190614.5205 | 2635700.8922 | 1190604.2025 | 2635695.5424 | 1190595.1219
54 | 2635691.261 | 1190587.8548 | 2635689.1928 | 1190584.3443
55 | 2635695.9483 | 1190627.7302 | 2635736.3709 | 1190612.6038
56 | 2635695.9483 | 1190627.7302 | 2635692.8815 | 1190629.4475
57 | 2635673.5622 | 1190557.8135 | 2635689.1928 | 1190584.3443
58 | 2635736.3709 | 1190612.6038 | 2635748.7309 | 1190607.9786 | 2635758.1761 | 1190601.9205 | 2635793.3491 | 1190567.5341 | 2635801.7673 | 1190562.3816 | 2635809.0468 | 1190559.4461
59 | 2635672.4542 | 1190640.8863 | 2635673.4946 | 1190640.3033 | 2635692.8815 | 1190629.4475
60 | 2635668.1467 | 1190548.6215 | 2635673.5622 | 1190557.8135
61 | 2635809.3664 | 1190559.3172 | 2635809.0468 | 1190559.4461
62 | 2635496.8962 | 1190662.2333 | 2635506.76 | 1190654.9544 | 2635638.5713 | 1190600.852 | 2635641.2924 | 1190599.7342 | 2635668.7057 | 1190642.954 | 2635672.4542 | 1190640.8863
63 | 2635717.5234 | 1190712.6602 | 2635701.828 | 1190687.6976 | 2635687.3934 | 1190664.8326 | 2635672.4542 | 1190640.8863
64 | 2635668.1467 | 1190548.6215 | 2635655.0345 | 1190526.3652 | 2635655.0345 | 1190526.3652
65 | 2635717.5234 | 1190712.6602 | 2635732.6339 | 1190734.6733 | 2635748.3251 | 1190760.2918 | 2635765.1938 | 1190786.9357
66 | 2635717.5234 | 1190712.6602 | 2635718.9682 | 1190712.024 | 2635725.2712 | 1190708.6375 | 2635748.3723 | 1190701.2824 | 2635801.3403 | 1190688.6807 | 2635845.5677 | 1190682.9419 | 2635897.1636 | 1190683.0731 | 2635930.3396 | 1190685.4954 | 2635946.1327 | 1190693.032
67 | 2635943.4123 | 1191074.9178 | 2635948.4365 | 1191094.4569
68 | 2635956.6828 | 1191074.197 | 2635948.0837 | 1191074.0231 | 2635944.7718 | 1191074.5257 | 2635943.4123 | 1191074.9178
69 | 2635939.3558 | 1191076.2497 | 2635943.4123 | 1191074.9178
70 | 2636026.9854 | 1191097.1316 | 2636011.1584 | 1191089.3767 | 2636000.5868 | 1191085.0331 | 2635988.6006 | 1191081.3814 | 2635979.3227 | 1191078.702 | 2635967.4512 | 1191076.2516 | 2635956.6828 | 1191074.197
71 | 2635956.6828 | 1191074.197 | 2635996.77 | 1191031.2589 | 2636001.8914 | 1191027.81 | 2636017.0502 | 1191021.6358
72 | 2635939.3558 | 1191076.2497 | 2635931.3689 | 1191060.4599 | 2635830.3664 | 1190899.883
73 | 2636026.9854 | 1191097.1316 | 2636033.8273 | 1191090.3024 | 2636104.1847 | 1191038.2977 | 2636111.962 | 1191031.8744 | 2636114.7271 | 1191028.5115 | 2636116.1817 | 1191024.985 | 2636116.8198 | 1191021.587 | 2636116.7273 | 1191019.2185 | 2636115.966 | 1191015.234 | 2636113.903 | 1191007.1283 | 2636113.5065 | 1190999.544 | 2636113.8865 | 1190996.9155
74 | 2636017.0502 | 1191021.6358 | 2636029.9185 | 1191016.3945 | 2636032.0399 | 1191014.8175
75 | 2635829.0866 | 1190897.8483 | 2635830.3664 | 1190899.883
76 | 2635805.1839 | 1190850.5467 | 2635806.5075 | 1190849.7875 | 2635849.6883 | 1190825.0879 | 2635864.8567 | 1190819.4756 | 2635894.3384 | 1190813.5267 | 2635908.7323 | 1190807.3985 | 2635939.0889 | 1190792.9059 | 2635953.0154 | 1190782.0836 | 2635961.3132 | 1190780.0341
77 | 2635800.8842 | 1190853.0112 | 2635805.1839 | 1190850.5467
78 | 2635805.1839 | 1190850.5467 | 2635790.6536 | 1190827.2473 | 2635767.1255 | 1190789.9867 | 2635765.1938 | 1190786.9357
79 | 2635971.4821 | 1190777.5224 | 2635961.3132 | 1190780.0341
80 | 2635800.8842 | 1190853.0112 | 2635813.9996 | 1190873.8625
81 | 2635643.3833 | 1189949.718 | 2635643.437 | 1189954.7989 | 2635638.7235 | 1190008.7666 | 2635637.5053 | 1190012.2946 | 2635634.94 | 1190017.9379 | 2635634.1284 | 1190022.3355 | 2635629.5852 | 1190070.7791 | 2635626.3924 | 1190096.0404 | 2635626.7515 | 1190099.7667 | 2635627.8869 | 1190103.7534 | 2635629.5007 | 1190106.7869
82 | 2635643.3833 | 1189949.718 | 2635645.0392 | 1189950.8173 | 2635647.8549 | 1189951.7791 | 2635651.6129 | 1189952.0349 | 2635655.2225 | 1189951.5783 | 2635658.519 | 1189951.2088 | 2635663.8478 | 1189951.474 | 2635668.3672 | 1189952.2716
83 | 2635629.5007 | 1190106.7869 | 2635630.3132 | 1190104.8017 | 2635631.659 | 1190102.8865 | 2635633.8276 | 1190101.1207 | 2635638.7845 | 1190098.4932 | 2635643.8624 | 1190097.3227 | 2635654.1431 | 1190095.7941 | 2635656.9445 | 1190096.6001 | 2635658.669 | 1190097.6776 | 2635659.7223 | 1190100.0852 | 2635660.8922 | 1190105.9398
84 | 2635629.5007 | 1190106.7869 | 2635628.3502 | 1190115.5959 | 2635627.4162 | 1190118.781 | 2635625.6733 | 1190122.0724 | 2635622.4823 | 1190125.2329 | 2635619.1794 | 1190127.9814 | 2635614.8405 | 1190130.5459 | 2635608.3124 | 1190133.2308 | 2635563.6729 | 1190148.6741 | 2635502.0343 | 1190167.063 | 2635452.6119 | 1190179.0214 | 2635441.806 | 1190183.0152 | 2635436.3451 | 1190185.7733 | 2635432.9279 | 1190188.9027
85 | 2635694.8794 | 1189965.0994 | 2635688.0845 | 1189960.0562 | 2635680.7425 | 1189955.9548 | 2635671.6712 | 1189952.8547 | 2635668.3672 | 1189952.2716
86 | 2635541.0888 | 1191031.3259 | 2635551.7087 | 1191022.2527
87 | 2635554.1424 | 1191002.7233 | 2635551.7087 | 1191022.2527 | 2635551.7087 | 1191022.2527
88 | 2635655.0345 | 1190526.3652 | 2635651.5693 | 1190524.3991 | 2635648.5002 | 1190523.7694 | 2635644.1989 | 1190525.1779 | 2635629.6131 | 1190535.0472
89 | 2635829.0866 | 1190897.8483 | 2635813.9996 | 1190873.8625
90 | 2635432.9279 | 1190188.9027 | 2635431.4843 | 1190190.2247 | 2635427.5786 | 1190195.6379 | 2635408.7193 | 1190230.7676 | 2635405.8653 | 1190240.1558 | 2635404.9465 | 1190248.5327 | 2635405.5652 | 1190254.8064 | 2635406.4565 | 1190259.6892
91 | 2635417.5596 | 1190290.6114 | 2635407.7367 | 1190266.7034 | 2635406.4565 | 1190259.6892
92 | 2635453.3399 | 1190370.3845 | 2635427.8374 | 1190315.6264 | 2635417.5596 | 1190290.6114
93 | 2635453.3399 | 1190370.3845 | 2635474.8581 | 1190343.3417 | 2635587.0541 | 1190274.1917 | 2635602.5763 | 1190268.3289
94 | 2635446.0906 | 1190384.1936 | 2635448.3161 | 1190379.204 | 2635448.9633 | 1190378.085 | 2635453.3399 | 1190370.3845
95 | 2635602.5763 | 1190268.3289 | 2635629.332 | 1190258.2232 | 2635693.2889 | 1190233.3236 | 2635702.7079 | 1190231.7455 | 2635719.0524 | 1190229.3948
96 | 2635740.7833 | 1190226.2695 | 2635719.0524 | 1190229.3948
97 | 2635302.7129 | 1190222.6342 | 2635321.0571 | 1190257.0033
98 | 2635948.547 | 1190231.9929 | 2635948.547 | 1190231.9929 | 2635968.4929 | 1190248.8327 | 2635983.9931 | 1190261.8773 | 2636003.9363 | 1190279.1175 | 2636007.8078 | 1190279.9965
99 | 2636146.1146 | 1190232.7815 | 2636136.2883 | 1190241.1824 | 2636104.081 | 1190285.1231 | 2636097.4893 | 1190292.0205 | 2636085.6202 | 1190293.9834 | 2636053.7756 | 1190290.4343 | 2636007.8078 | 1190279.9965
100 | 2635948.547 | 1190231.9929 | 2635943.9617 | 1190231.5401
101 | 2636146.1146 | 1190232.7815 | 2636437.7634 | 1190427.9086
102 | 2635934.5784 | 1190230.6137 | 2635943.9617 | 1190231.5401
103 | 2636525.3899 | 1190334.2802 | 2636515.3792 | 1190337.8434 | 2636507.9068 | 1190346.547 | 2636506.1145 | 1190352.8617 | 2636507.5816 | 1190362.3647 | 2636508.5589 | 1190369.6746 | 2636508.4833 | 1190375.8219 | 2636504.8632 | 1190396.789 | 2636503.0219 | 1190417.4 | 2636500.5587 | 1190423.7107 | 2636497.0365 | 1190426.1127 | 2636492.1743 | 1190425.6829 | 2636488.271 | 1190424.3139 | 2636480.7484 | 1190418.7429 | 2636474.9705 | 1190414.6722 | 2636468.24 | 1190413.0193 | 2636461.4904 | 1190413.245 | 2636457.2912 | 1190415.3761 | 2636451.6647 | 1190420.2668 | 2636446.4813 | 1190423.7482 | 2636437.7634 | 1190427.9086
104 | 2635934.5784 | 1190230.6137 | 2635934.2809 | 1190230.5843 | 2635897.8154 | 1190233.3229 | 2635892.8828 | 1190236.9619 | 2635890.3986 | 1190243.0615 | 2635895.6399 | 1190255.3328 | 2635898.8084 | 1190272.4722 | 2635903.8618 | 1190317.36 | 2635911.4972 | 1190339.829 | 2635953.8559 | 1190437.5357 | 2635958.2394 | 1190456.728 | 2635959.6902 | 1190488.1425 | 2635963.2722 | 1190511.2988 | 2635962.003 | 1190518.2282 | 2635963.5078 | 1190533.0119 | 2635960.9575 | 1190550.1281 | 2635961.2808 | 1190563.5817 | 2635969.3249 | 1190586.4646 | 2635974.8768 | 1190605.3526 | 2635985.859 | 1190626.5188 | 2635993.0722 | 1190650.6196 | 2635994.0378 | 1190663.7548 | 2635986.0253 | 1190673.7231 | 2635963.9285 | 1190691.5446 | 2635958.9886 | 1190694.1408
105 | 2635958.9886 | 1190694.1408 | 2635957.6335 | 1190694.853 | 2635947.0434 | 1190693.4665 | 2635946.1327 | 1190693.032
106 | 2636375.0424 | 1189781.9452 | 2636365.8878 | 1189766.4678
107 | 2636375.0424 | 1189781.9452 | 2636377.6919 | 1189786.4193 | 2636384.8039 | 1189793.1883 | 2636394.0043 | 1189793.8557 | 2636403.862 | 1189788.0013
108 | 2636375.0424 | 1189781.9452 | 2636369.7183 | 1189785.9151 | 2636352.0143 | 1189804.2064 | 2636349.464 | 1189808.0559
109 | 2636437.8411 | 1189817.1568 | 2636431.6443 | 1189794.0845 | 2636427.0038 | 1189783.4505 | 2636418.4172 | 1189782.1754 | 2636403.862 | 1189788.0013
110 | 2636372.653 | 1189901.6732 | 2636374.2104 | 1189901.3825 | 2636374.9119 | 1189900.1416 | 2636374.3054 | 1189898.2925 | 2636373.005 | 1189895.194 | 2636371.6386 | 1189890.3943 | 2636371.4577 | 1189882.5111 | 2636373.2323 | 1189870.3153 | 2636373.2166 | 1189860.3432 | 2636371.8633 | 1189853.3867 | 2636369.9531 | 1189848.9728 | 2636367.4173 | 1189845.8668 | 2636360.089 | 1189839.5634 | 2636352.9167 | 1189833.9502 | 2636350.0767 | 1189829.4528 | 2636348.1698 | 1189824.4941 | 2636347.1102 | 1189819.396 | 2636346.5197 | 1189814.9122 | 2636347.789 | 1189810.5843 | 2636349.464 | 1189808.0559
111 | 2635971.4821 | 1190777.5224 | 2635977.1832 | 1190776.1143 | 2635987.8755 | 1190766.7957 | 2636082.9335 | 1190688.0802 | 2636106.4016 | 1190669.2559 | 2636108.4058 | 1190667.0871
112 | 2636758.1637 | 1190533.2555 | 2636525.3899 | 1190334.2802
113 | 2636758.1637 | 1190533.2555 | 2636760.8956 | 1190537.8636
114 | 2635505.2203 | 1190739.78 | 2635482.4987 | 1190738.5003 | 2635478.4116 | 1190737.2532 | 2635474.0569 | 1190730.0811
115 | 2635505.2203 | 1190739.78 | 2635517.8287 | 1190857.2627 | 2635522.0797 | 1190879.7111 | 2635522.9445 | 1190884.2965 | 2635528.1595 | 1190901.0476 | 2635552.2516 | 1190977.0315 | 2635554.1424 | 1191002.7233
116 | 2635269.5373 | 1190156.8888 | 2635279.624 | 1190177.0388
117 | 2635302.7129 | 1190222.6342 | 2635298.453 | 1190214.653 | 2635279.624 | 1190177.0388
118 | 2636437.8411 | 1189817.1568 | 2637571.6266 | 1190298.4618
119 | 2636760.8956 | 1190537.8636 | 2637571.6266 | 1190298.4618

## bus_geodata
| x | y | coords
0 | 2634963.2595 | 1190557.0188
1 | 2634831.4657 | 1190589.606
2 | 2634809.3443 | 1190574.9312
3 | 2634858.6803 | 1190772.375
4 | 2634905.7482 | 1190948.7048
5 | 2634394.7446 | 1191035.9056
6 | 2634652.5224 | 1190755.6867
7 | 2635168.4582 | 1191016.9219
8 | 2634578.8985 | 1190684.8633
9 | 2634610.7638 | 1190710.7729
10 | 2635273.4828 | 1191067.4776
11 | 2635050.6181 | 1191235.947
12 | 2635241.5556 | 1191086.8735
13 | 2635044.4143 | 1191250.8439
14 | 2635228.9635 | 1190450.0182
15 | 2635255.9924 | 1190460.9241
16 | 2635223.6724 | 1190447.8833
17 | 2635322.0753 | 1190503.2034
18 | 2635318.3139 | 1190617.7524
19 | 2635396.9325 | 1190403.3578
20 | 2635320.3201 | 1190642.7742
21 | 2635278.2687 | 1190283.2712
22 | 2635418.5026 | 1190359.7395
23 | 2635237.2629 | 1190295.3237
24 | 2635405.0504 | 1190418.8115
25 | 2635407.0945 | 1190736.5644
26 | 2635446.3 | 1190704.4455
27 | 2635330.8689 | 1190774.335
28 | 2635244.7347 | 1191197.9164
29 | 2635385.7846 | 1191394.3986
30 | 2635334.4177 | 1190820.303
31 | 2635348.7027 | 1190831.2153
32 | 2635133.4328 | 1190328.967
33 | 2635116.2542 | 1190332.8243
34 | 2635203.057 | 1190020.4984
35 | 2635237.2153 | 1189996.6084
36 | 2635256.225 | 1190130.3579
37 | 2635240.081 | 1190026.6748
38 | 2635420.9499 | 1190353.3505
39 | 2635437.0085 | 1190376.1432
40 | 2635128.2839 | 1191344.6314
41 | 2635115.0603 | 1191400.429
42 | 2635113.414 | 1191403.4176
43 | 2635616.6426 | 1191249.6057
44 | 2635533.9869 | 1191061.7575
45 | 2635410.5924 | 1191400.1141
46 | 2635320.5028 | 1190645.052
47 | 2635456.5437 | 1190701.2377
48 | 2635695.5424 | 1190595.1219
49 | 2635691.261 | 1190587.8548
50 | 2635695.9483 | 1190627.7302
51 | 2635689.1928 | 1190584.3443
52 | 2635736.3709 | 1190612.6038
53 | 2635692.8815 | 1190629.4475
54 | 2635673.5622 | 1190557.8135
55 | 2635809.0468 | 1190559.4461
56 | 2635672.4542 | 1190640.8863
57 | 2635668.1467 | 1190548.6215
58 | 2635809.3664 | 1190559.3172
59 | 2635496.8962 | 1190662.2333
60 | 2635717.5234 | 1190712.6602
61 | 2635948.4365 | 1191094.4569
62 | 2635943.4123 | 1191074.9178
63 | 2635956.6828 | 1191074.197
64 | 2635939.3558 | 1191076.2497
65 | 2636026.9854 | 1191097.1316
66 | 2636017.0502 | 1191021.6358
67 | 2635830.3664 | 1190899.883
68 | 2635805.1839 | 1190850.5467
69 | 2635961.3132 | 1190780.0341
70 | 2635800.8842 | 1190853.0112
71 | 2635765.1938 | 1190786.9357
72 | 2635643.3833 | 1189949.718
73 | 2635629.5007 | 1190106.7869
74 | 2635668.3672 | 1189952.2716
75 | 2635541.0888 | 1191031.3259
76 | 2635551.7087 | 1191022.2527
77 | 2635655.0345 | 1190526.3652
78 | 2635629.6131 | 1190535.0472
79 | 2635829.0866 | 1190897.8483
80 | 2635813.9996 | 1190873.8625
81 | 2635406.4565 | 1190259.6892
82 | 2635432.9279 | 1190188.9027
83 | 2635417.5596 | 1190290.6114
84 | 2635453.3399 | 1190370.3845
85 | 2635660.8922 | 1190105.9398
86 | 2635602.5763 | 1190268.3289
87 | 2635446.0906 | 1190384.1936
88 | 2635719.0524 | 1190229.3948
89 | 2635321.0571 | 1190257.0033
90 | 2636007.8078 | 1190279.9965
91 | 2635948.547 | 1190231.9929
92 | 2636146.1146 | 1190232.7815
93 | 2635943.9617 | 1190231.5401
94 | 2636437.7634 | 1190427.9086
95 | 2635934.5784 | 1190230.6137
96 | 2635958.9886 | 1190694.1408
97 | 2635946.1327 | 1190693.032
98 | 2636365.8878 | 1189766.4678
99 | 2636375.0424 | 1189781.9452
100 | 2636403.862 | 1189788.0013
101 | 2636349.464 | 1189808.0559
102 | 2635694.8794 | 1189965.0994
103 | 2635971.4821 | 1190777.5224
104 | 2636108.4058 | 1190667.0871
105 | 2636525.3899 | 1190334.2802
106 | 2636758.1637 | 1190533.2555
107 | 2635474.0569 | 1190730.0811
108 | 2635505.2203 | 1190739.78
109 | 2635554.1424 | 1191002.7233
110 | 2635414.0546 | 1190448.0602
111 | 2635269.5373 | 1190156.8888
112 | 2635279.624 | 1190177.0388
113 | 2635302.7129 | 1190222.6342
114 | 2635740.7833 | 1190226.2695
115 | 2636113.8865 | 1190996.9155
116 | 2636032.0399 | 1191014.8175
117 | 2636372.653 | 1189901.6732
118 | 2636437.8411 | 1189817.1568
119 | 2637571.6266 | 1190298.4618
120 | 2636760.8956 | 1190537.8636
121 | 2635655.0345 | 1190526.3652

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98893 | -0.087648 | 0.00013313 | 3.3365e-05
1 | 0.98896 | -0.087411 | 3.774e-05 | 9.4585e-06
2 | 0.98896 | -0.08736 | 0 | 0
3 | 0.98903 | -0.086818 | 4.6795e-05 | 1.1728e-05
4 | 0.98909 | -0.086306 | 0 | 0
5 | 0.98871 | -0.089346 | 8.4508e-05 | 2.118e-05
6 | 0.98876 | -0.088947 | 0 | 0
7 | 0.98966 | -0.081222 | 0 | 0
8 | 0.98871 | -0.089265 | 0.00010125 | 2.5377e-05
9 | 0.98872 | -0.08922 | 0.00031855 | 7.9835e-05
10 | 0.98991 | -0.079013 | 0 | 0
11 | 0.98948 | -0.082542 | 0.00015681 | 3.9301e-05
12 | 0.98998 | -0.078436 | 0.00013293 | 3.3315e-05
13 | 0.98947 | -0.082599 | 0 | 0
14 | 0.98993 | -0.075279 | 4.9579e-05 | 1.2426e-05
15 | 0.98994 | -0.075241 | 0.00022824 | 5.7203e-05
16 | 0.98993 | -0.075284 | 7.712e-05 | 1.9328e-05
17 | 0.98998 | -0.074947 | 0 | 0
18 | 0.99086 | -0.068434 | 0.0001494 | 3.7443e-05
19 | 0.98909 | -0.081451 | 0 | 0
20 | 0.99106 | -0.066994 | 4.9448e-05 | 1.2393e-05
21 | 0.98867 | -0.084572 | 0 | 0
22 | 0.98878 | -0.083742 | 0 | 0
23 | 0.98865 | -0.084766 | 0.0002159 | 5.4109e-05
24 | 0.98908 | -0.081539 | 0.0004074 | 0.0001021
25 | 0.99285 | -0.053792 | 0 | 0
26 | 0.99332 | -0.050353 | 0.00022742 | 5.6996e-05
27 | 0.99214 | -0.059053 | 0 | 0
28 | 0.99028 | -0.075806 | 3.9807e-05 | 9.9766e-06
29 | 0.99076 | -0.071688 | 0.00027008 | 6.7688e-05
30 | 0.99213 | -0.059099 | 0 | 0
31 | 0.99213 | -0.059117 | 9.5607e-05 | 2.3961e-05
32 | 0.98861 | -0.085015 | 5.4763e-05 | 1.3725e-05
33 | 0.98861 | -0.085044 | 0.00016063 | 4.0258e-05
34 | 0.98826 | -0.087555 | 0 | 0
35 | 0.98822 | -0.087831 | 0 | 0
36 | 0.98835 | -0.086954 | 0.00027925 | 6.9988e-05
37 | 0.98819 | -0.088047 | 0.00046593 | 0.00011677
38 | 0.98877 | -0.083826 | 0 | 0
39 | 0.98868 | -0.084479 | 0.00015916 | 3.9889e-05
40 | 0.98941 | -0.083037 | 0.00010565 | 2.6477e-05
41 | 0.98939 | -0.083171 | 0.00010977 | 2.751e-05
42 | 0.98939 | -0.083175 | 0.0001146 | 2.872e-05
43 | 0.99145 | -0.065868 | 0 | 0
44 | 0.99195 | -0.061564 | 0.00034816 | 8.7256e-05
45 | 0.99082 | -0.071142 | 6.4019e-05 | 1.6045e-05
46 | 0.99107 | -0.066862 | 0.00023382 | 5.8601e-05
47 | 0.99341 | -0.049671 | 0 | 0
48 | 0.99812 | -0.014083 | 0.00035537 | 8.9064e-05
49 | 0.99831 | -0.012645 | 0.00015306 | 3.8359e-05
50 | 0.99732 | -0.02015 | 0 | 0
51 | 0.99841 | -0.011944 | 9.3825e-05 | 2.3515e-05
52 | 0.99727 | -0.020514 | 0.00024743 | 6.2011e-05
53 | 0.99724 | -0.020708 | 0.00034396 | 8.6204e-05
54 | 0.99911 | -0.0066215 | 0.00077849 | 0.00019511
55 | 0.99719 | -0.021052 | 0.00049113 | 0.00012309
56 | 0.99676 | -0.024347 | 0 | 0
57 | 0.99937 | -0.004696 | 0.00014549 | 3.6462e-05
58 | 0.99719 | -0.021052 | 9.1078e-05 | 2.2826e-05
59 | 0.99411 | -0.044383 | 0 | 0
60 | 0.99608 | -0.029566 | 0 | 0
61 | 0.99517 | -0.036269 | 0.00017753 | 4.4494e-05
62 | 0.99518 | -0.036232 | 0 | 0
63 | 0.99517 | -0.036331 | 0 | 0
64 | 0.99518 | -0.036193 | 0 | 0
65 | 0.99516 | -0.036377 | 0 | 0
66 | 0.99509 | -0.036874 | 0.00025244 | 6.3268e-05
67 | 0.99545 | -0.034262 | 0.00029332 | 7.3512e-05
68 | 0.99557 | -0.033368 | 0 | 0
69 | 0.99543 | -0.034388 | 0.00034487 | 8.6432e-05
70 | 0.99556 | -0.033451 | 0 | 0
71 | 0.9958 | -0.031647 | 5.8547e-05 | 1.4673e-05
72 | 0.98742 | -0.093647 | 0 | 0
73 | 0.9876 | -0.092349 | 0 | 0
74 | 0.9874 | -0.093853 | 0.00051847 | 0.00012994
75 | 0.99207 | -0.06057 | 0.00028556 | 7.1568e-05
76 | 0.99212 | -0.060187 | 0.00011866 | 2.9739e-05
77 | 1 | 0 | -0.018243 | -0.004226
78 | 0.99999 | -9.4262e-05 | 0.00032142 | 8.0554e-05
79 | 0.99545 | -0.034232 | 4.9915e-05 | 1.251e-05
80 | 0.9955 | -0.033867 | 0.00039412 | 9.8777e-05
81 | 0.98823 | -0.087768 | 0.00025498 | 6.3903e-05
82 | 0.98806 | -0.089021 | 8.7855e-05 | 2.2018e-05
83 | 0.98832 | -0.087151 | 0.00027899 | 6.9922e-05
84 | 0.98858 | -0.08526 | 0 | 0
85 | 0.98756 | -0.09263 | 0.00065029 | 0.00016298
86 | 0.98842 | -0.086433 | 0.00022521 | 5.6444e-05
87 | 0.98864 | -0.084821 | 0 | 0
88 | 0.98835 | -0.086922 | 5.6958e-05 | 1.4275e-05
89 | 0.98854 | -0.085554 | 0.00010848 | 2.7187e-05
90 | 0.99224 | -0.059768 | 0.0001003 | 2.5138e-05
91 | 0.9925 | -0.057671 | 0.00010106 | 2.5327e-05
92 | 0.99169 | -0.064179 | 0.0002064 | 5.1729e-05
93 | 0.99252 | -0.05754 | 0.00036577 | 9.1671e-05
94 | 0.99065 | -0.072572 | 9.5531e-05 | 2.3942e-05
95 | 0.99256 | -0.057237 | 0.00018615 | 4.6654e-05
96 | 0.99489 | -0.038921 | 3.1411e-05 | 7.8722e-06
97 | 0.99495 | -0.038463 | 0.0003171 | 7.9473e-05
98 | 0.98394 | -0.12402 | 0.00040642 | 0.00010186
99 | 0.98395 | -0.12394 | 0 | 0
100 | 0.98399 | -0.12364 | 0.00071889 | 0.00018017
101 | 0.98393 | -0.1241 | 0.00017274 | 4.3292e-05
102 | 0.98738 | -0.093935 | 0.00026535 | 6.6502e-05
103 | 0.99543 | -0.034413 | 0.00011407 | 2.8588e-05
104 | 0.9954 | -0.034606 | 0.00010029 | 2.5135e-05
105 | 0.99016 | -0.076482 | 8.3582e-05 | 2.0947e-05
106 | 0.98933 | -0.083119 | 8.3834e-05 | 2.1011e-05
107 | 0.99329 | -0.050706 | 0.00012121 | 3.0379e-05
108 | 0.99316 | -0.051748 | 0 | 0
109 | 0.99219 | -0.059623 | 5.4531e-05 | 1.3667e-05
110 | 0.98908 | -0.081566 | 8.3206e-05 | 2.0854e-05
111 | 0.98838 | -0.086721 | 0.00012689 | 3.1803e-05
112 | 0.98841 | -0.086515 | 0.00010814 | 2.7103e-05
113 | 0.98848 | -0.085988 | 7.8016e-05 | 1.9553e-05
114 | 0.98834 | -0.086995 | 0.00032297 | 8.0944e-05
115 | 0.99515 | -0.036452 | 4.4412e-05 | 1.1131e-05
116 | 0.99508 | -0.036942 | 0.00040561 | 0.00010166
117 | 0.9839 | -0.12435 | 0.00022391 | 5.6117e-05
118 | 0.98412 | -0.12269 | 0.00018308 | 4.5883e-05
119 | 0.98716 | -0.10007 | 6.2266e-05 | 1.5605e-05
120 | 0.98931 | -0.08323 | 3.8774e-05 | 9.7176e-06
121 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00013313 | -3.3365e-05 | 0.00013313 | 3.1256e-05 | 4.1026e-09 | -2.1085e-06 | 0.00020032 | 0.00019959 | 0.00020032 | 0.98893 | -0.087648 | 0.98896 | -0.087411 | 0.074191
1 | -0.00017087 | -4.0715e-05 | 0.00017087 | 4.0375e-05 | 1.0882e-09 | -3.402e-07 | 0.00025637 | 0.00025625 | 0.00025637 | 0.98896 | -0.087411 | 0.98896 | -0.08736 | 0.094952
2 | -0.00017087 | -4.0375e-05 | 0.00017088 | 3.6998e-05 | 1.0748e-08 | -3.3763e-06 | 0.00025625 | 0.00025517 | 0.00025625 | 0.98896 | -0.08736 | 0.98903 | -0.086818 | 0.094909
3 | -0.00021768 | -4.8726e-05 | 0.00021769 | 4.6347e-05 | 1.2256e-08 | -2.3792e-06 | 0.00032554 | 0.0003248 | 0.00032554 | 0.98903 | -0.086818 | 0.98909 | -0.086306 | 0.12057
4 | 0.00050449 | 0.00011443 | -0.00050433 | -0.00012017 | 1.6115e-07 | -5.7377e-06 | 0.0007549 | 0.00075682 | 0.00075682 | 0.98909 | -0.086306 | 0.98876 | -0.088947 | 0.2803
5 | -0.00072218 | -0.00016078 | 0.00072258 | 0.00015381 | 4.0236e-07 | -6.9634e-06 | 0.0010797 | 0.0010775 | 0.0010797 | 0.98909 | -0.086306 | 0.98966 | -0.081222 | 0.39988
6 | -8.4508e-05 | -2.118e-05 | 8.4512e-05 | 1.6298e-05 | 3.7939e-09 | -4.8818e-06 | 0.00012718 | 0.00012564 | 0.00012718 | 0.98871 | -0.089346 | 0.98876 | -0.088947 | 0.047106
7 | 0.00041982 | 0.00010387 | -0.0004198 | -0.00010467 | 1.5628e-08 | -7.9953e-07 | 0.00063132 | 0.0006316 | 0.0006316 | 0.98876 | -0.088947 | 0.98872 | -0.08922 | 0.23393
8 | -0.0012095 | -0.00027005 | 0.0012098 | 0.00026826 | 3.0189e-07 | -1.7878e-06 | 0.0018075 | 0.0018069 | 0.0018075 | 0.98966 | -0.081222 | 0.98991 | -0.079013 | 0.66943
9 | 0.00048693 | 0.00011623 | -0.00048685 | -0.00011941 | 8.3239e-08 | -3.178e-06 | 0.00073012 | 0.00073122 | 0.00073122 | 0.98966 | -0.081222 | 0.98948 | -0.082542 | 0.27082
10 | -0.00010125 | -2.5377e-05 | 0.00010126 | 2.4835e-05 | 6.117e-10 | -5.4183e-07 | 0.00015239 | 0.0001522 | 0.00015239 | 0.98871 | -0.089265 | 0.98872 | -0.08922 | 0.05644
11 | -0.0012098 | -0.00026826 | 0.0012099 | 0.00026779 | 7.8427e-08 | -4.6483e-07 | 0.0018069 | 0.0018067 | 0.0018069 | 0.98991 | -0.079013 | 0.98998 | -0.078436 | 0.66921
12 | 0.00033003 | 8.0109e-05 | -0.00033003 | -8.0315e-05 | 2.4717e-09 | -2.0632e-07 | 0.00049541 | 0.00049548 | 0.00049548 | 0.98948 | -0.082542 | 0.98947 | -0.082599 | 0.18351
13 | -0.0013428 | -0.00030111 | 0.0013432 | 0.00029921 | 4.0161e-07 | -1.9024e-06 | 0.0020064 | 0.0020058 | 0.0020064 | 0.98998 | -0.078436 | 0.99028 | -0.075806 | 0.74312
14 | 0.00033003 | 8.0315e-05 | -0.00033001 | -8.1924e-05 | 1.9296e-08 | -1.6086e-06 | 0.00049548 | 0.00049604 | 0.00049604 | 0.98947 | -0.082599 | 0.98941 | -0.083037 | 0.18372
15 | -0.0001267 | -3.168e-05 | 0.0001267 | 3.1306e-05 | 6.5902e-10 | -3.7446e-07 | 0.00019042 | 0.00019029 | 0.00019042 | 0.98993 | -0.075279 | 0.98994 | -0.075241 | 0.070526
16 | 7.712e-05 | 1.9255e-05 | -7.712e-05 | -1.9328e-05 | 4.7832e-11 | -7.3335e-08 | 0.0001159 | 0.00011592 | 0.00011592 | 0.98993 | -0.075279 | 0.98993 | -0.075284 | 0.042934
17 | -0.00035494 | -8.8508e-05 | 0.00035496 | 8.749e-05 | 1.4127e-08 | -1.0185e-06 | 0.00053337 | 0.00053301 | 0.00053337 | 0.98994 | -0.075241 | 0.98998 | -0.074947 | 0.19754
18 | -0.0052724 | -0.0012936 | 0.005277 | 0.0012939 | 4.5624e-06 | 2.5278e-07 | 0.0079151 | 0.0079146 | 0.0079151 | 0.98998 | -0.074947 | 0.99086 | -0.068434 | 2.9315
19 | 0.0049175 | 0.0012061 | -0.0049132 | -0.0012061 | 4.2483e-06 | 2.9215e-08 | 0.0073821 | 0.0073827 | 0.0073827 | 0.98998 | -0.074947 | 0.98909 | -0.081451 | 2.7343
20 | -0.0054264 | -0.0013313 | 0.0054274 | 0.0013314 | 1.0376e-06 | 7.5682e-08 | 0.008139 | 0.0081389 | 0.008139 | 0.99086 | -0.068434 | 0.99106 | -0.066994 | 3.0144
21 | 0.00049061 | 0.00012234 | -0.00049061 | -0.00012256 | 5.9793e-09 | -2.2356e-07 | 0.00073787 | 0.00073795 | 0.00073795 | 0.98909 | -0.081451 | 0.98908 | -0.081539 | 0.27332
22 | 0.0044226 | 0.0010838 | -0.0044213 | -0.0010839 | 1.3435e-06 | -1.089e-07 | 0.0066448 | 0.006645 | 0.006645 | 0.98909 | -0.081451 | 0.98878 | -0.083742 | 2.4611
23 | -0.0054769 | -0.0013438 | 0.005477 | 0.0013438 | 9.6183e-08 | 7.5483e-09 | 0.0082131 | 0.0082131 | 0.0082131 | 0.99106 | -0.066994 | 0.99107 | -0.066862 | 3.0419
24 | -0.00043131 | -0.00010592 | 0.00043136 | 0.00010365 | 4.6703e-08 | -2.2681e-06 | 0.00064839 | 0.0006476 | 0.00064839 | 0.98867 | -0.084572 | 0.98878 | -0.083742 | 0.24014
25 | 0.00043131 | 0.00010592 | -0.0004313 | -0.00010646 | 1.1224e-08 | -5.4415e-07 | 0.00064839 | 0.00064858 | 0.00064858 | 0.98867 | -0.084572 | 0.98865 | -0.084766 | 0.24021
26 | 0.0011672 | 0.00028603 | -0.0011672 | -0.00028611 | 1.3138e-08 | -8.2693e-08 | 0.0017543 | 0.0017543 | 0.0017543 | 0.98878 | -0.083742 | 0.98877 | -0.083826 | 0.64975
27 | 0.0028227 | 0.00069421 | -0.0028224 | -0.00069442 | 2.7784e-07 | -2.103e-07 | 0.0042432 | 0.0042433 | 0.0042433 | 0.98878 | -0.083742 | 0.98868 | -0.084479 | 1.5716
28 | 0.0002154 | 5.2353e-05 | -0.0002154 | -5.3757e-05 | 7.1848e-09 | -1.4047e-06 | 0.00032363 | 0.00032413 | 0.00032413 | 0.98865 | -0.084766 | 0.98861 | -0.085015 | 0.12005
29 | 8.3207e-05 | 2.046e-05 | -8.3206e-05 | -2.0853e-05 | 2.9908e-10 | -3.9289e-07 | 0.00012504 | 0.00012518 | 0.00012518 | 0.98908 | -0.081539 | 0.98908 | -0.081566 | 0.046363
30 | -0.0058164 | -0.0014266 | 0.0058191 | 0.0014269 | 2.6563e-06 | 2.9501e-07 | 0.0087063 | 0.008706 | 0.0087063 | 0.99285 | -0.053792 | 0.99332 | -0.050353 | 3.2246
31 | 0.0058164 | 0.0014266 | -0.0058123 | -0.0014262 | 4.0631e-06 | 4.5265e-07 | 0.0087063 | 0.0087067 | 0.0087067 | 0.99285 | -0.053792 | 0.99214 | -0.059053 | 3.2247
32 | -0.0060465 | -0.0014839 | 0.006047 | 0.001484 | 5.482e-07 | 7.1881e-08 | 0.0090467 | 0.0090467 | 0.0090467 | 0.99332 | -0.050353 | 0.99341 | -0.049671 | 3.3506
33 | 9.5608e-05 | 2.3134e-05 | -9.5607e-05 | -2.373e-05 | 5.9014e-10 | -5.9528e-07 | 0.00014311 | 0.00014331 | 0.00014331 | 0.99214 | -0.059053 | 0.99213 | -0.059099 | 0.053079
34 | 0.0057167 | 0.001403 | -0.0057108 | -0.0014024 | 5.9355e-06 | 6.0979e-07 | 0.0085636 | 0.0085642 | 0.0085642 | 0.99214 | -0.059053 | 0.99107 | -0.066862 | 3.1719
35 | -0.001383 | -0.00030918 | 0.0013837 | 0.00030632 | 6.4363e-07 | -2.8657e-06 | 0.0020656 | 0.0020646 | 0.0020656 | 0.99028 | -0.075806 | 0.99076 | -0.071688 | 0.76503
36 | -0.0016538 | -0.000374 | 0.0016539 | 0.00037369 | 1.0434e-07 | -3.1285e-07 | 0.0024701 | 0.00247 | 0.0024701 | 0.99076 | -0.071688 | 0.99082 | -0.071142 | 0.91485
37 | 9.5607e-05 | 2.373e-05 | -9.5607e-05 | -2.3961e-05 | 2.301e-10 | -2.3163e-07 | 0.00014331 | 0.00014339 | 0.00014339 | 0.99213 | -0.059099 | 0.99213 | -0.059117 | 0.053109
38 | 0.00016063 | 4.0033e-05 | -0.00016063 | -4.0258e-05 | 6.42e-10 | -2.255e-07 | 0.0002417 | 0.00024178 | 0.00024178 | 0.98861 | -0.085015 | 0.98861 | -0.085044 | 0.089547
39 | 0.00046596 | 0.00011547 | -0.00046594 | -0.0001162 | 1.754e-08 | -7.2561e-07 | 0.00070113 | 0.00070139 | 0.00070139 | 0.98826 | -0.087555 | 0.98822 | -0.087831 | 0.25977
40 | -0.00046596 | -0.00011547 | 0.000466 | 0.00011392 | 3.7436e-08 | -1.5507e-06 | 0.00070113 | 0.00070058 | 0.00070113 | 0.98826 | -0.087555 | 0.98835 | -0.086954 | 0.25968
41 | 0.00046594 | 0.0001162 | -0.00046593 | -0.00011677 | 1.3854e-08 | -5.727e-07 | 0.00070139 | 0.00070159 | 0.00070159 | 0.98822 | -0.087831 | 0.98819 | -0.088047 | 0.25985
42 | -0.00074525 | -0.00018391 | 0.00074527 | 0.00018354 | 2.3274e-08 | -3.7146e-07 | 0.001121 | 0.0011209 | 0.001121 | 0.98835 | -0.086954 | 0.98838 | -0.086721 | 0.41519
43 | 0.0011672 | 0.00028611 | -0.001167 | -0.0002878 | 2.6889e-07 | -1.6914e-06 | 0.0017543 | 0.0017549 | 0.0017549 | 0.98877 | -0.083826 | 0.98854 | -0.085554 | 0.64998
44 | 0.0026632 | 0.00065453 | -0.0026631 | -0.00065464 | 1.214e-07 | -1.0894e-07 | 0.0040037 | 0.0040038 | 0.0040038 | 0.98868 | -0.084479 | 0.98864 | -0.084821 | 1.4829
45 | 0.00022437 | 5.5447e-05 | -0.00022436 | -5.6186e-05 | 4.0971e-09 | -7.3964e-07 | 0.00033716 | 0.00033742 | 0.00033742 | 0.98941 | -0.083037 | 0.98939 | -0.083171 | 0.12497
46 | 0.0001146 | 2.8676e-05 | -0.0001146 | -2.872e-05 | 6.3235e-11 | -4.3795e-08 | 0.00017233 | 0.00017235 | 0.00017235 | 0.98939 | -0.083171 | 0.98939 | -0.083175 | 0.063832
47 | -0.0017189 | -0.00038685 | 0.0017198 | 0.00038452 | 8.4631e-07 | -2.3351e-06 | 0.002565 | 0.0025642 | 0.002565 | 0.99145 | -0.065868 | 0.99195 | -0.061564 | 0.95001
48 | 0.0017189 | 0.00038685 | -0.0017179 | -0.00038974 | 1.048e-06 | -2.8854e-06 | 0.002565 | 0.0025661 | 0.0025661 | 0.99145 | -0.065868 | 0.99082 | -0.071142 | 0.9504
49 | -0.0020679 | -0.00047177 | 0.0020682 | 0.00047134 | 2.409e-07 | -4.3063e-07 | 0.0030863 | 0.0030861 | 0.0030863 | 0.99195 | -0.061564 | 0.99207 | -0.06057 | 1.1431
50 | -0.0086985 | -0.0020971 | 0.0087044 | 0.0020987 | 5.9211e-06 | 1.5499e-06 | 0.013 | 0.013 | 0.013 | 0.99341 | -0.049671 | 0.99411 | -0.044383 | 4.815
51 | 0.0026514 | 0.00061316 | -0.0026511 | -0.00061347 | 3.2922e-07 | -3.1021e-07 | 0.0039541 | 0.0039542 | 0.0039542 | 0.99341 | -0.049671 | 0.99329 | -0.050706 | 1.4645
52 | -0.01592 | -0.0038417 | 0.015923 | 0.0038427 | 2.9519e-06 | 1.0251e-06 | 0.023683 | 0.023683 | 0.023683 | 0.99812 | -0.014083 | 0.99831 | -0.012645 | 8.7714
53 | 0.015565 | 0.0037526 | -0.015553 | -0.0037484 | 1.2143e-05 | 4.1963e-06 | 0.023153 | 0.023153 | 0.023153 | 0.99812 | -0.014083 | 0.99732 | -0.02015 | 8.5752
54 | -0.016076 | -0.0038811 | 0.016078 | 0.0038816 | 1.4536e-06 | 5.058e-07 | 0.023911 | 0.023911 | 0.023911 | 0.99831 | -0.012645 | 0.99841 | -0.011944 | 8.8558
55 | 0.00082972 | 0.0002062 | -0.00082967 | -0.00020675 | 4.1239e-08 | -5.4731e-07 | 0.0012373 | 0.0012375 | 0.0012375 | 0.99732 | -0.02015 | 0.99727 | -0.020514 | 0.45835
56 | 0.014723 | 0.0035422 | -0.014722 | -0.0035419 | 1.0534e-06 | 3.5931e-07 | 0.021916 | 0.021916 | 0.021916 | 0.99732 | -0.02015 | 0.99724 | -0.020708 | 8.117
57 | -0.016171 | -0.0039051 | 0.016182 | 0.003909 | 1.1114e-05 | 3.8718e-06 | 0.024051 | 0.02405 | 0.024051 | 0.99841 | -0.011944 | 0.99911 | -0.0066215 | 8.9076
58 | 0.00058225 | 0.00014473 | -0.00058221 | -0.00014591 | 4.2991e-08 | -1.175e-06 | 0.00086835 | 0.00086877 | 0.00086877 | 0.99727 | -0.020514 | 0.99719 | -0.021052 | 0.32177
59 | 0.014378 | 0.0034557 | -0.014371 | -0.0034534 | 6.692e-06 | 2.2686e-06 | 0.021403 | 0.021403 | 0.021403 | 0.99724 | -0.020708 | 0.99676 | -0.024347 | 7.9269
60 | -0.016961 | -0.0041041 | 0.016965 | 0.0041056 | 4.2309e-06 | 1.4875e-06 | 0.02521 | 0.02521 | 0.02521 | 0.99911 | -0.0066215 | 0.99937 | -0.004696 | 9.337
61 | 9.1078e-05 | 2.2822e-05 | -9.1078e-05 | -2.2826e-05 | 4.1337e-12 | -4.4939e-09 | 0.00013591 | 0.00013591 | 0.00013591 | 0.99719 | -0.021052 | 0.99719 | -0.021052 | 0.050336
62 | 0.0087269 | 0.0021046 | -0.0087044 | -0.0020987 | 2.2477e-05 | 5.874e-06 | 0.012999 | 0.013 | 0.013 | 0.99676 | -0.024347 | 0.99411 | -0.044383 | 4.8149
63 | 0.0056443 | 0.0013489 | -0.0056406 | -0.0013485 | 3.7322e-06 | 3.3228e-07 | 0.0084034 | 0.0084038 | 0.0084038 | 0.99676 | -0.024347 | 0.99608 | -0.029566 | 3.1125
64 | -0.017111 | -0.004142 | 0.017121 | 0.0041457 | 1.0421e-05 | 3.6694e-06 | 0.025426 | 0.025426 | 0.025426 | 0.99937 | -0.004696 | 1 | 0 | 9.4172
65 | 0.0022368 | 0.00054593 | -0.0022362 | -0.00054684 | 6.1323e-07 | -9.129e-07 | 0.0033363 | 0.0033367 | 0.0033367 | 0.99608 | -0.029566 | 0.9958 | -0.031647 | 1.2358
66 | 0.0034038 | 0.0008026 | -0.0034 | -0.0008042 | 3.7565e-06 | -1.6026e-06 | 0.0050675 | 0.0050685 | 0.0050685 | 0.99608 | -0.029566 | 0.99495 | -0.038463 | 1.8772
67 | -0.00017753 | -4.4494e-05 | 0.00017753 | 4.4232e-05 | 8.8678e-10 | -2.6179e-07 | 0.00026545 | 0.00026536 | 0.00026545 | 0.99517 | -0.036269 | 0.99518 | -0.036232 | 0.098316
68 | 0.00070253 | 0.0001718 | -0.00070252 | -0.00017197 | 9.1506e-09 | -1.6964e-07 | 0.0010489 | 0.001049 | 0.001049 | 0.99518 | -0.036232 | 0.99517 | -0.036331 | 0.38852
69 | -0.00088006 | -0.00021603 | 0.00088007 | 0.00021598 | 4.5896e-09 | -5.356e-08 | 0.0013143 | 0.0013143 | 0.0013143 | 0.99518 | -0.036232 | 0.99518 | -0.036193 | 0.48678
70 | 4.4413e-05 | 8.298e-06 | -4.4413e-05 | -9.2612e-06 | 1.9945e-10 | -9.6311e-07 | 6.5531e-05 | 6.5802e-05 | 6.5802e-05 | 0.99517 | -0.036331 | 0.99516 | -0.036377 | 0.024371
71 | 0.0006581 | 0.00016367 | -0.00065806 | -0.00016471 | 4.9088e-08 | -1.0372e-06 | 0.00098358 | 0.00098395 | 0.00098395 | 0.99517 | -0.036331 | 0.99509 | -0.036874 | 0.36443
72 | -0.00088007 | -0.00021598 | 0.00088029 | 0.00021337 | 2.2339e-07 | -2.6095e-06 | 0.0013143 | 0.0013134 | 0.0013143 | 0.99518 | -0.036193 | 0.99545 | -0.034262 | 0.48677
73 | 4.4413e-05 | 9.2611e-06 | -4.4412e-05 | -1.1131e-05 | 3.9226e-10 | -1.8696e-06 | 6.5802e-05 | 6.6408e-05 | 6.6408e-05 | 0.99516 | -0.036377 | 0.99515 | -0.036452 | 0.024596
74 | 0.00040561 | 0.00010144 | -0.00040561 | -0.00010166 | 3.7961e-09 | -2.1338e-07 | 0.00060646 | 0.00060654 | 0.00060654 | 0.99509 | -0.036874 | 0.99508 | -0.036942 | 0.22464
75 | -0.0011736 | -0.00028688 | 0.0011736 | 0.00028685 | 4.603e-09 | -2.9478e-08 | 0.0017518 | 0.0017518 | 0.0017518 | 0.99545 | -0.034262 | 0.99545 | -0.034232 | 0.64882
76 | 0.0005593 | 0.0001355 | -0.00055922 | -0.00013772 | 7.5211e-08 | -2.2202e-06 | 0.00083433 | 0.0008351 | 0.0008351 | 0.99557 | -0.033368 | 0.99543 | -0.034388 | 0.3093
77 | 0.0016178 | 0.00039745 | -0.0016178 | -0.00039751 | 1.8e-08 | -5.7377e-08 | 0.0024153 | 0.0024153 | 0.0024153 | 0.99557 | -0.033368 | 0.99556 | -0.033451 | 0.89455
78 | -0.0021771 | -0.00053295 | 0.0021776 | 0.00053217 | 4.9505e-07 | -7.8685e-07 | 0.0032496 | 0.0032492 | 0.0032496 | 0.99557 | -0.033368 | 0.9958 | -0.031647 | 1.2035
79 | 0.00021436 | 5.1293e-05 | -0.00021436 | -5.1429e-05 | 6.6768e-10 | -1.3591e-07 | 0.00031959 | 0.00031964 | 0.00031964 | 0.99543 | -0.034388 | 0.99543 | -0.034413 | 0.11838
80 | 0.0016178 | 0.00039751 | -0.0016177 | -0.00039779 | 8.9672e-08 | -2.8579e-07 | 0.0024153 | 0.0024154 | 0.0024154 | 0.99556 | -0.033451 | 0.9955 | -0.033867 | 0.89459
81 | -0.00078384 | -0.00019574 | 0.00078398 | 0.00019376 | 1.384e-07 | -1.9826e-06 | 0.001181 | 0.0011803 | 0.001181 | 0.98742 | -0.093647 | 0.9876 | -0.092349 | 0.4374
82 | 0.00078384 | 0.00019574 | -0.00078382 | -0.00019606 | 2.229e-08 | -3.19e-07 | 0.001181 | 0.0011811 | 0.0011811 | 0.98742 | -0.093647 | 0.9874 | -0.093853 | 0.43744
83 | 0.00065031 | 0.00016245 | -0.00065029 | -0.00016298 | 2.5137e-08 | -5.2735e-07 | 0.00097963 | 0.00097982 | 0.00097982 | 0.9876 | -0.092349 | 0.98756 | -0.09263 | 0.3629
84 | -0.0014343 | -0.00035621 | 0.0014349 | 0.00035362 | 6.4447e-07 | -2.5877e-06 | 0.0021599 | 0.0021589 | 0.0021599 | 0.9876 | -0.092349 | 0.98806 | -0.089021 | 0.79996
85 | 0.00026535 | 6.6121e-05 | -0.00026535 | -6.6502e-05 | 2.9738e-09 | -3.8018e-07 | 0.00039975 | 0.00039988 | 0.00039988 | 0.9874 | -0.093853 | 0.98738 | -0.093935 | 0.14811
86 | -0.0023537 | -0.00054291 | 0.0023538 | 0.00054277 | 1.0765e-07 | -1.3896e-07 | 0.0035144 | 0.0035143 | 0.0035144 | 0.99207 | -0.06057 | 0.99212 | -0.060187 | 1.3016
87 | -0.0024725 | -0.00057251 | 0.0024727 | 0.00057232 | 1.6741e-07 | -1.8977e-07 | 0.0036922 | 0.0036922 | 0.0036922 | 0.99212 | -0.060187 | 0.99219 | -0.059623 | 1.3675
88 | 0.00032142 | 8.0172e-05 | -0.00032142 | -8.0554e-05 | 4.1746e-09 | -3.8219e-07 | 0.00047814 | 0.00047828 | 0.00047828 | 1 | 0 | 0.99999 | -9.4262e-05 | 0.17714
89 | -0.0012235 | -0.00029936 | 0.0012236 | 0.00029902 | 5.8978e-08 | -3.4571e-07 | 0.0018264 | 0.0018263 | 0.0018264 | 0.99545 | -0.034232 | 0.9955 | -0.033867 | 0.67645
90 | 0.001523 | 0.00037474 | -0.0015228 | -0.00037564 | 2.5551e-07 | -9.0107e-07 | 0.0022908 | 0.0022912 | 0.0022912 | 0.98823 | -0.087768 | 0.98806 | -0.089021 | 0.84859
91 | -0.001778 | -0.00043864 | 0.0017782 | 0.00043827 | 1.4721e-07 | -3.6593e-07 | 0.0026748 | 0.0026746 | 0.0026748 | 0.98823 | -0.087768 | 0.98832 | -0.087151 | 0.99066
92 | -0.0020572 | -0.0005082 | 0.0020577 | 0.00050728 | 5.2254e-07 | -9.1995e-07 | 0.0030947 | 0.0030943 | 0.0030947 | 0.98832 | -0.087151 | 0.98858 | -0.08526 | 1.1462
93 | 0.00060527 | 0.0001475 | -0.00060517 | -0.00014981 | 9.4533e-08 | -2.3089e-06 | 0.00090958 | 0.0009104 | 0.0009104 | 0.98858 | -0.08526 | 0.98842 | -0.086433 | 0.33719
94 | -0.0026629 | -0.00065478 | 0.0026631 | 0.00065464 | 1.5618e-07 | -1.4013e-07 | 0.0040039 | 0.0040038 | 0.0040039 | 0.98858 | -0.08526 | 0.98864 | -0.084821 | 1.4829
95 | 0.00037996 | 9.3368e-05 | -0.00037993 | -9.4938e-05 | 2.514e-08 | -1.5705e-06 | 0.00057135 | 0.00057191 | 0.00057191 | 0.98842 | -0.086433 | 0.98835 | -0.086922 | 0.21182
96 | 0.00032297 | 8.0663e-05 | -0.00032297 | -8.0944e-05 | 3.2385e-09 | -2.8011e-07 | 0.00048616 | 0.00048626 | 0.00048626 | 0.98835 | -0.086922 | 0.98834 | -0.086995 | 0.18009
97 | 0.0010585 | 0.00026061 | -0.0010584 | -0.00026109 | 6.1593e-08 | -4.7573e-07 | 0.0015917 | 0.0015918 | 0.0015918 | 0.98854 | -0.085554 | 0.98848 | -0.085988 | 0.58957
98 | -0.0023907 | -0.00055847 | 0.0023913 | 0.00055771 | 6.1031e-07 | -7.5616e-07 | 0.0035713 | 0.0035709 | 0.0035713 | 0.99224 | -0.059768 | 0.9925 | -0.057671 | 1.3227
99 | 0.0022904 | 0.00053333 | -0.0022891 | -0.00053503 | 1.2282e-06 | -1.6984e-06 | 0.0034209 | 0.0034216 | 0.0034216 | 0.99224 | -0.059768 | 0.99169 | -0.064179 | 1.2672
100 | -0.0024923 | -0.00058304 | 0.0024924 | 0.00058299 | 3.9839e-08 | -4.4224e-08 | 0.0037224 | 0.0037224 | 0.0037224 | 0.9925 | -0.057671 | 0.99252 | -0.05754 | 1.3787
101 | 0.0020827 | 0.0004833 | -0.0020806 | -0.000487 | 2.1215e-06 | -3.7067e-06 | 0.0031119 | 0.0031134 | 0.0031134 | 0.99169 | -0.064179 | 0.99065 | -0.072572 | 1.1531
102 | -0.0028582 | -0.00067466 | 0.0028583 | 0.00067458 | 1.0731e-07 | -8.0589e-08 | 0.0042707 | 0.0042707 | 0.0042707 | 0.99252 | -0.05754 | 0.99256 | -0.057237 | 1.5817
103 | 0.0019851 | 0.00046306 | -0.0019841 | -0.00046491 | 9.4695e-07 | -1.8493e-06 | 0.0029699 | 0.0029707 | 0.0029707 | 0.99065 | -0.072572 | 0.99016 | -0.076482 | 1.1002
104 | -0.0030444 | -0.00072124 | 0.0030513 | 0.00071696 | 6.9181e-06 | -4.2813e-06 | 0.0045497 | 0.0045474 | 0.0045497 | 0.99256 | -0.057237 | 0.99489 | -0.038921 | 1.6851
105 | -0.0030827 | -0.00072483 | 0.0030829 | 0.00072472 | 1.7413e-07 | -1.0471e-07 | 0.0045944 | 0.0045943 | 0.0045944 | 0.99489 | -0.038921 | 0.99495 | -0.038463 | 1.7016
106 | -0.00040642 | -0.00010186 | 0.00040643 | 0.00010163 | 4.2384e-09 | -2.2677e-07 | 0.00061463 | 0.00061455 | 0.00061463 | 0.98394 | -0.12402 | 0.98395 | -0.12394 | 0.22764
107 | -0.00080309 | -0.00019923 | 0.00080312 | 0.00019879 | 3.2822e-08 | -4.4094e-07 | 0.0012138 | 0.0012136 | 0.0012138 | 0.98395 | -0.12394 | 0.98399 | -0.12364 | 0.44955
108 | 0.00039666 | 9.76e-05 | -0.00039665 | -9.8063e-05 | 8.2285e-09 | -4.6316e-07 | 0.00059922 | 0.00059939 | 0.00059939 | 0.98395 | -0.12394 | 0.98393 | -0.1241 | 0.222
109 | -0.001522 | -0.00037896 | 0.0015222 | 0.00037827 | 1.9767e-07 | -6.8434e-07 | 0.0023007 | 0.0023005 | 0.0023007 | 0.98399 | -0.12364 | 0.98412 | -0.12269 | 0.85212
110 | 0.00022392 | 5.4772e-05 | -0.00022391 | -5.6116e-05 | 7.5794e-09 | -1.3443e-06 | 0.00033816 | 0.00033863 | 0.00033863 | 0.98393 | -0.1241 | 0.9839 | -0.12435 | 0.12542
111 | 0.00010029 | 2.2841e-05 | -0.00010029 | -2.5135e-05 | 2.4625e-09 | -2.2936e-06 | 0.00014915 | 0.00014992 | 0.00014992 | 0.99543 | -0.034413 | 0.9954 | -0.034606 | 0.055526
112 | 0.0019006 | 0.00044396 | -0.001899 | -0.0004473 | 1.5474e-06 | -3.3403e-06 | 0.0028451 | 0.0028464 | 0.0028464 | 0.99016 | -0.076482 | 0.98933 | -0.083119 | 1.0542
113 | 0.0018152 | 0.00042629 | -0.0018152 | -0.00042635 | 2.4737e-08 | -5.9274e-08 | 0.0027203 | 0.0027203 | 0.0027203 | 0.98933 | -0.083119 | 0.98931 | -0.08323 | 1.0075
114 | 0.0025299 | 0.00058309 | -0.0025296 | -0.00058343 | 3.146e-07 | -3.3743e-07 | 0.0037726 | 0.0037728 | 0.0037728 | 0.99329 | -0.050706 | 0.99316 | -0.051748 | 1.3973
115 | 0.0025296 | 0.00058343 | -0.0025272 | -0.00058599 | 2.3872e-06 | -2.5554e-06 | 0.0037728 | 0.0037739 | 0.0037739 | 0.99316 | -0.051748 | 0.99219 | -0.059623 | 1.3978
116 | -0.00087217 | -0.00021534 | 0.00087219 | 0.00021506 | 2.4199e-08 | -2.7949e-07 | 0.0013119 | 0.0013118 | 0.0013119 | 0.98838 | -0.086721 | 0.98841 | -0.086515 | 0.4859
117 | -0.00098033 | -0.00024216 | 0.0009804 | 0.00024154 | 6.9341e-08 | -6.2845e-07 | 0.0014746 | 0.0014744 | 0.0014746 | 0.98841 | -0.086515 | 0.98848 | -0.085988 | 0.54616
118 | -0.0017053 | -0.00042416 | 0.0017104 | 0.00041042 | 5.0944e-06 | -1.3739e-05 | 0.0025773 | 0.0025718 | 0.0025773 | 0.98412 | -0.12269 | 0.98716 | -0.10007 | 0.95455
119 | -0.0017726 | -0.00042602 | 0.0017764 | 0.00041663 | 3.7431e-06 | -9.3912e-06 | 0.0026657 | 0.002662 | 0.0026657 | 0.98716 | -0.10007 | 0.98931 | -0.08323 | 0.98729

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.018543 | 0.0043013

## res_load
| p_mw | q_mvar
0 | 0.00013313 | 3.3365e-05
1 | 3.774e-05 | 9.4585e-06
2 | 4.6795e-05 | 1.1728e-05
3 | 8.4508e-05 | 2.118e-05
4 | 0.00010125 | 2.5377e-05
5 | 0.00031855 | 7.9835e-05
6 | 0.00015681 | 3.9301e-05
7 | 0.00013293 | 3.3315e-05
8 | 4.9579e-05 | 1.2426e-05
9 | 0.00022824 | 5.7203e-05
10 | 7.712e-05 | 1.9328e-05
11 | 0.0001494 | 3.7443e-05
12 | 4.9448e-05 | 1.2393e-05
13 | 0.0002159 | 5.4109e-05
14 | 0.0004074 | 0.0001021
15 | 0.00022742 | 5.6996e-05
16 | 3.9807e-05 | 9.9766e-06
17 | 0.00027008 | 6.7688e-05
18 | 9.5607e-05 | 2.3961e-05
19 | 5.4763e-05 | 1.3725e-05
20 | 0.00016063 | 4.0258e-05
21 | 0.00027925 | 6.9988e-05
22 | 0.00046593 | 0.00011677
23 | 0.00015916 | 3.9889e-05
24 | 0.00010565 | 2.6477e-05
25 | 0.00010977 | 2.751e-05
26 | 0.0001146 | 2.872e-05
27 | 0.00034816 | 8.7256e-05
28 | 6.4019e-05 | 1.6045e-05
29 | 0.00023382 | 5.8601e-05
30 | 0.00035537 | 8.9064e-05
31 | 0.00015306 | 3.8359e-05
32 | 9.3825e-05 | 2.3515e-05
33 | 0.00024743 | 6.2011e-05
34 | 0.00034396 | 8.6204e-05
35 | 0.00077849 | 0.00019511
36 | 0.00049113 | 0.00012309
37 | 0.00014549 | 3.6462e-05
38 | 9.1078e-05 | 2.2826e-05
39 | 0.00017753 | 4.4494e-05
40 | 0.00025244 | 6.3268e-05
41 | 0.00029332 | 7.3512e-05
42 | 0.00034487 | 8.6432e-05
43 | 5.8547e-05 | 1.4673e-05
44 | 0.00051847 | 0.00012994
45 | 0.00028556 | 7.1568e-05
46 | 0.00011866 | 2.9739e-05
47 | 0.00030056 | 7.5327e-05
48 | 0.00032142 | 8.0554e-05
49 | 4.9915e-05 | 1.251e-05
50 | 0.00039412 | 9.8777e-05
51 | 0.00025498 | 6.3903e-05
52 | 8.7855e-05 | 2.2018e-05
53 | 0.00027899 | 6.9922e-05
54 | 0.00065029 | 0.00016298
55 | 0.00022521 | 5.6444e-05
56 | 5.6958e-05 | 1.4275e-05
57 | 0.00010848 | 2.7187e-05
58 | 0.0001003 | 2.5138e-05
59 | 0.00010106 | 2.5327e-05
60 | 0.0002064 | 5.1729e-05
61 | 0.00036577 | 9.1671e-05
62 | 9.5531e-05 | 2.3942e-05
63 | 0.00018615 | 4.6654e-05
64 | 3.1411e-05 | 7.8722e-06
65 | 0.0003171 | 7.9473e-05
66 | 0.00040642 | 0.00010186
67 | 0.00071889 | 0.00018017
68 | 0.00017274 | 4.3292e-05
69 | 0.00026535 | 6.6502e-05
70 | 0.00011407 | 2.8588e-05
71 | 0.00010029 | 2.5135e-05
72 | 8.3582e-05 | 2.0947e-05
73 | 8.3834e-05 | 2.1011e-05
74 | 0.00012121 | 3.0379e-05
75 | 5.4531e-05 | 1.3667e-05
76 | 8.3206e-05 | 2.0854e-05
77 | 0.00012689 | 3.1803e-05
78 | 0.00010814 | 2.7103e-05
79 | 7.8016e-05 | 1.9553e-05
80 | 0.00032297 | 8.0944e-05
81 | 4.4412e-05 | 1.1131e-05
82 | 0.00040561 | 0.00010166
83 | 0.00022391 | 5.6117e-05
84 | 0.00018308 | 4.5883e-05
85 | 6.2266e-05 | 1.5605e-05
86 | 3.8774e-05 | 9.7176e-06

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1