## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1010-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1010-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1010-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1010-5_0_3_node_131 | 0.4 | n |  | TRUE
4 | bus_LV_1010-5_0_3_node_125 | 0.4 | n |  | TRUE
5 | bus_LV_1010-5_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1010-5_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1010-5_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1010-5_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1010-5_0_3_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_1010-5_0_3_node_12 | 0.4 | n |  | TRUE
11 | bus_LV_1010-5_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1010-5_0_3_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1010-5_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1010-5_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1010-5_0_3_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_1010-5_0_3_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_1010-5_0_3_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1010-5_0_3_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_1010-5_0_3_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_1010-5_0_3_node_76 | 0.4 | n |  | TRUE
21 | bus_LV_1010-5_0_3_node_18 | 0.4 | n |  | TRUE
22 | bus_LV_1010-5_0_3_node_100 | 0.4 | n |  | TRUE
23 | bus_LV_1010-5_0_3_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1010-5_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1010-5_0_3_node_75 | 0.4 | n |  | TRUE
26 | bus_LV_1010-5_0_3_node_99 | 0.4 | n |  | TRUE
27 | bus_LV_1010-5_0_3_node_74 | 0.4 | n |  | TRUE
28 | bus_LV_1010-5_0_3_node_73 | 0.4 | n |  | TRUE
29 | bus_LV_1010-5_0_3_node_77 | 0.4 | n |  | TRUE
30 | bus_LV_1010-5_0_3_node_78 | 0.4 | n |  | TRUE
31 | bus_LV_1010-5_0_3_node_101 | 0.4 | n |  | TRUE
32 | bus_LV_1010-5_0_3_node_98 | 0.4 | n |  | TRUE
33 | bus_LV_1010-5_0_3_node_108 | 0.4 | n |  | TRUE
34 | bus_LV_1010-5_0_3_node_110 | 0.4 | n |  | TRUE
35 | bus_LV_1010-5_0_3_node_52 | 0.4 | n |  | TRUE
36 | bus_LV_1010-5_0_3_node_87 | 0.4 | n |  | TRUE
37 | bus_LV_1010-5_0_3_node_84 | 0.4 | n |  | TRUE
38 | bus_LV_1010-5_0_3_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1010-5_0_3_node_24 | 0.4 | n |  | TRUE
40 | bus_LV_1010-5_0_3_node_25 | 0.4 | n |  | TRUE
41 | bus_LV_1010-5_0_3_node_26 | 0.4 | n |  | TRUE
42 | bus_LV_1010-5_0_3_node_83 | 0.4 | n |  | TRUE
43 | bus_LV_1010-5_0_3_node_51 | 0.4 | n |  | TRUE
44 | bus_LV_1010-5_0_3_node_114 | 0.4 | n |  | TRUE
45 | bus_LV_1010-5_0_3_node_49 | 0.4 | n |  | TRUE
46 | bus_LV_1010-5_0_3_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_1010-5_0_3_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_1010-5_0_3_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_1010-5_0_3_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_1010-5_0_3_node_31 | 0.4 | n |  | TRUE
51 | bus_LV_1010-5_0_3_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_1010-5_0_3_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_1010-5_0_3_node_135 | 0.4 | n |  | TRUE
54 | bus_LV_1010-5_0_3_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_1010-5_0_3_node_136 | 0.4 | n |  | TRUE
56 | bus_LV_1010-5_0_3_node_126 | 0.4 | n |  | TRUE
57 | bus_LV_1010-5_0_3_node_79 | 0.4 | n |  | TRUE
58 | bus_LV_1010-5_0_3_node_35 | 0.4 | n |  | TRUE
59 | bus_LV_1010-5_0_3_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_1010-5_0_3_node_37 | 0.4 | n |  | TRUE
61 | bus_LV_1010-5_0_3_node_38 | 0.4 | n |  | TRUE
62 | bus_LV_1010-5_0_3_node_39 | 0.4 | n |  | TRUE
63 | bus_LV_1010-5_0_3_node_62 | 0.4 | n |  | TRUE
64 | bus_LV_1010-5_0_3_node_111 | 0.4 | n |  | TRUE
65 | bus_LV_1010-5_0_3_node_60 | 0.4 | n |  | TRUE
66 | bus_LV_1010-5_0_3_node_40 | 0.4 | n |  | TRUE
67 | bus_LV_1010-5_0_3_node_41 | 0.4 | n |  | TRUE
68 | bus_LV_1010-5_0_3_node_42 | 0.4 | n |  | TRUE
69 | bus_LV_1010-5_0_3_node_43 | 0.4 | n |  | TRUE
70 | bus_LV_1010-5_0_3_node_44 | 0.4 | n |  | TRUE
71 | bus_LV_1010-5_0_3_node_46 | 0.4 | n |  | TRUE
72 | bus_LV_1010-5_0_3_node_45 | 0.4 | n |  | TRUE
73 | bus_LV_1010-5_0_3_node_70 | 0.4 | n |  | TRUE
74 | bus_LV_1010-5_0_3_node_95 | 0.4 | n |  | TRUE
75 | bus_LV_1010-5_0_3_node_86 | 0.4 | n |  | TRUE
76 | bus_LV_1010-5_0_3_node_67 | 0.4 | n |  | TRUE
77 | bus_LV_1010-5_0_3_node_47 | 0.4 | n |  | TRUE
78 | bus_LV_1010-5_0_3_node_48 | 0.4 | n |  | TRUE
79 | bus_LV_1010-5_0_3_node_50 | 0.4 | n |  | TRUE
80 | bus_LV_1010-5_0_3_node_105 | 0.4 | n |  | TRUE
81 | bus_LV_1010-5_0_3_node_106 | 0.4 | n |  | TRUE
82 | bus_LV_1010-5_0_3_node_53 | 0.4 | n |  | TRUE
83 | bus_LV_1010-5_0_3_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_1010-5_0_3_node_55 | 0.4 | n |  | TRUE
85 | bus_LV_1010-5_0_3_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_1010-5_0_3_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_1010-5_0_3_node_58 | 0.4 | n |  | TRUE
88 | bus_LV_1010-5_0_3_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_1010-5_0_3_node_61 | 0.4 | n |  | TRUE
90 | bus_LV_1010-5_0_3_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_1010-5_0_3_node_132 | 0.4 | n |  | TRUE
92 | bus_LV_1010-5_0_3_node_119 | 0.4 | n |  | TRUE
93 | bus_LV_1010-5_0_3_node_112 | 0.4 | n |  | TRUE
94 | bus_LV_1010-5_0_3_node_118 | 0.4 | n |  | TRUE
95 | bus_LV_1010-5_0_3_node_64 | 0.4 | n |  | TRUE
96 | bus_LV_1010-5_0_3_node_65 | 0.4 | n |  | TRUE
97 | bus_LV_1010-5_0_3_node_66 | 0.4 | n |  | TRUE
98 | bus_LV_1010-5_0_3_node_68 | 0.4 | n |  | TRUE
99 | bus_LV_1010-5_0_3_node_69 | 0.4 | n |  | TRUE
100 | bus_LV_1010-5_0_3_node_71 | 0.4 | n |  | TRUE
101 | bus_LV_1010-5_0_3_node_72 | 0.4 | n |  | TRUE
102 | bus_LV_1010-5_0_3_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_1010-5_0_3_node_121 | 0.4 | n |  | TRUE
104 | bus_LV_1010-5_0_3_node_88 | 0.4 | n |  | TRUE
105 | bus_LV_1010-5_0_3_node_81 | 0.4 | n |  | TRUE
106 | bus_LV_1010-5_0_3_node_89 | 0.4 | n |  | TRUE
107 | bus_LV_1010-5_0_3_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_1010-5_0_3_node_104 | 0.4 | n |  | TRUE
109 | bus_LV_1010-5_0_3_node_127 | 0.4 | n |  | TRUE
110 | bus_LV_1010-5_0_3_node_128 | 0.4 | n |  | TRUE
111 | bus_LV_1010-5_0_3_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_1010-5_0_3_node_115 | 0.4 | n |  | TRUE
113 | bus_LV_1010-5_0_3_node_139 | 0.4 | n |  | TRUE
114 | bus_LV_1010-5_0_3_node_140 | 0.4 | n |  | TRUE
115 | bus_LV_1010-5_0_3_node_138 | 0.4 | n |  | TRUE
116 | bus_LV_1010-5_0_3_node_141 | 0.4 | n |  | TRUE
117 | bus_LV_1010-5_0_3_node_129 | 0.4 | n |  | TRUE
118 | bus_LV_1010-5_0_3_node_122 | 0.4 | n |  | TRUE
119 | bus_LV_1010-5_0_3_node_97 | 0.4 | n |  | TRUE
120 | bus_LV_1010-5_0_3_node_123 | 0.4 | n |  | TRUE
121 | bus_LV_1010-5_0_3_node_90 | 0.4 | n |  | TRUE
122 | bus_LV_1010-5_0_3_node_91 | 0.4 | n |  | TRUE
123 | bus_LV_1010-5_0_3_node_92 | 0.4 | n |  | TRUE
124 | bus_LV_1010-5_0_3_node_93 | 0.4 | n |  | TRUE
125 | bus_LV_1010-5_0_3_node_94 | 0.4 | n |  | TRUE
126 | bus_LV_1010-5_0_3_node_96 | 0.4 | n |  | TRUE
127 | bus_LV_1010-5_0_3_node_102 | 0.4 | n |  | TRUE
128 | bus_LV_1010-5_0_3_node_103 | 0.4 | n |  | TRUE
129 | bus_LV_1010-5_0_3_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_1010-5_0_3_node_134 | 0.4 | n |  | TRUE
131 | bus_LV_1010-5_0_3_node_133 | 0.4 | n |  | TRUE
132 | bus_LV_1010-5_0_3_node_107 | 0.4 | n |  | TRUE
133 | bus_LV_1010-5_0_3_node_109 | 0.4 | n |  | TRUE
134 | bus_LV_1010-5_0_3_node_116 | 0.4 | n |  | TRUE
135 | bus_LV_1010-5_0_3_node_117 | 0.4 | n |  | TRUE
136 | bus_LV_1010-5_0_3_node_124 | 0.4 | n |  | TRUE
137 | bus_LV_1010-5_0_3_node_130 | 0.4 | n |  | TRUE
138 | bus_LV_1010-5_0_3_node_137 | 0.4 | n |  | TRUE
139 | bus_MV_126_0_node_69 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1010-5_0_3_load_0 | 0 | 0.00080685 | 0.00020222 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1010-5_0_3_load_2 | 2 | 0.00047047 | 0.00011791 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1010-5_0_3_load_131 | 3 | 0.0010734 | 0.00026902 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1010-5_0_3_load_4 | 5 | 0.0097808 | 0.0024513 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1010-5_0_3_load_5 | 6 | 0.0032809 | 0.00082227 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1010-5_0_3_load_6 | 7 | 0.0058905 | 0.0014763 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1010-5_0_3_load_9 | 9 | 0.017967 | 0.0045029 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1010-5_0_3_load_15 | 12 | 0.001634 | 0.00040952 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1010-5_0_3_load_16 | 16 | 0.002454 | 0.00061504 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1010-5_0_3_load_21 | 18 | 0.02156 | 0.0054035 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1010-5_0_3_load_22 | 19 | 0.0020238 | 0.00050721 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1010-5_0_3_load_19 | 23 | 0.0012406 | 0.00031094 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1010-5_0_3_load_20 | 24 | 0.0013284 | 0.00033293 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1010-5_0_3_load_99 | 26 | 0.0011273 | 0.00028252 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1010-5_0_3_load_74 | 27 | 0.0017843 | 0.00044718 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1010-5_0_3_load_73 | 28 | 0.00046943 | 0.00011765 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1010-5_0_3_load_77 | 29 | 0.00072595 | 0.00018194 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1010-5_0_3_load_78 | 30 | 0.00078087 | 0.0001957 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1010-5_0_3_load_101 | 31 | 0.00090226 | 0.00022613 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1010-5_0_3_load_108 | 33 | 0.00097476 | 0.0002443 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1010-5_0_3_load_110 | 34 | 0.0009229 | 0.0002313 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1010-5_0_3_load_87 | 36 | 0.0033172 | 0.00083137 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1010-5_0_3_load_84 | 37 | 0.0025197 | 0.00063148 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1010-5_0_3_load_24 | 39 | 0.00069703 | 0.00017469 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1010-5_0_3_load_25 | 40 | 0.00026839 | 6.7264e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1010-5_0_3_load_26 | 41 | 0.00079808 | 0.00020002 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1010-5_0_3_load_51 | 43 | 0.00077538 | 0.00019433 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1010-5_0_3_load_114 | 44 | 0.00059381 | 0.00014882 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1010-5_0_3_load_49 | 45 | 0.00091146 | 0.00022843 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1010-5_0_3_load_27 | 46 | 0.00076674 | 0.00019216 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1010-5_0_3_load_29 | 48 | 0.00031479 | 7.8895e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1010-5_0_3_load_31 | 50 | 0.00028826 | 7.2245e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1010-5_0_3_load_32 | 52 | 0.00063459 | 0.00015904 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1010-5_0_3_load_34 | 54 | 0.0011695 | 0.00029309 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1010-5_0_3_load_136 | 55 | 0.00035979 | 9.0172e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1010-5_0_3_load_126 | 56 | 0.0011218 | 0.00028114 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1010-5_0_3_load_79 | 57 | 0.00091695 | 0.00022981 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1010-5_0_3_load_35 | 58 | 0.00087546 | 0.00021941 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1010-5_0_3_load_37 | 60 | 0.0013256 | 0.00033223 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1010-5_0_3_load_38 | 61 | 0.0023292 | 0.00058374 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1010-5_0_3_load_39 | 62 | 0.0012919 | 0.00032379 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1010-5_0_3_load_111 | 64 | 0.0013643 | 0.00034192 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1010-5_0_3_load_40 | 66 | 0.0052883 | 0.0013254 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1010-5_0_3_load_41 | 67 | 0.0033391 | 0.00083686 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1010-5_0_3_load_42 | 68 | 0.0016297 | 0.00040845 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1010-5_0_3_load_43 | 69 | 0.0017262 | 0.00043264 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1010-5_0_3_load_44 | 70 | 0.0054178 | 0.0013578 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1010-5_0_3_load_46 | 71 | 0.0016303 | 0.0004086 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1010-5_0_3_load_45 | 72 | 0.0026859 | 0.00067314 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1010-5_0_3_load_95 | 74 | 0.0011069 | 0.00027742 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1010-5_0_3_load_67 | 76 | 0.0029464 | 0.00073844 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1010-5_0_3_load_47 | 77 | 0.00092641 | 0.00023218 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1010-5_0_3_load_48 | 78 | 0.0010698 | 0.00026812 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1010-5_0_3_load_50 | 79 | 0.00087924 | 0.00022036 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1010-5_0_3_load_105 | 80 | 0.00099182 | 0.00024857 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1010-5_0_3_load_106 | 81 | 0.0015184 | 0.00038054 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1010-5_0_3_load_53 | 82 | 0.0011373 | 0.00028502 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1010-5_0_3_load_54 | 83 | 0.0027129 | 0.00067991 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1010-5_0_3_load_55 | 84 | 0.0011363 | 0.00028478 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1010-5_0_3_load_56 | 85 | 0.0036658 | 0.00091873 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1010-5_0_3_load_57 | 86 | 0.0012288 | 0.00030797 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1010-5_0_3_load_58 | 87 | 0.0006226 | 0.00015604 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1010-5_0_3_load_61 | 89 | 0.001036 | 0.00025964 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1010-5_0_3_load_63 | 90 | 0.0019136 | 0.00047959 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1010-5_0_3_load_132 | 91 | 0.003183 | 0.00079773 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1010-5_0_3_load_119 | 92 | 0.0019821 | 0.00049676 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1010-5_0_3_load_112 | 93 | 0.0013643 | 0.00034192 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1010-5_0_3_load_118 | 94 | 0.0020357 | 0.00051019 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1010-5_0_3_load_64 | 95 | 0.0037932 | 0.00095066 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1010-5_0_3_load_65 | 96 | 0.0040923 | 0.0010256 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1010-5_0_3_load_68 | 98 | 0.0016066 | 0.00040265 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1010-5_0_3_load_69 | 99 | 0.0033931 | 0.0008504 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1010-5_0_3_load_71 | 100 | 0.0024897 | 0.00062397 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1010-5_0_3_load_72 | 101 | 0.0014751 | 0.00036969 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1010-5_0_3_load_80 | 102 | 0.0020779 | 0.00052077 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1010-5_0_3_load_121 | 103 | 0.0035722 | 0.00089528 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1010-5_0_3_load_88 | 104 | 0.0016241 | 0.00040703 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1010-5_0_3_load_81 | 105 | 0.0019936 | 0.00049964 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1010-5_0_3_load_89 | 106 | 0.0008265 | 0.00020714 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1010-5_0_3_load_82 | 107 | 0.0021368 | 0.00053554 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1010-5_0_3_load_127 | 109 | 0.00085177 | 0.00021347 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1010-5_0_3_load_128 | 110 | 0.0011628 | 0.00029143 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1010-5_0_3_load_115 | 112 | 0.00050646 | 0.00012693 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1010-5_0_3_load_140 | 114 | 0.00075087 | 0.00018818 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1010-5_0_3_load_141 | 116 | 0.002138 | 0.00053583 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1010-5_0_3_load_129 | 117 | 0.0016252 | 0.00040731 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1010-5_0_3_load_122 | 118 | 0.00069011 | 0.00017296 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1010-5_0_3_load_97 | 119 | 0.001927 | 0.00048295 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1010-5_0_3_load_123 | 120 | 0.00064303 | 0.00016116 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1010-5_0_3_load_90 | 121 | 0.0025743 | 0.00064517 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1010-5_0_3_load_91 | 122 | 0.0013745 | 0.00034449 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1010-5_0_3_load_93 | 124 | 0.00088025 | 0.00022061 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1010-5_0_3_load_94 | 125 | 0.0024346 | 0.00061016 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1010-5_0_3_load_96 | 126 | 0.00088025 | 0.00022061 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1010-5_0_3_load_102 | 127 | 0.0028988 | 0.00072651 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1010-5_0_3_load_103 | 128 | 0.0022044 | 0.00055246 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1010-5_0_3_load_120 | 129 | 0.0010757 | 0.0002696 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1010-5_0_3_load_134 | 130 | 0.0015487 | 0.00038815 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1010-5_0_3_load_133 | 131 | 0.0013269 | 0.00033256 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1010-5_0_3_load_107 | 132 | 0.0015699 | 0.00039346 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1010-5_0_3_load_109 | 133 | 0.0016511 | 0.00041381 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1010-5_0_3_load_116 | 134 | 0.0028578 | 0.00071622 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1010-5_0_3_load_117 | 135 | 0.0028106 | 0.0007044 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1010-5_0_3_load_124 | 136 | 0.0013477 | 0.00033776 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1010-5_0_3_load_130 | 137 | 0.0017791 | 0.00044588 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1010-5_0_3_load_137 | 138 | 0.00048652 | 0.00012193 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1010-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.055246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1010-5_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.11955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1010-5_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.26987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1010-5_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.058346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1010-5_0_3_line_4 | NAYY 4x150 SE | 4 | 137 | 0.033881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1010-5_0_3_line_5 | NAYY 4x150 SE | 4 | 136 | 0.036243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1010-5_0_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.025852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1010-5_0_3_line_7 | NAYY 4x150 SE | 5 | 7 | 0.003859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1010-5_0_3_line_8 | NAYY 4x150 SE | 6 | 8 | 0.056526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1010-5_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.067818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
10 | LV_1010-5_0_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.071098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1010-5_0_3_line_11 | NAYY 4x150 SE | 9 | 13 | 0.015073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1010-5_0_3_line_12 | NAYY 4x150 SE | 10 | 17 | 0.009589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1010-5_0_3_line_13 | NAYY 4x150 SE | 10 | 11 | 0.031166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1010-5_0_3_line_14 | NAYY 4x150 SE | 11 | 12 | 0.018801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1010-5_0_3_line_15 | NAYY 4x150 SE | 12 | 20 | 0.015097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1010-5_0_3_line_16 | NAYY 4x150 SE | 13 | 14 | 0.011647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1010-5_0_3_line_17 | NAYY 4x150 SE | 14 | 15 | 0.019788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1010-5_0_3_line_18 | NAYY 4x150 SE | 14 | 16 | 0.036898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1010-5_0_3_line_19 | NAYY 4x150 SE | 15 | 18 | 0.024264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1010-5_0_3_line_20 | NAYY 4x150 SE | 15 | 19 | 0.15306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1010-5_0_3_line_21 | NAYY 4x150 SE | 17 | 23 | 0.055474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1010-5_0_3_line_22 | NAYY 4x150 SE | 17 | 24 | 0.031716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1010-5_0_3_line_23 | NAYY 4x150 SE | 18 | 25 | 0.054022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1010-5_0_3_line_24 | NAYY 4x150 SE | 19 | 26 | 0.079629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1010-5_0_3_line_25 | NAYY 4x150 SE | 20 | 29 | 0.017177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1010-5_0_3_line_26 | NAYY 4x150 SE | 20 | 30 | 0.015846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1010-5_0_3_line_27 | NAYY 4x150 SE | 21 | 22 | 0.075741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1010-5_0_3_line_28 | NAYY 4x150 SE | 22 | 31 | 0.079787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1010-5_0_3_line_29 | NAYY 4x150 SE | 22 | 32 | 0.005229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1010-5_0_3_line_30 | NAYY 4x150 SE | 24 | 28 | 0.012425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1010-5_0_3_line_31 | NAYY 4x150 SE | 25 | 36 | 0.069784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1010-5_0_3_line_32 | NAYY 4x150 SE | 25 | 37 | 0.041461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1010-5_0_3_line_33 | NAYY 4x150 SE | 26 | 32 | 0.018297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1010-5_0_3_line_34 | NAYY 4x150 SE | 27 | 28 | 0.030263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1010-5_0_3_line_35 | NAYY 4x150 SE | 30 | 57 | 0.019153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1010-5_0_3_line_36 | NAYY 4x150 SE | 31 | 129 | 0.006535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1010-5_0_3_line_37 | NAYY 4x150 SE | 32 | 74 | 0.012588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1010-5_0_3_line_38 | NAYY 4x150 SE | 32 | 72 | 0.015806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1010-5_0_3_line_39 | NAYY 4x150 SE | 33 | 34 | 0.030915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1010-5_0_3_line_40 | NAYY 4x150 SE | 33 | 35 | 0.006765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1010-5_0_3_line_41 | NAYY 4x150 SE | 35 | 80 | 0.024861 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1010-5_0_3_line_42 | NAYY 4x150 SE | 35 | 79 | 0.04091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1010-5_0_3_line_43 | NAYY 4x150 SE | 36 | 106 | 0.020435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1010-5_0_3_line_44 | NAYY 4x150 SE | 38 | 39 | 0.052726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1010-5_0_3_line_45 | NAYY 4x150 SE | 38 | 40 | 0.10229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1010-5_0_3_line_46 | NAYY 4x150 SE | 38 | 41 | 0.019994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1010-5_0_3_line_47 | NAYY 4x150 SE | 39 | 42 | 0.053243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1010-5_0_3_line_48 | NAYY 4x150 SE | 41 | 43 | 0.010564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1010-5_0_3_line_49 | NAYY 4x150 SE | 42 | 44 | 0.063279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1010-5_0_3_line_50 | NAYY 4x150 SE | 43 | 45 | 0.011261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1010-5_0_3_line_51 | NAYY 4x150 SE | 44 | 111 | 0.24946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1010-5_0_3_line_52 | NAYY 4x150 SE | 45 | 77 | 0.025636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1010-5_0_3_line_53 | NAYY 4x150 SE | 46 | 47 | 0.16583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1010-5_0_3_line_54 | NAYY 4x150 SE | 47 | 48 | 0.094259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1010-5_0_3_line_55 | NAYY 4x150 SE | 47 | 49 | 0.18704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1010-5_0_3_line_56 | NAYY 4x150 SE | 48 | 50 | 0.1133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1010-5_0_3_line_57 | NAYY 4x150 SE | 49 | 51 | 0.193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1010-5_0_3_line_58 | NAYY 4x150 SE | 49 | 52 | 0.01756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1010-5_0_3_line_59 | NAYY 4x150 SE | 50 | 53 | 0.019155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1010-5_0_3_line_60 | NAYY 4x150 SE | 51 | 54 | 0.24658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1010-5_0_3_line_61 | NAYY 4x150 SE | 53 | 55 | 0.13577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1010-5_0_3_line_62 | NAYY 4x150 SE | 54 | 56 | 0.062429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1010-5_0_3_line_63 | NAYY 4x150 SE | 56 | 57 | 0.14469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
64 | LV_1010-5_0_3_line_64 | NAYY 4x150 SE | 58 | 59 | 0.012229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1010-5_0_3_line_65 | NAYY 4x150 SE | 59 | 60 | 0.078676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1010-5_0_3_line_66 | NAYY 4x150 SE | 59 | 61 | 0.064017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1010-5_0_3_line_67 | NAYY 4x150 SE | 60 | 62 | 0.028364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1010-5_0_3_line_68 | NAYY 4x150 SE | 62 | 63 | 0.011228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1010-5_0_3_line_69 | NAYY 4x150 SE | 63 | 64 | 0.022813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1010-5_0_3_line_70 | NAYY 4x150 SE | 63 | 65 | 0.052734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1010-5_0_3_line_71 | NAYY 4x150 SE | 64 | 93 | 0.0067537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1010-5_0_3_line_72 | NAYY 4x150 SE | 65 | 89 | 0.012754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1010-5_0_3_line_73 | NAYY 4x150 SE | 65 | 90 | 0.016841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1010-5_0_3_line_74 | NAYY 4x150 SE | 65 | 88 | 0.008447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1010-5_0_3_line_75 | NAYY 4x150 SE | 66 | 67 | 0.034338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1010-5_0_3_line_76 | NAYY 4x150 SE | 66 | 68 | 0.030182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1010-5_0_3_line_77 | NAYY 4x150 SE | 67 | 69 | 0.0078165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1010-5_0_3_line_78 | NAYY 4x150 SE | 68 | 70 | 0.0048654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1010-5_0_3_line_79 | NAYY 4x150 SE | 70 | 71 | 0.0016257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1010-5_0_3_line_80 | NAYY 4x150 SE | 71 | 73 | 0.015826 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1010-5_0_3_line_81 | NAYY 4x150 SE | 73 | 75 | 0.042642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1010-5_0_3_line_82 | NAYY 4x150 SE | 73 | 76 | 0.03138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1010-5_0_3_line_83 | NAYY 4x150 SE | 74 | 123 | 0.016563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1010-5_0_3_line_84 | NAYY 4x150 SE | 75 | 104 | 0.0097796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1010-5_0_3_line_85 | NAYY 4x150 SE | 76 | 96 | 0.017006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1010-5_0_3_line_86 | NAYY 4x150 SE | 77 | 78 | 0.014477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1010-5_0_3_line_87 | NAYY 4x150 SE | 78 | 79 | 0.010054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1010-5_0_3_line_88 | NAYY 4x150 SE | 80 | 81 | 0.00053648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1010-5_0_3_line_89 | NAYY 4x150 SE | 81 | 132 | 0.020308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1010-5_0_3_line_90 | NAYY 4x150 SE | 82 | 83 | 0.023778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1010-5_0_3_line_91 | NAYY 4x150 SE | 82 | 84 | 0.016433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1010-5_0_3_line_92 | NAYY 4x150 SE | 83 | 85 | 0.0055353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1010-5_0_3_line_93 | NAYY 4x150 SE | 84 | 86 | 0.020162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1010-5_0_3_line_94 | NAYY 4x150 SE | 84 | 87 | 0.02182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1010-5_0_3_line_95 | NAYY 4x150 SE | 85 | 88 | 0.032216 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1010-5_0_3_line_96 | NAYY 4x150 SE | 89 | 91 | 0.021245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1010-5_0_3_line_97 | NAYY 4x150 SE | 90 | 92 | 0.0078037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1010-5_0_3_line_98 | NAYY 4x150 SE | 92 | 94 | 0.014078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1010-5_0_3_line_99 | NAYY 4x150 SE | 93 | 129 | 0.027803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1010-5_0_3_line_100 | NAYY 4x150 SE | 94 | 135 | 0.013405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1010-5_0_3_line_101 | NAYY 4x150 SE | 95 | 96 | 0.006457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1010-5_0_3_line_102 | NAYY 4x150 SE | 95 | 97 | 0.020688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1010-5_0_3_line_103 | NAYY 4x150 SE | 97 | 98 | 0.017437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1010-5_0_3_line_104 | NAYY 4x150 SE | 97 | 99 | 0.0099427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1010-5_0_3_line_105 | NAYY 4x150 SE | 98 | 100 | 0.020029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1010-5_0_3_line_106 | NAYY 4x150 SE | 99 | 101 | 0.0014037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1010-5_0_3_line_107 | NAYY 4x150 SE | 100 | 102 | 0.0040478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1010-5_0_3_line_108 | NAYY 4x150 SE | 101 | 103 | 0.014713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1010-5_0_3_line_109 | NAYY 4x150 SE | 102 | 105 | 0.019339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1010-5_0_3_line_110 | NAYY 4x150 SE | 104 | 117 | 0.0070803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1010-5_0_3_line_111 | NAYY 4x150 SE | 105 | 107 | 0.0040734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1010-5_0_3_line_112 | NAYY 4x150 SE | 106 | 118 | 0.022081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1010-5_0_3_line_113 | NAYY 4x150 SE | 107 | 108 | 0.033691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1010-5_0_3_line_114 | NAYY 4x150 SE | 108 | 109 | 0.0098084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1010-5_0_3_line_115 | NAYY 4x150 SE | 108 | 110 | 0.0096421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1010-5_0_3_line_116 | NAYY 4x150 SE | 109 | 130 | 0.0069459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1010-5_0_3_line_117 | NAYY 4x150 SE | 110 | 131 | 0.011287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1010-5_0_3_line_118 | NAYY 4x150 SE | 111 | 112 | 0.079829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1010-5_0_3_line_119 | NAYY 4x150 SE | 112 | 113 | 0.013129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1010-5_0_3_line_120 | NAYY 4x150 SE | 112 | 114 | 0.0070911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1010-5_0_3_line_121 | NAYY 4x150 SE | 113 | 115 | 0.098444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1010-5_0_3_line_122 | NAYY 4x150 SE | 114 | 116 | 0.024726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
123 | LV_1010-5_0_3_line_123 | NAYY 4x150 SE | 115 | 138 | 0.11476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1010-5_0_3_line_124 | NAYY 4x150 SE | 117 | 119 | 0.037144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1010-5_0_3_line_125 | NAYY 4x150 SE | 118 | 120 | 0.020753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1010-5_0_3_line_126 | NAYY 4x150 SE | 119 | 125 | 0.0026485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1010-5_0_3_line_127 | NAYY 4x150 SE | 120 | 136 | 0.021122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1010-5_0_3_line_128 | NAYY 4x150 SE | 121 | 122 | 0.0020654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1010-5_0_3_line_129 | NAYY 4x150 SE | 121 | 123 | 0.035095 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1010-5_0_3_line_130 | NAYY 4x150 SE | 122 | 124 | 0.0014915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_1010-5_0_3_line_131 | NAYY 4x150 SE | 123 | 125 | 0.014242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_1010-5_0_3_line_132 | NAYY 4x150 SE | 124 | 126 | 0.0067556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_1010-5_0_3_line_133 | NAYY 4x150 SE | 126 | 127 | 0.023092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_1010-5_0_3_line_134 | NAYY 4x150 SE | 127 | 128 | 0.023587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_1010-5_0_3_line_135 | NAYY 4x150 SE | 132 | 133 | 0.00283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_1010-5_0_3_line_136 | NAYY 4x150 SE | 133 | 134 | 0.025469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_1010-5_0_3_line_137 | NAYY 4x150 SE | 134 | 135 | 0.02974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1010-5_0_3_trafo_18 | 0.25 MVA 20/0.4 kV | 139 | 21 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2634410.7196 | 1189190.8069 | 2634401.9563 | 1189190.8677 | 2634392.3117 | 1189203.6192 | 2634383.6364 | 1189229.5278 | 2634381.458 | 1189231.8328
1 | 2634410.7196 | 1189190.8069 | 2634421.8794 | 1189181.1657 | 2634441.6711 | 1189166.4826 | 2634500.8212 | 1189136.4177 | 2634504.074 | 1189134.4242 | 2634504.9274 | 1189126.625 | 2634504.9087 | 1189124.483
2 | 2634637.6528 | 1188889.5209 | 2634504.9087 | 1189124.483
3 | 2634625.7556 | 1188835.2651 | 2634629.1887 | 1188843.0336 | 2634635.5894 | 1188867.8283 | 2634641.111 | 1188879.7666 | 2634641.138 | 1188885.6477 | 2634637.6528 | 1188889.5209
4 | 2634654.9808 | 1188840.8481 | 2634647.1763 | 1188835.9226 | 2634637.9954 | 1188831.5894 | 2634631.5146 | 1188829.8955 | 2634625.7556 | 1188835.2651
5 | 2634625.7556 | 1188835.2651 | 2634619.1129 | 1188825.944 | 2634617.645 | 1188822.5781 | 2634617.3027 | 1188819.7747 | 2634618.091 | 1188816.6664 | 2634620.0515 | 1188813.9763 | 2634624.2578 | 1188812.0106 | 2634628.9134 | 1188811.4706 | 2634631.3271 | 1188811.7997
6 | 2634922.9457 | 1188895.4844 | 2634914.953 | 1188883.546 | 2634905.1059 | 1188889.4564
7 | 2634925.0926 | 1188898.691 | 2634922.9457 | 1188895.4844
8 | 2634881.8401 | 1188934.0026 | 2634881.1684 | 1188913.1431 | 2634882.4966 | 1188906.4027 | 2634886.0064 | 1188900.9202 | 2634905.1059 | 1188889.4564
9 | 2634881.8401 | 1188934.0026 | 2634877.147 | 1188929.2061 | 2634865.9246 | 1188917.9459 | 2634854.9431 | 1188905.8978 | 2634850.3551 | 1188900.068 | 2634846.0473 | 1188891.9497 | 2634839.7359 | 1188883.4195 | 2634838.5584 | 1188882.211
10 | 2634881.8401 | 1188934.0026 | 2634881.1094 | 1188939.0011 | 2634892.2104 | 1188950.1383 | 2634906.8975 | 1188963.6311 | 2634926.606 | 1188981.8668 | 2634924.0293 | 1188984.2753
11 | 2634826.947 | 1188872.6394 | 2634832.3144 | 1188876.9285 | 2634836.3696 | 1188879.9648 | 2634838.5584 | 1188882.211
12 | 2634916.967 | 1188990.7821 | 2634923.0171 | 1188985.2254 | 2634924.0293 | 1188984.2753
13 | 2634924.0293 | 1188984.2753 | 2634926.606 | 1188981.8668 | 2634944.6439 | 1188997.5136 | 2634947.2756 | 1188994.8275
14 | 2634947.2756 | 1188994.8275 | 2634952.3856 | 1188989.61 | 2634959.7814 | 1188984.7617 | 2634962.2309 | 1188983.738
15 | 2634976.583 | 1188979.6236 | 2634970.8522 | 1188980.1349 | 2634962.2309 | 1188983.738
16 | 2634818.306 | 1188880.449 | 2634822.431 | 1188876.7154 | 2634826.947 | 1188872.6394
17 | 2634818.306 | 1188880.449 | 2634815.647 | 1188877.3207 | 2634812.4704 | 1188872.7221 | 2634809.7947 | 1188868.5376 | 2634807.1815 | 1188864.1089
18 | 2634818.306 | 1188880.449 | 2634819.4573 | 1188881.812 | 2634823.0582 | 1188885.6016 | 2634827.3751 | 1188889.5399 | 2634831.4484 | 1188893.3878 | 2634833.5752 | 1188896.2017 | 2634835.3902 | 1188900.181 | 2634837.9839 | 1188904.0315 | 2634842.1838 | 1188908.1693
19 | 2634807.1815 | 1188864.1089 | 2634788.8212 | 1188879.9719
20 | 2634807.1815 | 1188864.1089 | 2634803.7573 | 1188858.7973 | 2634798.5314 | 1188852.4636 | 2634789.4416 | 1188841.6717 | 2634780.042 | 1188830.3555 | 2634763.7845 | 1188811.3622 | 2634744.5473 | 1188787.9492 | 2634729.6189 | 1188769.8863 | 2634710.114 | 1188745.8266
21 | 2634916.967 | 1188990.7821 | 2634907.8082 | 1188985.3591 | 2634890.2402 | 1188980.6766 | 2634888.1217 | 1188980.3752 | 2634865.32 | 1188978.586 | 2634863.6854 | 1188978.6827
22 | 2634916.967 | 1188990.7821 | 2634899.0688 | 1189002.2062 | 2634897.9124 | 1189008.2694 | 2634900.2591 | 1189011.8851
23 | 2634742.627 | 1188904.723 | 2634747.4687 | 1188904.9845 | 2634759.2921 | 1188902.0848 | 2634763.7748 | 1188899.7985 | 2634778.0526 | 1188889.2756 | 2634788.8212 | 1188879.9719
24 | 2634661.3439 | 1188682.9494 | 2634671.5724 | 1188698.0229 | 2634685.0936 | 1188715.4882 | 2634705.6956 | 1188740.3764 | 2634710.114 | 1188745.8266
25 | 2634976.583 | 1188979.6236 | 2634974.2264 | 1188962.6118
26 | 2634976.583 | 1188979.6236 | 2634983.7484 | 1188978.9873 | 2634991.5045 | 1188975.1527
27 | 2634655.1842 | 1188665.8887 | 2634671.7809 | 1188692.3099 | 2634699.5556 | 1188727.2116
28 | 2634655.1842 | 1188665.8887 | 2634640.0614 | 1188637.8084 | 2634619.3073 | 1188594.6458
29 | 2634655.1842 | 1188665.8887 | 2634652.8274 | 1188667.198 | 2634650.6007 | 1188668.4302
30 | 2634900.2591 | 1189011.8851 | 2634907.0239 | 1189022.3076
31 | 2634742.627 | 1188904.723 | 2634739.2541 | 1188903.7251 | 2634734.7244 | 1188900.9529 | 2634729.075 | 1188895.3061 | 2634722.5269 | 1188886.808 | 2634712.6497 | 1188871.0535 | 2634705.6635 | 1188857.8504 | 2634702.1061 | 1188849.9029
32 | 2634742.627 | 1188904.723 | 2634731.6852 | 1188881.8584 | 2634731.3743 | 1188865.748
33 | 2634650.6007 | 1188668.4302 | 2634653.997 | 1188674.6643 | 2634654.5404 | 1188675.6569 | 2634657.214 | 1188677.5956 | 2634660.8862 | 1188682.2749 | 2634661.3439 | 1188682.9494
34 | 2634922.7356 | 1189048.1623 | 2634913.5066 | 1189032.2953 | 2634907.0239 | 1189022.3076
35 | 2635003.973 | 1188960.6274 | 2635001.6432 | 1188962.972 | 2634991.5045 | 1188975.1527 | 2634991.5045 | 1188975.1527
36 | 2634619.3073 | 1188594.6458 | 2634616.4754 | 1188588.7563
37 | 2634650.6007 | 1188668.4302 | 2634639.5978 | 1188674.5449
38 | 2634650.6007 | 1188668.4302 | 2634647.1139 | 1188662.04 | 2634646.1402 | 1188660.2667 | 2634644.1194 | 1188654.9077 | 2634643.77 | 1188654.215
39 | 2634710.4542 | 1188645.6976 | 2634736.9002 | 1188629.5643
40 | 2634711.3092 | 1188638.9878 | 2634710.4542 | 1188645.6976
41 | 2634711.3092 | 1188638.9878 | 2634698.785 | 1188617.5118
42 | 2634711.3092 | 1188638.9878 | 2634717.6526 | 1188602.5605 | 2634718.8943 | 1188598.8269
43 | 2634690.9217 | 1188833.3204 | 2634692.1487 | 1188834.0705 | 2634695.6094 | 1188837.0477 | 2634698.3447 | 1188841.4992 | 2634702.1061 | 1188849.9029
44 | 2634748.2319 | 1188512.934 | 2634749.7374 | 1188503.2264 | 2634768.4195 | 1188473.9079 | 2634771.612 | 1188466.4233
45 | 2634748.2319 | 1188512.934 | 2634755.973 | 1188511.756 | 2634781.4937 | 1188514.55 | 2634807.4262 | 1188517.3464 | 2634814.9706 | 1188519.836 | 2634837.1469 | 1188535.0285 | 2634843.9946 | 1188538.9219
46 | 2634748.2319 | 1188512.934 | 2634744.0884 | 1188517.179 | 2634737.2863 | 1188528.7457 | 2634737.0991 | 1188529.3615
47 | 2634789.9116 | 1188416.5018 | 2634782.2671 | 1188435.1785 | 2634776.2528 | 1188455.5435 | 2634771.612 | 1188466.4233
48 | 2634737.0991 | 1188529.3615 | 2634734.0266 | 1188539.4688
49 | 2634789.9116 | 1188416.5018 | 2634769.7872 | 1188356.5084
50 | 2634734.0266 | 1188539.4688 | 2634730.7514 | 1188550.2426
51 | 2634906.2804 | 1188193.5918 | 2634898.9618 | 1188202.0538 | 2634887.6825 | 1188206.8796 | 2634864.3145 | 1188214.0809 | 2634852.0001 | 1188221.1464 | 2634853.1831 | 1188228.913 | 2634858.471 | 1188233.8353 | 2634862.5315 | 1188239.9733 | 2634861.0797 | 1188243.0221 | 2634855.7454 | 1188246.0593 | 2634845.1121 | 1188244.7746 | 2634834.0632 | 1188244.0989 | 2634829.7535 | 1188246.7198 | 2634815.2375 | 1188280.8982 | 2634798.3219 | 1188304.0569 | 2634775.4657 | 1188329.6158 | 2634768.2242 | 1188343.2366 | 2634769.7872 | 1188356.5084
52 | 2634726.306 | 1188575.4686 | 2634729.9927 | 1188552.7386 | 2634730.7514 | 1188550.2426
53 | 2635305.4805 | 1188502.9064 | 2635324.7267 | 1188507.7445 | 2635339.3763 | 1188512.111 | 2635350.0275 | 1188516.7541 | 2635368.163 | 1188522.3863 | 2635423.0659 | 1188524.934 | 2635442.4728 | 1188530.963 | 2635451.332 | 1188539.3644 | 2635453.457 | 1188545.0244 | 2635459.3863 | 1188547.8068
54 | 2635305.4805 | 1188502.9064 | 2635293.0111 | 1188481.9217 | 2635275.2686 | 1188461.3284 | 2635266.6524 | 1188451.7393 | 2635248.1251 | 1188429.6851 | 2635247.5885 | 1188428.8748
55 | 2635305.4805 | 1188502.9064 | 2635326.0501 | 1188540.7367 | 2635359.0331 | 1188590.847 | 2635385.4531 | 1188619.496 | 2635392.032 | 1188629.14 | 2635400.842 | 1188651.0149 | 2635398.9546 | 1188655.4728 | 2635398.4528 | 1188660.3614
56 | 2635187.0537 | 1188333.2644 | 2635202.666 | 1188354.1108 | 2635233.4502 | 1188407.5203 | 2635247.5885 | 1188428.8748
57 | 2635398.4528 | 1188660.3614 | 2635388.5748 | 1188670.7976 | 2635385.7321 | 1188680.7417 | 2635370.134 | 1188697.592 | 2635362.0448 | 1188697.0218 | 2635348.5896 | 1188717.8203 | 2635340.169 | 1188721.7172 | 2635334.5621 | 1188727.0537 | 2635325.7524 | 1188730.9594 | 2635318.3734 | 1188727.6697 | 2635310.3028 | 1188730.4348 | 2635294.4062 | 1188741.0358 | 2635276.2028 | 1188741.8624 | 2635261.3093 | 1188755.6933 | 2635251.0313 | 1188761.5916
58 | 2635398.4528 | 1188660.3614 | 2635399.971 | 1188666.7516 | 2635402.273 | 1188670.8785 | 2635405.969 | 1188674.002 | 2635407.3125 | 1188674.4849
59 | 2635175.5712 | 1188317.9324 | 2635187.0537 | 1188333.2644
60 | 2635251.0313 | 1188761.5916 | 2635243.0943 | 1188753.3183 | 2635236.4532 | 1188730.8894 | 2635226.9426 | 1188725.6085 | 2635210.2873 | 1188731.6472 | 2635202.8499 | 1188739.5856 | 2635191.6832 | 1188753.9388 | 2635173.15 | 1188765.4919 | 2635167.5534 | 1188775.5867 | 2635162.2943 | 1188780.1583 | 2635150.5802 | 1188782.5464 | 2635136.9287 | 1188800.565 | 2635132.4675 | 1188804.3631 | 2635128.903 | 1188804.8091 | 2635132.9674 | 1188788.0461 | 2635125.7713 | 1188782.1564 | 2635123.82 | 1188779.3434 | 2635120.5279 | 1188776.2558 | 2635117.0786 | 1188777.8698 | 2635108.8352 | 1188788.0159 | 2635092.2354 | 1188795.8049
61 | 2635175.5712 | 1188317.9324 | 2635233.5237 | 1188299.018 | 2635242.4326 | 1188299.0704 | 2635248.8231 | 1188301.9429 | 2635254.8491 | 1188307.1255 | 2635259.0787 | 1188314.2542 | 2635260.8207 | 1188321.5462 | 2635261.4736 | 1188331.1329 | 2635264.974 | 1188341.6369 | 2635269.207 | 1188349.466 | 2635272.9183 | 1188353.9347
62 | 2635092.2354 | 1188795.8049 | 2635086.0666 | 1188798.6994 | 2635073.4888 | 1188815.7461 | 2635078.2616 | 1188831.6826 | 2635081.3688 | 1188849.2033
63 | 2635003.973 | 1188960.6274 | 2635011.1105 | 1188953.4444 | 2635069.9239 | 1188900.971 | 2635079.1516 | 1188889.4077 | 2635083.5427 | 1188874.1363 | 2635082.4258 | 1188855.164 | 2635081.3688 | 1188849.2033
64 | 2634531.5909 | 1188435.6409 | 2634523.5591 | 1188426.4189
65 | 2634531.5909 | 1188435.6409 | 2634544.5545 | 1188452.1022 | 2634555.1104 | 1188466.7709 | 2634563.4813 | 1188480.7155 | 2634570.0916 | 1188493.0936 | 2634574.3099 | 1188501.4428
66 | 2634565.0429 | 1188381.8937 | 2634559.4942 | 1188397.0254 | 2634555.3677 | 1188406.2622 | 2634550.0377 | 1188413.9022 | 2634531.5909 | 1188435.6409
67 | 2634574.3099 | 1188501.4428 | 2634575.6798 | 1188504.154 | 2634586.7198 | 1188526.9471
68 | 2634591.6144 | 1188537.0524 | 2634586.7198 | 1188526.9471
69 | 2634591.6144 | 1188537.0524 | 2634601.5004 | 1188557.6124
70 | 2634632.7859 | 1188504.3392 | 2634627.2244 | 1188511.1219 | 2634604.3669 | 1188527.9211 | 2634591.6144 | 1188537.0524
71 | 2634604.427 | 1188563.699 | 2634601.5004 | 1188557.6124
72 | 2634632.7859 | 1188504.3392 | 2634631.6884 | 1188498.9078 | 2634627.9521 | 1188492.7376
73 | 2634632.7859 | 1188504.3392 | 2634641.2699 | 1188518.8873
74 | 2634640.3213 | 1188500.4807 | 2634632.7859 | 1188504.3392
75 | 2634585.8413 | 1188623.8384 | 2634596.1241 | 1188617.3215 | 2634601.7551 | 1188628.8713 | 2634605.5807 | 1188637.3646
76 | 2634585.8413 | 1188623.8384 | 2634579.7493 | 1188627.6993 | 2634559.8563 | 1188634.466 | 2634557.9347 | 1188634.8358
77 | 2634613.3239 | 1188638.4321 | 2634613.3239 | 1188638.4321 | 2634605.5807 | 1188637.3646 | 2634605.5807 | 1188637.3646
78 | 2634557.9347 | 1188634.8358 | 2634553.157 | 1188635.7553
79 | 2634551.5606 | 1188636.0625 | 2634553.157 | 1188635.7553
80 | 2634535.9436 | 1188638.5971 | 2634545.5544 | 1188637.2184 | 2634551.5606 | 1188636.0625
81 | 2634535.9436 | 1188638.5971 | 2634540.4137 | 1188653.0639 | 2634545.7678 | 1188661.0658 | 2634557.5122 | 1188674.574
82 | 2634535.9436 | 1188638.5971 | 2634534.0288 | 1188630.7152 | 2634534.3322 | 1188619.0996 | 2634537.1407 | 1188607.7938
83 | 2634625.12 | 1188682.5906 | 2634639.5978 | 1188674.5449
84 | 2634557.5122 | 1188674.574 | 2634566.0941 | 1188679.2635
85 | 2634541.1657 | 1188591.2758 | 2634541.1022 | 1188591.8462 | 2634537.1407 | 1188607.7938
86 | 2634726.306 | 1188575.4686 | 2634725.9664 | 1188577.5619 | 2634722.0671 | 1188589.2868
87 | 2634722.0671 | 1188589.2868 | 2634718.8943 | 1188598.8269
88 | 2634698.785 | 1188617.5118 | 2634698.5147 | 1188617.0484
89 | 2634688.284 | 1188599.5052 | 2634698.5147 | 1188617.0484
90 | 2634685.2635 | 1188475.2937 | 2634686.1426 | 1188484.1924 | 2634675.8153 | 1188494.8442
91 | 2634676.1132 | 1188461.6445 | 2634685.2635 | 1188475.2937 | 2634685.2635 | 1188475.2937
92 | 2634675.8153 | 1188494.8442 | 2634671.9623 | 1188498.8182
93 | 2634676.1132 | 1188461.6445 | 2634659.4461 | 1188459.1468 | 2634656.7461 | 1188461.0597
94 | 2634676.1132 | 1188461.6445 | 2634670.6123 | 1188456.61 | 2634664.5642 | 1188449.9159 | 2634660.6186 | 1188446.316
95 | 2634640.3213 | 1188500.4807 | 2634653.4878 | 1188498.9226 | 2634662.2017 | 1188500.9963 | 2634671.9623 | 1188498.8182
96 | 2634616.9477 | 1188474.5651 | 2634627.9521 | 1188492.7376
97 | 2634645.2012 | 1188525.6285 | 2634641.2699 | 1188518.8873
98 | 2634645.2012 | 1188525.6285 | 2634652.293 | 1188537.7892
99 | 2634604.427 | 1188563.699 | 2634616.4754 | 1188588.7563
100 | 2634652.293 | 1188537.7892 | 2634659.046 | 1188549.369
101 | 2634541.8802 | 1188584.8585 | 2634541.1657 | 1188591.2758
102 | 2634539.3605 | 1188564.5104 | 2634542.4455 | 1188579.7808 | 2634541.8802 | 1188584.8585
103 | 2634539.3605 | 1188564.5104 | 2634532.1207 | 1188548.6476
104 | 2634539.3605 | 1188564.5104 | 2634548.2565 | 1188560.0697
105 | 2634523.8049 | 1188530.4271 | 2634532.1207 | 1188548.6476
106 | 2634549.5124 | 1188559.4428 | 2634548.2565 | 1188560.0697
107 | 2634523.8049 | 1188530.4271 | 2634522.1242 | 1188526.7446
108 | 2634562.6761 | 1188552.8718 | 2634549.5124 | 1188559.4428
109 | 2634522.1242 | 1188526.7446 | 2634514.0947 | 1188509.1515
110 | 2634566.0941 | 1188679.2635 | 2634568.0808 | 1188680.3491 | 2634572.5888 | 1188682.0447
111 | 2634514.0947 | 1188509.1515 | 2634512.4034 | 1188505.4458
112 | 2634671.577 | 1188822.7383 | 2634680.528 | 1188826.9661 | 2634690.9217 | 1188833.3204
113 | 2634526.2191 | 1188481.001 | 2634514.6089 | 1188490.4614 | 2634508.2216 | 1188496.2834 | 2634512.4034 | 1188505.4458
114 | 2634526.2191 | 1188481.001 | 2634522.1266 | 1188472.0872
115 | 2634526.2191 | 1188481.001 | 2634531.8985 | 1188488.793
116 | 2634519.2284 | 1188465.7748 | 2634522.1266 | 1188472.0872
117 | 2634538.5469 | 1188497.9144 | 2634531.8985 | 1188488.793
118 | 2634871.8559 | 1188124.0765 | 2634890.3546 | 1188143.5946 | 2634895.9327 | 1188153.7102 | 2634900.579 | 1188164.0428 | 2634903.0952 | 1188176.0083 | 2634906.2804 | 1188193.5918
119 | 2634871.8559 | 1188124.0765 | 2634877.7587 | 1188119.0526 | 2634882.4578 | 1188116.3896
120 | 2634871.8559 | 1188124.0765 | 2634868.4861 | 1188130.3158
121 | 2634882.4578 | 1188116.3896 | 2634893.1335 | 1188110.4374 | 2634905.6208 | 1188106.4746 | 2634916.6697 | 1188104.5601 | 2634925.0133 | 1188103.4971 | 2634933.822 | 1188103.7819 | 2634944.6923 | 1188105.0348 | 2634956.8267 | 1188107.9515 | 2634974.7007 | 1188119.4619
122 | 2634873.1668 | 1188154.4226 | 2634873.1316 | 1188149.9756 | 2634868.6996 | 1188134.2747 | 2634868.4861 | 1188130.3158
123 | 2634974.7007 | 1188119.4619 | 2634988.0795 | 1188099.9851 | 2634992.3291 | 1188092.0167 | 2634995.7939 | 1188083.8881 | 2634998.7006 | 1188075.9897 | 2635000.2488 | 1188069.5064 | 2635001.3192 | 1188062.5423 | 2635000.3915 | 1188054.2102 | 2634996.9823 | 1188042.3617 | 2634995.4372 | 1188036.5495 | 2634994.6966 | 1188027.5182 | 2634993.6088 | 1188023.0872 | 2634988.6383 | 1188013.52
124 | 2634608.8926 | 1188687.2772 | 2634608.8926 | 1188687.2772 | 2634592.484 | 1188687.6716 | 2634580.9582 | 1188685.1927 | 2634572.5888 | 1188682.0447
125 | 2634671.577 | 1188822.7383 | 2634667.4223 | 1188820.7759 | 2634652.4633 | 1188815.8979 | 2634652.0493 | 1188815.8058
126 | 2634608.8926 | 1188687.2772 | 2634611.4371 | 1188686.5423
127 | 2634652.0493 | 1188815.8058 | 2634638.3636 | 1188812.7592 | 2634631.3271 | 1188811.7997
128 | 2634644.053 | 1188714.5662 | 2634643.0007 | 1188712.789
129 | 2634625.12 | 1188682.5906 | 2634643.0007 | 1188712.789
130 | 2634644.813 | 1188715.8496 | 2634644.053 | 1188714.5662
131 | 2634625.12 | 1188682.5906 | 2634611.4371 | 1188686.5423
132 | 2634644.813 | 1188715.8496 | 2634648.2549 | 1188721.6626
133 | 2634660.0202 | 1188741.5328 | 2634648.2549 | 1188721.6626
134 | 2634645.0567 | 1188752.6878 | 2634662.472 | 1188745.6736 | 2634660.0202 | 1188741.5328
135 | 2634688.284 | 1188599.5052 | 2634686.8584 | 1188597.0605
136 | 2634674.0279 | 1188575.0594 | 2634686.8584 | 1188597.0605
137 | 2634674.0279 | 1188575.0594 | 2634659.046 | 1188549.369

## bus_geodata
| x | y | coords
0 | 2634381.458 | 1189231.8328
1 | 2634410.7196 | 1189190.8069
2 | 2634504.9087 | 1189124.483
3 | 2634637.6528 | 1188889.5209
4 | 2634625.7556 | 1188835.2651
5 | 2634922.9457 | 1188895.4844
6 | 2634905.1059 | 1188889.4564
7 | 2634925.0926 | 1188898.691
8 | 2634881.8401 | 1188934.0026
9 | 2634838.5584 | 1188882.211
10 | 2634924.0293 | 1188984.2753
11 | 2634947.2756 | 1188994.8275
12 | 2634962.2309 | 1188983.738
13 | 2634826.947 | 1188872.6394
14 | 2634818.306 | 1188880.449
15 | 2634807.1815 | 1188864.1089
16 | 2634842.1838 | 1188908.1693
17 | 2634916.967 | 1188990.7821
18 | 2634788.8212 | 1188879.9719
19 | 2634710.114 | 1188745.8266
20 | 2634976.583 | 1188979.6236
21 | 2634699.5556 | 1188727.2116
22 | 2634655.1842 | 1188665.8887
23 | 2634863.6854 | 1188978.6827
24 | 2634900.2591 | 1189011.8851
25 | 2634742.627 | 1188904.723
26 | 2634661.3439 | 1188682.9494
27 | 2634922.7356 | 1189048.1623
28 | 2634907.0239 | 1189022.3076
29 | 2634974.2264 | 1188962.6118
30 | 2634991.5045 | 1188975.1527
31 | 2634619.3073 | 1188594.6458
32 | 2634650.6007 | 1188668.4302
33 | 2634710.4542 | 1188645.6976
34 | 2634736.9002 | 1188629.5643
35 | 2634711.3092 | 1188638.9878
36 | 2634702.1061 | 1188849.9029
37 | 2634731.3743 | 1188865.748
38 | 2634748.2319 | 1188512.934
39 | 2634771.612 | 1188466.4233
40 | 2634843.9946 | 1188538.9219
41 | 2634737.0991 | 1188529.3615
42 | 2634789.9116 | 1188416.5018
43 | 2634734.0266 | 1188539.4688
44 | 2634769.7872 | 1188356.5084
45 | 2634730.7514 | 1188550.2426
46 | 2635459.3863 | 1188547.8068
47 | 2635305.4805 | 1188502.9064
48 | 2635247.5885 | 1188428.8748
49 | 2635398.4528 | 1188660.3614
50 | 2635187.0537 | 1188333.2644
51 | 2635251.0313 | 1188761.5916
52 | 2635407.3125 | 1188674.4849
53 | 2635175.5712 | 1188317.9324
54 | 2635092.2354 | 1188795.8049
55 | 2635272.9183 | 1188353.9347
56 | 2635081.3688 | 1188849.2033
57 | 2635003.973 | 1188960.6274
58 | 2634523.5591 | 1188426.4189
59 | 2634531.5909 | 1188435.6409
60 | 2634574.3099 | 1188501.4428
61 | 2634565.0429 | 1188381.8937
62 | 2634586.7198 | 1188526.9471
63 | 2634591.6144 | 1188537.0524
64 | 2634601.5004 | 1188557.6124
65 | 2634632.7859 | 1188504.3392
66 | 2634585.8413 | 1188623.8384
67 | 2634605.5807 | 1188637.3646
68 | 2634557.9347 | 1188634.8358
69 | 2634613.3239 | 1188638.4321
70 | 2634553.157 | 1188635.7553
71 | 2634551.5606 | 1188636.0625
72 | 2634643.77 | 1188654.215
73 | 2634535.9436 | 1188638.5971
74 | 2634639.5978 | 1188674.5449
75 | 2634557.5122 | 1188674.574
76 | 2634537.1407 | 1188607.7938
77 | 2634726.306 | 1188575.4686
78 | 2634722.0671 | 1188589.2868
79 | 2634718.8943 | 1188598.827
80 | 2634698.785 | 1188617.5118
81 | 2634698.5147 | 1188617.0484
82 | 2634685.2635 | 1188475.2937
83 | 2634675.8153 | 1188494.8442
84 | 2634676.1132 | 1188461.6445
85 | 2634671.9623 | 1188498.8182
86 | 2634656.7461 | 1188461.0597
87 | 2634660.6186 | 1188446.316
88 | 2634640.3213 | 1188500.4807
89 | 2634627.9521 | 1188492.7376
90 | 2634641.2699 | 1188518.8873
91 | 2634616.9477 | 1188474.5651
92 | 2634645.2012 | 1188525.6285
93 | 2634604.427 | 1188563.699
94 | 2634652.293 | 1188537.7892
95 | 2634541.8802 | 1188584.8585
96 | 2634541.1657 | 1188591.2758
97 | 2634539.3605 | 1188564.5104
98 | 2634532.1207 | 1188548.6476
99 | 2634548.2565 | 1188560.0697
100 | 2634523.8049 | 1188530.4271
101 | 2634549.5124 | 1188559.4428
102 | 2634522.1242 | 1188526.7446
103 | 2634562.6761 | 1188552.8718
104 | 2634566.0941 | 1188679.2635
105 | 2634514.0947 | 1188509.1515
106 | 2634690.9217 | 1188833.3204
107 | 2634512.4034 | 1188505.4458
108 | 2634526.2191 | 1188481.001
109 | 2634522.1266 | 1188472.0872
110 | 2634531.8985 | 1188488.793
111 | 2634906.2804 | 1188193.5918
112 | 2634871.8559 | 1188124.0765
113 | 2634882.4578 | 1188116.3896
114 | 2634868.4861 | 1188130.3158
115 | 2634974.7007 | 1188119.4619
116 | 2634873.1668 | 1188154.4226
117 | 2634572.5888 | 1188682.0447
118 | 2634671.577 | 1188822.7383
119 | 2634608.8926 | 1188687.2772
120 | 2634652.0494 | 1188815.8058
121 | 2634643.0007 | 1188712.789
122 | 2634644.053 | 1188714.5662
123 | 2634625.12 | 1188682.5906
124 | 2634644.813 | 1188715.8496
125 | 2634611.4371 | 1188686.5423
126 | 2634648.2549 | 1188721.6626
127 | 2634660.0202 | 1188741.5328
128 | 2634645.0567 | 1188752.6878
129 | 2634616.4754 | 1188588.7563
130 | 2634519.2284 | 1188465.7748
131 | 2634538.5469 | 1188497.9144
132 | 2634688.284 | 1188599.5052
133 | 2634686.8584 | 1188597.0605
134 | 2634674.0279 | 1188575.0594
135 | 2634659.046 | 1188549.369
136 | 2634631.3271 | 1188811.7997
137 | 2634654.9808 | 1188840.8481
138 | 2634988.6383 | 1188013.52
139 | 2634655.1842 | 1188665.8887

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97524 | -0.17468 | 0.00080685 | 0.00020222
1 | 0.9753 | -0.17421 | 0 | 0
2 | 0.97544 | -0.17318 | 0.00047047 | 0.00011791
3 | 0.97595 | -0.16949 | 0.0010734 | 0.00026902
4 | 0.97615 | -0.16802 | 0 | 0
5 | 0.97619 | -0.1676 | 0.0097808 | 0.0024513
6 | 0.97678 | -0.16336 | 0.0032809 | 0.00082227
7 | 0.97616 | -0.16784 | 0.0058905 | 0.0014763
8 | 0.97835 | -0.15217 | 0 | 0
9 | 0.97942 | -0.14447 | 0.017967 | 0.0045029
10 | 0.97788 | -0.15557 | 0 | 0
11 | 0.97775 | -0.15653 | 0 | 0
12 | 0.97767 | -0.15711 | 0.001634 | 0.00040952
13 | 0.97979 | -0.14182 | 0 | 0
14 | 0.98008 | -0.13978 | 0 | 0
15 | 0.98058 | -0.13614 | 0 | 0
16 | 0.97994 | -0.14072 | 0.002454 | 0.00061504
17 | 0.97781 | -0.15605 | 0 | 0
18 | 0.97935 | -0.14499 | 0.02156 | 0.0054035
19 | 0.98712 | -0.089689 | 0.0020238 | 0.00050721
20 | 0.97762 | -0.15749 | 0 | 0
21 | 1 | 0 | -0.22754 | -0.057361
22 | 0.99183 | -0.056583 | 0 | 0
23 | 0.97771 | -0.15677 | 0.0012406 | 0.00031094
24 | 0.97765 | -0.15724 | 0.0013284 | 0.00033293
25 | 0.97828 | -0.15261 | 0 | 0
26 | 0.9906 | -0.065213 | 0.0011273 | 0.00028252
27 | 0.97753 | -0.1581 | 0.0017843 | 0.00044718
28 | 0.97761 | -0.15753 | 0.00046943 | 0.00011765
29 | 0.9776 | -0.15762 | 0.00072595 | 0.00018194
30 | 0.97757 | -0.15785 | 0.00078087 | 0.0001957
31 | 0.98862 | -0.079096 | 0.00090226 | 0.00022613
32 | 0.99141 | -0.059542 | 0 | 0
33 | 0.97562 | -0.17166 | 0.00097476 | 0.0002443
34 | 0.97558 | -0.17196 | 0.0009229 | 0.0002313
35 | 0.97564 | -0.17152 | 0 | 0
36 | 0.97717 | -0.16064 | 0.0033172 | 0.00083137
37 | 0.97813 | -0.1537 | 0.0025197 | 0.00063148
38 | 0.97399 | -0.18347 | 0 | 0
39 | 0.97359 | -0.18638 | 0.00069703 | 0.00017469
40 | 0.97395 | -0.18377 | 0.00026839 | 6.7264e-05
41 | 0.97414 | -0.18231 | 0.00079808 | 0.00020002
42 | 0.97324 | -0.18893 | 0 | 0
43 | 0.97424 | -0.18161 | 0.00077538 | 0.00019433
44 | 0.97282 | -0.19195 | 0.00059381 | 0.00014882
45 | 0.97436 | -0.18077 | 0.00091146 | 0.00022843
46 | 0.97453 | -0.18039 | 0.00076674 | 0.00019216
47 | 0.97471 | -0.17904 | 0 | 0
48 | 0.97458 | -0.18002 | 0.00031479 | 7.8895e-05
49 | 0.97519 | -0.17553 | 0 | 0
50 | 0.97447 | -0.18081 | 0.00028826 | 7.2245e-05
51 | 0.97585 | -0.17058 | 0 | 0
52 | 0.97517 | -0.17564 | 0.00063459 | 0.00015904
53 | 0.97446 | -0.18089 | 0 | 0
54 | 0.9767 | -0.16423 | 0.0011695 | 0.00029309
55 | 0.97439 | -0.18141 | 0.00035979 | 9.0172e-05
56 | 0.97702 | -0.16185 | 0.0011218 | 0.00028114
57 | 0.97752 | -0.15823 | 0.00091695 | 0.00022981
58 | 0.98309 | -0.11822 | 0.00087546 | 0.00021941
59 | 0.98311 | -0.11811 | 0 | 0
60 | 0.98347 | -0.1155 | 0.0013256 | 0.00033223
61 | 0.98289 | -0.11965 | 0.0023292 | 0.00058374
62 | 0.98366 | -0.11417 | 0.0012919 | 0.00032379
63 | 0.98375 | -0.11349 | 0 | 0
64 | 0.98543 | -0.10158 | 0.0013643 | 0.00034192
65 | 0.98031 | -0.13798 | 0 | 0
66 | 0.97808 | -0.15367 | 0.0052883 | 0.0013254
67 | 0.97783 | -0.15548 | 0.0033391 | 0.00083686
68 | 0.97854 | -0.15041 | 0.0016297 | 0.00040845
69 | 0.97781 | -0.15562 | 0.0017262 | 0.00043264
70 | 0.97862 | -0.1498 | 0.0054178 | 0.0013578
71 | 0.97867 | -0.1495 | 0.0016303 | 0.0004086
72 | 0.99135 | -0.059973 | 0.0026859 | 0.00067314
73 | 0.9791 | -0.14637 | 0 | 0
74 | 0.99007 | -0.068896 | 0.0011069 | 0.00027742
75 | 0.98243 | -0.12268 | 0 | 0
76 | 0.97752 | -0.15765 | 0.0029464 | 0.00073844
77 | 0.97466 | -0.17861 | 0.00092641 | 0.00023218
78 | 0.97484 | -0.17725 | 0.0010698 | 0.00026812
79 | 0.97499 | -0.1762 | 0.00087924 | 0.00022036
80 | 0.9761 | -0.16819 | 0.00099182 | 0.00024857
81 | 0.97611 | -0.16811 | 0.0015184 | 0.00038054
82 | 0.97949 | -0.14384 | 0.0011373 | 0.00028502
83 | 0.97963 | -0.14282 | 0.0027129 | 0.00067991
84 | 0.97942 | -0.14435 | 0.0011363 | 0.00028478
85 | 0.97969 | -0.14243 | 0.0036658 | 0.00091873
86 | 0.97938 | -0.14461 | 0.0012288 | 0.00030797
87 | 0.9794 | -0.14449 | 0.0006226 | 0.00015604
88 | 0.98018 | -0.13891 | 0 | 0
89 | 0.98023 | -0.13854 | 0.001036 | 0.00025964
90 | 0.97957 | -0.14326 | 0.0019136 | 0.00047959
91 | 0.98013 | -0.13924 | 0.003183 | 0.00079773
92 | 0.97925 | -0.14555 | 0.0019821 | 0.00049676
93 | 0.98595 | -0.097963 | 0.0013643 | 0.00034192
94 | 0.97871 | -0.1494 | 0.0020357 | 0.00051019
95 | 0.97648 | -0.16511 | 0.0037932 | 0.00095066
96 | 0.97674 | -0.16326 | 0.0040923 | 0.0010256
97 | 0.97577 | -0.17024 | 0 | 0
98 | 0.97538 | -0.17302 | 0.0016066 | 0.00040265
99 | 0.97564 | -0.17112 | 0.0033931 | 0.0008504
100 | 0.97498 | -0.17588 | 0.0024897 | 0.00062397
101 | 0.97563 | -0.17119 | 0.0014751 | 0.00036969
102 | 0.97492 | -0.17635 | 0.0020779 | 0.00052077
103 | 0.97556 | -0.17174 | 0.0035722 | 0.00089528
104 | 0.9832 | -0.11727 | 0.0016241 | 0.00040703
105 | 0.97466 | -0.17818 | 0.0019936 | 0.00049964
106 | 0.97694 | -0.16229 | 0.0008265 | 0.00020714
107 | 0.97462 | -0.17848 | 0.0021368 | 0.00053554
108 | 0.97438 | -0.18022 | 0 | 0
109 | 0.97434 | -0.18046 | 0.00085177 | 0.00021347
110 | 0.97434 | -0.18047 | 0.0011628 | 0.00029143
111 | 0.9714 | -0.20229 | 0 | 0
112 | 0.97094 | -0.20559 | 0.00050646 | 0.00012693
113 | 0.97094 | -0.20566 | 0 | 0
114 | 0.97091 | -0.20581 | 0.00075087 | 0.00018818
115 | 0.97087 | -0.20619 | 0 | 0
116 | 0.97084 | -0.20637 | 0.002138 | 0.00053583
117 | 0.98377 | -0.11324 | 0.0016252 | 0.00040731
118 | 0.97672 | -0.16387 | 0.00069011 | 0.00017296
119 | 0.98684 | -0.091558 | 0.001927 | 0.00048295
120 | 0.97654 | -0.16521 | 0.00064303 | 0.00016116
121 | 0.98779 | -0.084936 | 0.0025743 | 0.00064517
122 | 0.98777 | -0.08511 | 0.0013745 | 0.00034449
123 | 0.98834 | -0.081055 | 0 | 0
124 | 0.98775 | -0.085215 | 0.00088025 | 0.00022061
125 | 0.98707 | -0.089964 | 0.0024346 | 0.00061016
126 | 0.98769 | -0.085629 | 0.00088025 | 0.00022061
127 | 0.98752 | -0.086836 | 0.0028988 | 0.00072651
128 | 0.98745 | -0.087368 | 0.0022044 | 0.00055246
129 | 0.9881 | -0.082737 | 0.0010757 | 0.0002696
130 | 0.97433 | -0.18058 | 0.0015487 | 0.00038815
131 | 0.97432 | -0.18063 | 0.0013269 | 0.00033256
132 | 0.97656 | -0.16486 | 0.0015699 | 0.00039346
133 | 0.97663 | -0.16436 | 0.0016511 | 0.00041381
134 | 0.97732 | -0.15942 | 0.0028578 | 0.00071622
135 | 0.97824 | -0.15278 | 0.0028106 | 0.0007044
136 | 0.97637 | -0.16644 | 0.0013477 | 0.00033776
137 | 0.97606 | -0.16866 | 0.0017791 | 0.00044588
138 | 0.97078 | -0.20678 | 0.00048652 | 0.00012193
139 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00080685 | -0.00020222 | 0.00080691 | 0.00020155 | 5.2237e-08 | -6.6929e-07 | 0.0012311 | 0.0012308 | 0.0012311 | 0.97524 | -0.17468 | 0.9753 | -0.17421 | 0.45596
1 | -0.00080691 | -0.00020155 | 0.00080702 | 0.0002001 | 1.1296e-07 | -1.4486e-06 | 0.0012308 | 0.0012303 | 0.0012308 | 0.9753 | -0.17421 | 0.97544 | -0.17318 | 0.45587
2 | -0.0012775 | -0.00031801 | 0.0012781 | 0.00031488 | 6.3863e-07 | -3.1248e-06 | 0.001948 | 0.0019468 | 0.001948 | 0.97544 | -0.17318 | 0.97595 | -0.16949 | 0.72148
3 | -0.0023515 | -0.0005839 | 0.002352 | 0.00058335 | 4.6746e-07 | -5.4943e-07 | 0.0035834 | 0.0035831 | 0.0035834 | 0.97595 | -0.16949 | 0.97615 | -0.16802 | 1.3272
4 | 0.0017792 | 0.00044551 | -0.0017791 | -0.00044588 | 1.5551e-07 | -3.6369e-07 | 0.0027121 | 0.0027122 | 0.0027122 | 0.97615 | -0.16802 | 0.97606 | -0.16866 | 1.0045
5 | -0.0041312 | -0.0010289 | 0.0041321 | 0.0010288 | 8.9623e-07 | -1.0847e-07 | 0.0062952 | 0.006295 | 0.0062952 | 0.97615 | -0.16802 | 0.97637 | -0.16644 | 2.3315
6 | -0.015672 | -0.0039276 | 0.015681 | 0.0039309 | 9.2053e-06 | 3.2171e-06 | 0.023888 | 0.023888 | 0.023888 | 0.97619 | -0.1676 | 0.97678 | -0.16336 | 8.8475
7 | 0.0058907 | 0.0014763 | -0.0058905 | -0.0014763 | 1.9415e-07 | 2.643e-08 | 0.0089793 | 0.0089793 | 0.0089793 | 0.97619 | -0.1676 | 0.97616 | -0.16784 | 3.3257
8 | -0.018962 | -0.0047531 | 0.018991 | 0.0047637 | 2.9431e-05 | 1.0611e-05 | 0.028886 | 0.028886 | 0.028886 | 0.97678 | -0.16336 | 0.97835 | -0.15217 | 10.6986
9 | -0.032545 | -0.0081358 | 0.03258 | 0.0081466 | 3.4552e-05 | 1.0732e-05 | 0.049492 | 0.049492 | 0.049492 | 0.97835 | -0.15217 | 0.97942 | -0.14447 | 6.1102
10 | 0.013554 | 0.0033721 | -0.013548 | -0.0033724 | 6.28e-06 | -2.6177e-07 | 0.020607 | 0.020608 | 0.020608 | 0.97835 | -0.15217 | 0.97788 | -0.15557 | 2.5441
11 | -0.050547 | -0.012649 | 0.050565 | 0.012656 | 1.8486e-05 | 6.5407e-06 | 0.076788 | 0.076788 | 0.076788 | 0.97942 | -0.14447 | 0.97979 | -0.14182 | 9.48
12 | 0.004824 | 0.0012074 | -0.0048237 | -0.0012074 | 3.2237e-07 | 3.7e-09 | 0.00734 | 0.0073401 | 0.0073401 | 0.97788 | -0.15557 | 0.97781 | -0.15605 | 2.7185
13 | 0.0087241 | 0.0021649 | -0.008723 | -0.0021657 | 1.1411e-06 | -7.3391e-07 | 0.013268 | 0.013268 | 0.013268 | 0.97788 | -0.15557 | 0.97775 | -0.15653 | 1.638
14 | 0.008723 | 0.0021657 | -0.0087223 | -0.0021661 | 6.8844e-07 | -4.4257e-07 | 0.013268 | 0.013268 | 0.013268 | 0.97775 | -0.15653 | 0.97767 | -0.15711 | 1.6381
15 | 0.0070883 | 0.0017566 | -0.0070879 | -0.001757 | 3.6502e-07 | -4.2754e-07 | 0.010781 | 0.010781 | 0.010781 | 0.97767 | -0.15711 | 0.97762 | -0.15749 | 1.331
16 | -0.050565 | -0.012656 | 0.050579 | 0.012661 | 1.4285e-05 | 5.0539e-06 | 0.076788 | 0.076788 | 0.076788 | 0.97979 | -0.14182 | 0.98008 | -0.13978 | 9.48
17 | -0.053034 | -0.013276 | 0.05306 | 0.013285 | 2.6681e-05 | 9.5135e-06 | 0.080514 | 0.080514 | 0.080514 | 0.98008 | -0.13978 | 0.98058 | -0.13614 | 9.94
18 | 0.0024543 | 0.0006147 | -0.002454 | -0.00061504 | 3.197e-07 | -3.4195e-07 | 0.0037262 | 0.0037264 | 0.0037264 | 0.98008 | -0.13978 | 0.97994 | -0.14072 | 1.3801
19 | 0.035111 | 0.0087995 | -0.035068 | -0.0087833 | 4.2982e-05 | 1.6226e-05 | 0.053281 | 0.053281 | 0.053281 | 0.98058 | -0.13614 | 0.97935 | -0.14499 | 19.7336
20 | -0.088172 | -0.022085 | 0.088742 | 0.022298 | 0.0005699 | 0.00021336 | 0.13379 | 0.13379 | 0.13379 | 0.98058 | -0.13614 | 0.98712 | -0.089689 | 16.5178
21 | 0.0012408 | 0.00031029 | -0.0012406 | -0.00031094 | 1.234e-07 | -6.4832e-07 | 0.0018879 | 0.0018882 | 0.0018882 | 0.97781 | -0.15605 | 0.97771 | -0.15677 | 0.69933
22 | 0.0035829 | 0.00089714 | -0.0035823 | -0.00089732 | 5.8832e-07 | -1.7149e-07 | 0.0054521 | 0.0054523 | 0.0054523 | 0.97781 | -0.15605 | 0.97765 | -0.15724 | 2.0194
23 | 0.013508 | 0.0033798 | -0.013494 | -0.003375 | 1.4198e-05 | 4.7816e-06 | 0.020522 | 0.020523 | 0.020523 | 0.97935 | -0.14499 | 0.97828 | -0.15261 | 7.601
24 | -0.090765 | -0.022805 | 0.091076 | 0.022921 | 0.00031015 | 0.00011622 | 0.13684 | 0.13684 | 0.13684 | 0.98712 | -0.089689 | 0.9906 | -0.065213 | 16.8942
25 | 0.00072596 | 0.00018173 | -0.00072595 | -0.00018194 | 1.3086e-08 | -2.1034e-07 | 0.0011049 | 0.001105 | 0.001105 | 0.97762 | -0.15749 | 0.9776 | -0.15762 | 0.40925
26 | 0.006362 | 0.0015753 | -0.0063617 | -0.0015758 | 3.0863e-07 | -4.7732e-07 | 0.0096766 | 0.0096768 | 0.0096768 | 0.97762 | -0.15749 | 0.97757 | -0.15785 | 1.1947
27 | 0.22674 | 0.057361 | -0.22494 | -0.056673 | 0.0017953 | 0.00068754 | 0.33757 | 0.33758 | 0.33758 | 1 | 0 | 0.99183 | -0.056583 | 41.676
28 | 0.056004 | 0.01411 | -0.055828 | -0.014044 | 0.00017585 | 6.5581e-05 | 0.084048 | 0.084048 | 0.084048 | 0.99183 | -0.056583 | 0.98862 | -0.079096 | 15.5645
29 | 0.16894 | 0.042563 | -0.16887 | -0.042537 | 6.9909e-05 | 2.6686e-05 | 0.25353 | 0.25353 | 0.25353 | 0.99183 | -0.056583 | 0.99141 | -0.059542 | 31.2998
30 | 0.0022539 | 0.00056439 | -0.0022538 | -0.00056451 | 9.1241e-08 | -1.2071e-07 | 0.0034304 | 0.0034305 | 0.0034305 | 0.97765 | -0.15724 | 0.97761 | -0.15753 | 1.2705
31 | 0.010974 | 0.0027439 | -0.010962 | -0.0027401 | 1.213e-05 | 3.79e-06 | 0.01669 | 0.01669 | 0.01669 | 0.97828 | -0.15261 | 0.97717 | -0.16064 | 6.1815
32 | 0.00252 | 0.00063111 | -0.0025197 | -0.00063148 | 3.8011e-07 | -3.743e-07 | 0.0038329 | 0.0038331 | 0.0038331 | 0.97828 | -0.15261 | 0.97813 | -0.1537 | 1.4197
33 | -0.092203 | -0.023204 | 0.092276 | 0.023231 | 7.3039e-05 | 2.7385e-05 | 0.13853 | 0.13853 | 0.13853 | 0.9906 | -0.065213 | 0.99141 | -0.059542 | 17.1031
34 | -0.0017843 | -0.00044718 | 0.0017844 | 0.00044686 | 1.393e-07 | -3.2584e-07 | 0.0027161 | 0.0027159 | 0.0027161 | 0.97753 | -0.1581 | 0.97761 | -0.15753 | 1.006
35 | 0.0055808 | 0.0013801 | -0.0055805 | -0.0013807 | 2.8705e-07 | -6.0996e-07 | 0.0084882 | 0.0084885 | 0.0084885 | 0.97757 | -0.15785 | 0.97752 | -0.15823 | 1.048
36 | 0.054926 | 0.013818 | -0.054898 | -0.013808 | 2.7883e-05 | 1.064e-05 | 0.08269 | 0.08269 | 0.08269 | 0.98862 | -0.079096 | 0.9881 | -0.082737 | 30.626
37 | 0.073904 | 0.018632 | -0.073807 | -0.018595 | 9.6713e-05 | 3.7035e-05 | 0.11096 | 0.11096 | 0.11096 | 0.99141 | -0.059542 | 0.99007 | -0.068896 | 41.0971
38 | 0.002686 | 0.000673 | -0.0026859 | -0.00067314 | 1.603e-07 | -1.4215e-07 | 0.0040314 | 0.0040315 | 0.0040315 | 0.99141 | -0.059542 | 0.99135 | -0.059973 | 1.4931
39 | 0.00092294 | 0.00023093 | -0.0009229 | -0.0002313 | 3.8222e-08 | -3.7133e-07 | 0.0014075 | 0.0014077 | 0.0014077 | 0.97562 | -0.17166 | 0.97558 | -0.17196 | 0.52136
40 | -0.0018977 | -0.00047523 | 0.0018977 | 0.00047516 | 3.5361e-08 | -7.0878e-08 | 0.0028943 | 0.0028942 | 0.0028943 | 0.97562 | -0.17166 | 0.97564 | -0.17152 | 1.0719
41 | -0.012727 | -0.0031806 | 0.012733 | 0.0031826 | 5.8431e-06 | 1.9368e-06 | 0.019408 | 0.019407 | 0.019408 | 0.97564 | -0.17152 | 0.9761 | -0.16819 | 7.188
42 | 0.010829 | 0.0027055 | -0.010822 | -0.0027033 | 6.9613e-06 | 2.1669e-06 | 0.016513 | 0.016514 | 0.016514 | 0.97564 | -0.17152 | 0.97499 | -0.1762 | 6.1161
43 | 0.0076447 | 0.0019087 | -0.007643 | -0.0019083 | 1.7273e-06 | 4.0841e-07 | 0.011639 | 0.011639 | 0.011639 | 0.97717 | -0.16064 | 0.97694 | -0.16229 | 4.3106
44 | 0.0051857 | 0.001292 | -0.0051837 | -0.0012919 | 2.0637e-06 | 1.378e-07 | 0.0079198 | 0.0079201 | 0.0079201 | 0.97399 | -0.18347 | 0.97359 | -0.18638 | 2.9334
45 | 0.0002684 | 6.5995e-05 | -0.00026839 | -6.7264e-05 | 1.072e-08 | -1.2689e-06 | 0.00040959 | 0.00041005 | 0.00041005 | 0.97399 | -0.18347 | 0.97395 | -0.18377 | 0.15187
46 | -0.0054541 | -0.001358 | 0.005455 | 0.0013581 | 8.6559e-07 | 8.4039e-08 | 0.0083294 | 0.0083293 | 0.0083294 | 0.97399 | -0.18347 | 0.97414 | -0.18231 | 3.085
47 | 0.0044866 | 0.0011172 | -0.0044851 | -0.0011173 | 1.5612e-06 | -6.1419e-08 | 0.0068547 | 0.006855 | 0.006855 | 0.97359 | -0.18638 | 0.97324 | -0.18893 | 2.5389
48 | -0.0062531 | -0.0015581 | 0.0062537 | 0.0015582 | 6.01e-07 | 9.9621e-08 | 0.0095484 | 0.0095484 | 0.0095484 | 0.97414 | -0.18231 | 0.97424 | -0.18161 | 3.5364
49 | 0.0044851 | 0.0011173 | -0.0044832 | -0.0011173 | 1.8555e-06 | -7.2324e-08 | 0.006855 | 0.0068552 | 0.0068552 | 0.97324 | -0.18893 | 0.97282 | -0.19195 | 2.539
50 | -0.0070291 | -0.0017526 | 0.0070299 | 0.0017527 | 8.0939e-07 | 1.7107e-07 | 0.010733 | 0.010733 | 0.010733 | 0.97424 | -0.18161 | 0.97436 | -0.18077 | 3.975
51 | 0.0038894 | 0.00096853 | -0.0038839 | -0.0009695 | 5.5063e-06 | -9.7494e-07 | 0.005947 | 0.0059481 | 0.0059481 | 0.97282 | -0.19195 | 0.9714 | -0.20229 | 2.203
52 | -0.0079413 | -0.0019812 | 0.0079437 | 0.0019818 | 2.3516e-06 | 5.8506e-07 | 0.012125 | 0.012124 | 0.012125 | 0.97436 | -0.18077 | 0.97466 | -0.17861 | 4.4906
53 | -0.00076674 | -0.00019216 | 0.00076688 | 0.00019015 | 1.4174e-07 | -2.012e-06 | 0.0011707 | 0.00117 | 0.0011707 | 0.97453 | -0.18039 | 0.97471 | -0.17904 | 0.43361
54 | 0.00096307 | 0.00023688 | -0.00096294 | -0.00023801 | 1.269e-07 | -1.1259e-06 | 0.0014686 | 0.0014691 | 0.0014691 | 0.97471 | -0.17904 | 0.97458 | -0.18002 | 0.5441
55 | -0.00173 | -0.00042703 | 0.0017308 | 0.00042501 | 8.1233e-07 | -2.0199e-06 | 0.0026386 | 0.0026378 | 0.0026386 | 0.97471 | -0.17904 | 0.97519 | -0.17553 | 0.97728
56 | 0.00064815 | 0.00015911 | -0.00064808 | -0.0001605 | 6.9108e-08 | -1.3851e-06 | 0.00098842 | 0.00098892 | 0.00098892 | 0.97458 | -0.18002 | 0.97447 | -0.18081 | 0.36627
57 | -0.0023654 | -0.00058384 | 0.0023669 | 0.00058203 | 1.5657e-06 | -1.8074e-06 | 0.0036061 | 0.0036052 | 0.0036061 | 0.97519 | -0.17553 | 0.97585 | -0.17058 | 1.3356
58 | 0.0006346 | 0.00015883 | -0.00063459 | -0.00015904 | 1.0274e-08 | -2.1513e-07 | 0.00096825 | 0.00096833 | 0.00096833 | 0.97519 | -0.17553 | 0.97517 | -0.17564 | 0.35864
59 | 0.00035982 | 8.8253e-05 | -0.00035982 | -8.8491e-05 | 3.5999e-09 | -2.3725e-07 | 0.00054876 | 0.00054884 | 0.00054884 | 0.97447 | -0.18081 | 0.97446 | -0.18089 | 0.20327
60 | -0.0023669 | -0.00058203 | 0.0023689 | 0.00057972 | 1.9993e-06 | -2.3143e-06 | 0.0036052 | 0.0036041 | 0.0036052 | 0.97585 | -0.17058 | 0.9767 | -0.16423 | 1.3353
61 | 0.00035982 | 8.8491e-05 | -0.00035979 | -9.0172e-05 | 2.5549e-08 | -1.6815e-06 | 0.00054884 | 0.00054944 | 0.00054944 | 0.97446 | -0.18089 | 0.97439 | -0.18141 | 0.2035
62 | -0.0035384 | -0.00087281 | 0.0035395 | 0.00087247 | 1.1299e-06 | -3.4698e-07 | 0.0053858 | 0.0053855 | 0.0053858 | 0.9767 | -0.16423 | 0.97702 | -0.16185 | 1.9947
63 | -0.0046613 | -0.0011536 | 0.0046636 | 0.0011509 | 2.2714e-06 | -2.7522e-06 | 0.0070939 | 0.0070927 | 0.0070939 | 0.97702 | -0.16185 | 0.97752 | -0.15823 | 1.3137
64 | -0.00087546 | -0.00021941 | 0.00087547 | 0.00021926 | 1.3399e-08 | -1.4991e-07 | 0.0013251 | 0.001325 | 0.0013251 | 0.98309 | -0.11822 | 0.98311 | -0.11811 | 0.49078
65 | -0.0032051 | -0.00080238 | 0.0032063 | 0.00080183 | 1.1552e-06 | -5.5367e-07 | 0.0048509 | 0.0048506 | 0.0048509 | 0.98311 | -0.11811 | 0.98347 | -0.1155 | 1.7966
66 | 0.0023297 | 0.00058312 | -0.0023292 | -0.00058374 | 4.9665e-07 | -6.2052e-07 | 0.0035259 | 0.0035262 | 0.0035262 | 0.98311 | -0.11811 | 0.98289 | -0.11965 | 1.306
67 | -0.0045319 | -0.0011341 | 0.0045327 | 0.001134 | 8.3198e-07 | -3.9989e-08 | 0.0068562 | 0.0068561 | 0.0068562 | 0.98347 | -0.1155 | 0.98366 | -0.11417 | 2.5393
68 | -0.0058247 | -0.0014578 | 0.0058252 | 0.0014579 | 5.4387e-07 | 6.6634e-08 | 0.0088105 | 0.0088104 | 0.0088105 | 0.98366 | -0.11417 | 0.98375 | -0.11349 | 3.2631
69 | -0.050869 | -0.012769 | 0.050954 | 0.012801 | 8.4295e-05 | 3.2131e-05 | 0.076951 | 0.076951 | 0.076951 | 0.98375 | -0.11349 | 0.98543 | -0.10158 | 28.5005
70 | 0.045044 | 0.011311 | -0.044891 | -0.011253 | 0.00015279 | 5.8098e-05 | 0.068141 | 0.068141 | 0.068141 | 0.98375 | -0.11349 | 0.98031 | -0.13798 | 25.2375
71 | -0.052318 | -0.013143 | 0.052344 | 0.013153 | 2.6309e-05 | 1.0033e-05 | 0.079011 | 0.079011 | 0.079011 | 0.98543 | -0.10158 | 0.98595 | -0.097963 | 29.2635
72 | 0.0042196 | 0.0010572 | -0.0042193 | -0.0010572 | 3.2649e-07 | -3.5219e-08 | 0.0064049 | 0.0064049 | 0.0064049 | 0.98031 | -0.13798 | 0.98023 | -0.13854 | 2.3722
73 | 0.03016 | 0.0075616 | -0.030138 | -0.0075534 | 2.2026e-05 | 8.2594e-06 | 0.045781 | 0.045782 | 0.045782 | 0.98031 | -0.13798 | 0.97957 | -0.14326 | 16.9561
74 | 0.010511 | 0.0026338 | -0.01051 | -0.0026334 | 1.3418e-06 | 4.0958e-07 | 0.015955 | 0.015955 | 0.015955 | 0.98031 | -0.13798 | 0.98018 | -0.13891 | 5.9093
75 | 0.0050667 | 0.0012695 | -0.0050654 | -0.0012694 | 1.2731e-06 | 5.8802e-08 | 0.0077081 | 0.0077082 | 0.0077082 | 0.97808 | -0.15367 | 0.97783 | -0.15548 | 2.8549
76 | -0.010355 | -0.0025948 | 0.01036 | 0.0025963 | 4.6739e-06 | 1.4187e-06 | 0.015753 | 0.015753 | 0.015753 | 0.97808 | -0.15367 | 0.97854 | -0.15041 | 5.8346
77 | 0.0017263 | 0.00043255 | -0.0017262 | -0.00043264 | 3.3658e-08 | -8.5102e-08 | 0.0026269 | 0.002627 | 0.002627 | 0.97783 | -0.15548 | 0.97781 | -0.15562 | 0.97295
78 | -0.011989 | -0.0030047 | 0.01199 | 0.003005 | 1.0091e-06 | 3.27e-07 | 0.018232 | 0.018232 | 0.018232 | 0.97854 | -0.15041 | 0.97862 | -0.1498 | 6.7524
79 | -0.017408 | -0.0043629 | 0.017409 | 0.0043631 | 7.1075e-07 | 2.5294e-07 | 0.026469 | 0.026469 | 0.026469 | 0.97862 | -0.1498 | 0.97867 | -0.1495 | 9.8035
80 | -0.019039 | -0.0047717 | 0.019047 | 0.0047747 | 8.2754e-06 | 2.9839e-06 | 0.028948 | 0.028948 | 0.028948 | 0.97867 | -0.1495 | 0.9791 | -0.14637 | 10.7216
81 | -0.053634 | -0.013456 | 0.053811 | 0.013524 | 0.00017682 | 6.7468e-05 | 0.081517 | 0.081517 | 0.081517 | 0.9791 | -0.14637 | 0.98243 | -0.12268 | 30.1916
82 | 0.034587 | 0.0086814 | -0.034533 | -0.008661 | 5.4113e-05 | 2.0419e-05 | 0.052569 | 0.052569 | 0.052569 | 0.9791 | -0.14637 | 0.97752 | -0.15765 | 19.4701
83 | 0.0727 | 0.018318 | -0.072577 | -0.01827 | 0.00012347 | 4.7276e-05 | 0.1093 | 0.1093 | 0.1093 | 0.99007 | -0.068896 | 0.98834 | -0.081055 | 40.481
84 | -0.053811 | -0.013524 | 0.053852 | 0.013539 | 4.0551e-05 | 1.5473e-05 | 0.081517 | 0.081517 | 0.081517 | 0.98243 | -0.12268 | 0.9832 | -0.11727 | 30.1915
85 | 0.031586 | 0.0079225 | -0.031562 | -0.0079133 | 2.4535e-05 | 9.2237e-06 | 0.048084 | 0.048084 | 0.048084 | 0.97752 | -0.15765 | 0.97674 | -0.16326 | 17.8089
86 | -0.0088701 | -0.0022139 | 0.0088717 | 0.0022144 | 1.6558e-06 | 4.5641e-07 | 0.013539 | 0.013539 | 0.013539 | 0.97466 | -0.17861 | 0.97484 | -0.17725 | 5.0144
87 | -0.0099416 | -0.0024825 | 0.009943 | 0.0024829 | 1.4441e-06 | 4.3004e-07 | 0.015172 | 0.015172 | 0.015172 | 0.97484 | -0.17725 | 0.97499 | -0.1762 | 5.6192
88 | -0.013725 | -0.0034311 | 0.013725 | 0.0034312 | 1.465e-07 | 4.9641e-08 | 0.020919 | 0.020919 | 0.020919 | 0.9761 | -0.16819 | 0.97611 | -0.16811 | 7.748
89 | -0.015243 | -0.0038117 | 0.01525 | 0.0038141 | 6.8409e-06 | 2.3771e-06 | 0.023234 | 0.023234 | 0.023234 | 0.97611 | -0.16811 | 0.97656 | -0.16486 | 8.6052
90 | -0.0041252 | -0.0010332 | 0.0041258 | 0.0010331 | 5.8269e-07 | -7.5223e-08 | 0.0062667 | 0.0062666 | 0.0062667 | 0.97949 | -0.14384 | 0.97963 | -0.14282 | 2.321
91 | 0.002988 | 0.00074816 | -0.0029878 | -0.00074829 | 2.1126e-07 | -1.2556e-07 | 0.004539 | 0.0045391 | 0.0045391 | 0.97949 | -0.14384 | 0.97942 | -0.14435 | 1.6811
92 | -0.0068387 | -0.001713 | 0.0068391 | 0.0017131 | 3.7267e-07 | 7.3641e-08 | 0.010387 | 0.010387 | 0.010387 | 0.97963 | -0.14282 | 0.97969 | -0.14243 | 3.8472
93 | 0.0012289 | 0.00030773 | -0.0012288 | -0.00030797 | 4.3851e-08 | -2.3686e-07 | 0.0018669 | 0.001867 | 0.001867 | 0.97942 | -0.14435 | 0.97938 | -0.14461 | 0.69148
94 | 0.00062261 | 0.00015577 | -0.0006226 | -0.00015604 | 1.2182e-08 | -2.6991e-07 | 0.00094583 | 0.00094592 | 0.00094592 | 0.97942 | -0.14435 | 0.9794 | -0.14449 | 0.35034
95 | -0.010505 | -0.0026318 | 0.01051 | 0.0026334 | 5.1175e-06 | 1.5624e-06 | 0.015955 | 0.015955 | 0.015955 | 0.97969 | -0.14243 | 0.98018 | -0.13891 | 5.9093
96 | 0.0031833 | 0.00079759 | -0.003183 | -0.00079773 | 3.0956e-07 | -1.4872e-07 | 0.0048323 | 0.0048323 | 0.0048323 | 0.98023 | -0.13854 | 0.98013 | -0.13924 | 1.7898
97 | 0.028225 | 0.0070738 | -0.028216 | -0.0070704 | 8.9514e-06 | 3.3446e-06 | 0.042875 | 0.042875 | 0.042875 | 0.97957 | -0.14326 | 0.97925 | -0.14555 | 15.8795
98 | 0.026234 | 0.0065737 | -0.02622 | -0.0065685 | 1.3959e-05 | 5.1918e-06 | 0.039863 | 0.039863 | 0.039863 | 0.97925 | -0.14555 | 0.97871 | -0.1494 | 14.764
99 | -0.053708 | -0.013495 | 0.053823 | 0.013538 | 0.00011403 | 4.3501e-05 | 0.08107 | 0.08107 | 0.08107 | 0.98595 | -0.097963 | 0.9881 | -0.082737 | 30.0261
100 | 0.024184 | 0.0060583 | -0.024173 | -0.0060541 | 1.1308e-05 | 4.1809e-06 | 0.036768 | 0.036768 | 0.036768 | 0.97871 | -0.1494 | 0.97824 | -0.15278 | 13.6178
101 | -0.027463 | -0.006885 | 0.02747 | 0.0068877 | 7.0567e-06 | 2.6333e-06 | 0.04185 | 0.04185 | 0.04185 | 0.97648 | -0.16511 | 0.97674 | -0.16326 | 15.4999
102 | 0.023669 | 0.0059344 | -0.023653 | -0.0059282 | 1.6795e-05 | 6.2011e-06 | 0.036069 | 0.03607 | 0.03607 | 0.97648 | -0.16511 | 0.97577 | -0.17024 | 13.3591
103 | 0.015211 | 0.0038126 | -0.015205 | -0.0038106 | 5.8544e-06 | 2.034e-06 | 0.023196 | 0.023196 | 0.023196 | 0.97577 | -0.17024 | 0.97538 | -0.17302 | 8.5912
104 | 0.0084418 | 0.0021156 | -0.0084408 | -0.0021153 | 1.0282e-06 | 2.7128e-07 | 0.012873 | 0.012873 | 0.012873 | 0.97577 | -0.17024 | 0.97564 | -0.17112 | 4.768
105 | 0.013598 | 0.0034079 | -0.013593 | -0.0034061 | 5.3786e-06 | 1.8188e-06 | 0.020745 | 0.020745 | 0.020745 | 0.97538 | -0.17302 | 0.97498 | -0.17588 | 7.6835
106 | 0.0050476 | 0.0012649 | -0.0050476 | -0.0012649 | 5.191e-08 | 2.4364e-09 | 0.0076984 | 0.0076984 | 0.0076984 | 0.97564 | -0.17112 | 0.97563 | -0.17119 | 2.8513
107 | 0.011103 | 0.0027821 | -0.011103 | -0.0027819 | 7.253e-07 | 2.2849e-07 | 0.016946 | 0.016946 | 0.016946 | 0.97498 | -0.17588 | 0.97492 | -0.17635 | 6.2761
108 | 0.0035725 | 0.0008952 | -0.0035722 | -0.00089528 | 2.7255e-07 | -7.8884e-08 | 0.0054486 | 0.0054487 | 0.0054487 | 0.97563 | -0.17119 | 0.97556 | -0.17174 | 2.018
109 | 0.0090247 | 0.0022611 | -0.0090224 | -0.0022605 | 2.2895e-06 | 6.3951e-07 | 0.013774 | 0.013774 | 0.013774 | 0.97492 | -0.17635 | 0.97466 | -0.17818 | 5.1016
110 | -0.055476 | -0.013946 | 0.055507 | 0.013958 | 3.1156e-05 | 1.1893e-05 | 0.083975 | 0.083975 | 0.083975 | 0.9832 | -0.11727 | 0.98377 | -0.11324 | 31.1018
111 | 0.0070288 | 0.0017609 | -0.0070285 | -0.0017608 | 2.9268e-07 | 6.1806e-08 | 0.010731 | 0.010731 | 0.010731 | 0.97466 | -0.17818 | 0.97462 | -0.17848 | 3.9743
112 | 0.0068165 | 0.0017012 | -0.006815 | -0.0017009 | 1.4846e-06 | 2.9456e-07 | 0.01038 | 0.01038 | 0.01038 | 0.97694 | -0.16229 | 0.97672 | -0.16387 | 3.8444
113 | 0.0048917 | 0.0012253 | -0.0048905 | -0.0012252 | 1.1726e-06 | 3.124e-08 | 0.0074682 | 0.0074683 | 0.0074683 | 0.97462 | -0.17848 | 0.97438 | -0.18022 | 2.766
114 | 0.0024006 | 0.00060146 | -0.0024005 | -0.00060155 | 8.2258e-08 | -9.0528e-08 | 0.003666 | 0.0036661 | 0.0036661 | 0.97438 | -0.18022 | 0.97434 | -0.18046 | 1.3578
115 | 0.0024899 | 0.00062378 | -0.0024898 | -0.00062386 | 8.6987e-08 | -8.6638e-08 | 0.0038023 | 0.0038023 | 0.0038023 | 0.97438 | -0.18022 | 0.97434 | -0.18047 | 1.4083
116 | 0.0015488 | 0.00038808 | -0.0015487 | -0.00038815 | 2.4248e-08 | -7.7182e-08 | 0.0023652 | 0.0023653 | 0.0023653 | 0.97434 | -0.18046 | 0.97433 | -0.18058 | 0.87603
117 | 0.001327 | 0.00033243 | -0.0013269 | -0.00033256 | 2.8924e-08 | -1.2945e-07 | 0.0020265 | 0.0020265 | 0.0020265 | 0.97434 | -0.18047 | 0.97432 | -0.18063 | 0.75056
118 | 0.0038839 | 0.0009695 | -0.0038821 | -0.00096981 | 1.7625e-06 | -3.0991e-07 | 0.0059481 | 0.0059484 | 0.0059484 | 0.9714 | -0.20229 | 0.97094 | -0.20559 | 2.2031
119 | 0.0004866 | 0.00011917 | -0.0004866 | -0.00011933 | 4.5442e-09 | -1.6063e-07 | 0.00074474 | 0.0007448 | 0.0007448 | 0.97094 | -0.20559 | 0.97094 | -0.20566 | 0.27585
120 | 0.0028891 | 0.00072371 | -0.002889 | -0.00072377 | 8.6741e-08 | -5.4338e-08 | 0.0044275 | 0.0044276 | 0.0044276 | 0.97094 | -0.20559 | 0.97091 | -0.20581 | 1.6398
121 | 0.0004866 | 0.00011933 | -0.00048656 | -0.00012053 | 3.4096e-08 | -1.2043e-06 | 0.0007448 | 0.00074523 | 0.00074523 | 0.97094 | -0.20566 | 0.97087 | -0.20619 | 0.27601
122 | 0.0021381 | 0.00053558 | -0.002138 | -0.00053583 | 1.6567e-07 | -2.4205e-07 | 0.0032768 | 0.0032769 | 0.0032769 | 0.97091 | -0.20581 | 0.97084 | -0.20637 | 1.2137
123 | 0.00048656 | 0.00012053 | -0.00048652 | -0.00012193 | 3.9796e-08 | -1.4036e-06 | 0.00074523 | 0.00074574 | 0.00074574 | 0.97087 | -0.20619 | 0.97078 | -0.20678 | 0.2762
124 | -0.057132 | -0.014365 | 0.057305 | 0.014431 | 0.00017316 | 6.6125e-05 | 0.086433 | 0.086433 | 0.086433 | 0.98377 | -0.11324 | 0.98684 | -0.091558 | 32.0122
125 | 0.0061249 | 0.0015279 | -0.0061237 | -0.0015278 | 1.1269e-06 | 1.7375e-07 | 0.0093286 | 0.0093287 | 0.0093287 | 0.97672 | -0.16387 | 0.97654 | -0.16521 | 3.4551
126 | -0.059232 | -0.014914 | 0.059246 | 0.014919 | 1.3191e-05 | 5.0395e-06 | 0.089339 | 0.089339 | 0.089339 | 0.98684 | -0.091558 | 0.98707 | -0.089964 | 33.0883
127 | 0.0054807 | 0.0013666 | -0.0054798 | -0.0013665 | 9.1872e-07 | 8.9143e-08 | 0.0083489 | 0.0083489 | 0.0083489 | 0.97654 | -0.16521 | 0.97637 | -0.16644 | 3.0922
128 | 0.0082399 | 0.0020646 | -0.0082397 | -0.0020645 | 1.9857e-07 | 4.9933e-08 | 0.012412 | 0.012412 | 0.012412 | 0.98779 | -0.084936 | 0.98777 | -0.08511 | 4.5972
129 | -0.010814 | -0.0027098 | 0.01082 | 0.0027116 | 5.8114e-06 | 1.7857e-06 | 0.01629 | 0.01629 | 0.01629 | 0.98779 | -0.084936 | 0.98834 | -0.081055 | 6.0334
130 | 0.0068651 | 0.0017201 | -0.006865 | -0.00172 | 9.9543e-08 | 1.9194e-08 | 0.010342 | 0.010342 | 0.010342 | 0.98777 | -0.08511 | 0.98775 | -0.085215 | 3.8303
131 | 0.061757 | 0.015559 | -0.06168 | -0.01553 | 7.6879e-05 | 2.9386e-05 | 0.093009 | 0.093009 | 0.093009 | 0.98834 | -0.081055 | 0.98707 | -0.089964 | 34.4477
132 | 0.0059848 | 0.0014994 | -0.0059845 | -0.0014994 | 3.4265e-07 | 4.5322e-08 | 0.0090157 | 0.0090157 | 0.0090157 | 0.98775 | -0.085215 | 0.98769 | -0.085629 | 3.3392
133 | 0.0051042 | 0.0012788 | -0.0051033 | -0.0012787 | 8.5204e-07 | 3.2218e-08 | 0.0076896 | 0.0076897 | 0.0076897 | 0.98769 | -0.085629 | 0.98752 | -0.086836 | 2.848
134 | 0.0022045 | 0.00055223 | -0.0022044 | -0.00055246 | 1.624e-07 | -2.3929e-07 | 0.0033217 | 0.0033218 | 0.0033218 | 0.98752 | -0.086836 | 0.98745 | -0.087368 | 1.2303
135 | -0.01682 | -0.0042076 | 0.016821 | 0.004208 | 1.1597e-06 | 4.1062e-07 | 0.025626 | 0.025626 | 0.025626 | 0.97656 | -0.16486 | 0.97663 | -0.16436 | 9.4912
136 | -0.018472 | -0.0046218 | 0.018485 | 0.0046263 | 1.2586e-05 | 4.522e-06 | 0.028142 | 0.028142 | 0.028142 | 0.97663 | -0.16436 | 0.97732 | -0.15942 | 10.4229
137 | -0.021343 | -0.0053425 | 0.021362 | 0.0053497 | 1.9593e-05 | 7.1627e-06 | 0.032493 | 0.032493 | 0.032493 | 0.97732 | -0.15942 | 0.97824 | -0.15278 | 12.0344

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22754 | 0.057361

## res_load
| p_mw | q_mvar
0 | 0.00080685 | 0.00020222
1 | 0.00047047 | 0.00011791
2 | 0.0010734 | 0.00026902
3 | 0.0097808 | 0.0024513
4 | 0.0032809 | 0.00082227
5 | 0.0058905 | 0.0014763
6 | 0.017967 | 0.0045029
7 | 0.001634 | 0.00040952
8 | 0.002454 | 0.00061504
9 | 0.02156 | 0.0054035
10 | 0.0020238 | 0.00050721
11 | 0.0012406 | 0.00031094
12 | 0.0013284 | 0.00033293
13 | 0.0011273 | 0.00028252
14 | 0.0017843 | 0.00044718
15 | 0.00046943 | 0.00011765
16 | 0.00072595 | 0.00018194
17 | 0.00078087 | 0.0001957
18 | 0.00090226 | 0.00022613
19 | 0.00097476 | 0.0002443
20 | 0.0009229 | 0.0002313
21 | 0.0033172 | 0.00083137
22 | 0.0025197 | 0.00063148
23 | 0.00069703 | 0.00017469
24 | 0.00026839 | 6.7264e-05
25 | 0.00079808 | 0.00020002
26 | 0.00077538 | 0.00019433
27 | 0.00059381 | 0.00014882
28 | 0.00091146 | 0.00022843
29 | 0.00076674 | 0.00019216
30 | 0.00031479 | 7.8895e-05
31 | 0.00028826 | 7.2245e-05
32 | 0.00063459 | 0.00015904
33 | 0.0011695 | 0.00029309
34 | 0.00035979 | 9.0172e-05
35 | 0.0011218 | 0.00028114
36 | 0.00091695 | 0.00022981
37 | 0.00087546 | 0.00021941
38 | 0.0013256 | 0.00033223
39 | 0.0023292 | 0.00058374
40 | 0.0012919 | 0.00032379
41 | 0.0013643 | 0.00034192
42 | 0.0052883 | 0.0013254
43 | 0.0033391 | 0.00083686
44 | 0.0016297 | 0.00040845
45 | 0.0017262 | 0.00043264
46 | 0.0054178 | 0.0013578
47 | 0.0016303 | 0.0004086
48 | 0.0026859 | 0.00067314
49 | 0.0011069 | 0.00027742
50 | 0.0029464 | 0.00073844
51 | 0.00092641 | 0.00023218
52 | 0.0010698 | 0.00026812
53 | 0.00087924 | 0.00022036
54 | 0.00099182 | 0.00024857
55 | 0.0015184 | 0.00038054
56 | 0.0011373 | 0.00028502
57 | 0.0027129 | 0.00067991
58 | 0.0011363 | 0.00028478
59 | 0.0036658 | 0.00091873
60 | 0.0012288 | 0.00030797
61 | 0.0006226 | 0.00015604
62 | 0.001036 | 0.00025964
63 | 0.0019136 | 0.00047959
64 | 0.003183 | 0.00079773
65 | 0.0019821 | 0.00049676
66 | 0.0013643 | 0.00034192
67 | 0.0020357 | 0.00051019
68 | 0.0037932 | 0.00095066
69 | 0.0040923 | 0.0010256
70 | 0.0016066 | 0.00040265
71 | 0.0033931 | 0.0008504
72 | 0.0024897 | 0.00062397
73 | 0.0014751 | 0.00036969
74 | 0.0020779 | 0.00052077
75 | 0.0035722 | 0.00089528
76 | 0.0016241 | 0.00040703
77 | 0.0019936 | 0.00049964
78 | 0.0008265 | 0.00020714
79 | 0.0021368 | 0.00053554
80 | 0.00085177 | 0.00021347
81 | 0.0011628 | 0.00029143
82 | 0.00050646 | 0.00012693
83 | 0.00075087 | 0.00018818
84 | 0.002138 | 0.00053583
85 | 0.0016252 | 0.00040731
86 | 0.00069011 | 0.00017296
87 | 0.001927 | 0.00048295
88 | 0.00064303 | 0.00016116
89 | 0.0025743 | 0.00064517
90 | 0.0013745 | 0.00034449
91 | 0.00088025 | 0.00022061
92 | 0.0024346 | 0.00061016
93 | 0.00088025 | 0.00022061
94 | 0.0028988 | 0.00072651
95 | 0.0022044 | 0.00055246
96 | 0.0010757 | 0.0002696
97 | 0.0015487 | 0.00038815
98 | 0.0013269 | 0.00033256
99 | 0.0015699 | 0.00039346
100 | 0.0016511 | 0.00041381
101 | 0.0028578 | 0.00071622
102 | 0.0028106 | 0.0007044
103 | 0.0013477 | 0.00033776
104 | 0.0017791 | 0.00044588
105 | 0.00048652 | 0.00012193

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1