## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1010-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1010-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1010-7_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1010-7_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1010-7_0_4_node_119 | 0.4 | n |  | TRUE
5 | bus_LV_1010-7_0_4_node_105 | 0.4 | n |  | TRUE
6 | bus_LV_1010-7_0_4_node_114 | 0.4 | n |  | TRUE
7 | bus_LV_1010-7_0_4_node_98 | 0.4 | n |  | TRUE
8 | bus_LV_1010-7_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1010-7_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1010-7_0_4_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1010-7_0_4_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_1010-7_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_1010-7_0_4_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_1010-7_0_4_node_25 | 0.4 | n |  | TRUE
15 | bus_LV_1010-7_0_4_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_1010-7_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1010-7_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1010-7_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1010-7_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1010-7_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1010-7_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1010-7_0_4_node_123 | 0.4 | n |  | TRUE
23 | bus_LV_1010-7_0_4_node_121 | 0.4 | n |  | TRUE
24 | bus_LV_1010-7_0_4_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_1010-7_0_4_node_125 | 0.4 | n |  | TRUE
26 | bus_LV_1010-7_0_4_node_126 | 0.4 | n |  | TRUE
27 | bus_LV_1010-7_0_4_node_122 | 0.4 | n |  | TRUE
28 | bus_LV_1010-7_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1010-7_0_4_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_1010-7_0_4_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_1010-7_0_4_node_124 | 0.4 | n |  | TRUE
32 | bus_LV_1010-7_0_4_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_1010-7_0_4_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_1010-7_0_4_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_1010-7_0_4_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1010-7_0_4_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1010-7_0_4_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1010-7_0_4_node_21 | 0.4 | n |  | TRUE
39 | bus_LV_1010-7_0_4_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1010-7_0_4_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_1010-7_0_4_node_24 | 0.4 | n |  | TRUE
42 | bus_LV_1010-7_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_1010-7_0_4_node_118 | 0.4 | n |  | TRUE
44 | bus_LV_1010-7_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_1010-7_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_1010-7_0_4_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_1010-7_0_4_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_1010-7_0_4_node_35 | 0.4 | n |  | TRUE
49 | bus_LV_1010-7_0_4_node_53 | 0.4 | n |  | TRUE
50 | bus_LV_1010-7_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_1010-7_0_4_node_74 | 0.4 | n |  | TRUE
52 | bus_LV_1010-7_0_4_node_37 | 0.4 | n |  | TRUE
53 | bus_LV_1010-7_0_4_node_75 | 0.4 | n |  | TRUE
54 | bus_LV_1010-7_0_4_node_104 | 0.4 | n |  | TRUE
55 | bus_LV_1010-7_0_4_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_1010-7_0_4_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_1010-7_0_4_node_103 | 0.4 | n |  | TRUE
58 | bus_LV_1010-7_0_4_node_68 | 0.4 | n |  | TRUE
59 | bus_LV_1010-7_0_4_node_40 | 0.4 | n |  | TRUE
60 | bus_LV_1010-7_0_4_node_42 | 0.4 | n |  | TRUE
61 | bus_LV_1010-7_0_4_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_1010-7_0_4_node_43 | 0.4 | n |  | TRUE
63 | bus_LV_1010-7_0_4_node_73 | 0.4 | n |  | TRUE
64 | bus_LV_1010-7_0_4_node_78 | 0.4 | n |  | TRUE
65 | bus_LV_1010-7_0_4_node_77 | 0.4 | n |  | TRUE
66 | bus_LV_1010-7_0_4_node_45 | 0.4 | n |  | TRUE
67 | bus_LV_1010-7_0_4_node_87 | 0.4 | n |  | TRUE
68 | bus_LV_1010-7_0_4_node_71 | 0.4 | n |  | TRUE
69 | bus_LV_1010-7_0_4_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_1010-7_0_4_node_47 | 0.4 | n |  | TRUE
71 | bus_LV_1010-7_0_4_node_48 | 0.4 | n |  | TRUE
72 | bus_LV_1010-7_0_4_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_1010-7_0_4_node_50 | 0.4 | n |  | TRUE
74 | bus_LV_1010-7_0_4_node_72 | 0.4 | n |  | TRUE
75 | bus_LV_1010-7_0_4_node_69 | 0.4 | n |  | TRUE
76 | bus_LV_1010-7_0_4_node_70 | 0.4 | n |  | TRUE
77 | bus_LV_1010-7_0_4_node_52 | 0.4 | n |  | TRUE
78 | bus_LV_1010-7_0_4_node_83 | 0.4 | n |  | TRUE
79 | bus_LV_1010-7_0_4_node_82 | 0.4 | n |  | TRUE
80 | bus_LV_1010-7_0_4_node_54 | 0.4 | n |  | TRUE
81 | bus_LV_1010-7_0_4_node_55 | 0.4 | n |  | TRUE
82 | bus_LV_1010-7_0_4_node_56 | 0.4 | n |  | TRUE
83 | bus_LV_1010-7_0_4_node_58 | 0.4 | n |  | TRUE
84 | bus_LV_1010-7_0_4_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_1010-7_0_4_node_86 | 0.4 | n |  | TRUE
86 | bus_LV_1010-7_0_4_node_59 | 0.4 | n |  | TRUE
87 | bus_LV_1010-7_0_4_node_60 | 0.4 | n |  | TRUE
88 | bus_LV_1010-7_0_4_node_61 | 0.4 | n |  | TRUE
89 | bus_LV_1010-7_0_4_node_62 | 0.4 | n |  | TRUE
90 | bus_LV_1010-7_0_4_node_63 | 0.4 | n |  | TRUE
91 | bus_LV_1010-7_0_4_node_64 | 0.4 | n |  | TRUE
92 | bus_LV_1010-7_0_4_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_1010-7_0_4_node_65 | 0.4 | n |  | TRUE
94 | bus_LV_1010-7_0_4_node_66 | 0.4 | n |  | TRUE
95 | bus_LV_1010-7_0_4_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_1010-7_0_4_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_1010-7_0_4_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_1010-7_0_4_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_1010-7_0_4_node_94 | 0.4 | n |  | TRUE
100 | bus_LV_1010-7_0_4_node_85 | 0.4 | n |  | TRUE
101 | bus_LV_1010-7_0_4_node_106 | 0.4 | n |  | TRUE
102 | bus_LV_1010-7_0_4_node_100 | 0.4 | n |  | TRUE
103 | bus_LV_1010-7_0_4_node_91 | 0.4 | n |  | TRUE
104 | bus_LV_1010-7_0_4_node_99 | 0.4 | n |  | TRUE
105 | bus_LV_1010-7_0_4_node_88 | 0.4 | n |  | TRUE
106 | bus_LV_1010-7_0_4_node_89 | 0.4 | n |  | TRUE
107 | bus_LV_1010-7_0_4_node_90 | 0.4 | n |  | TRUE
108 | bus_LV_1010-7_0_4_node_92 | 0.4 | n |  | TRUE
109 | bus_LV_1010-7_0_4_node_96 | 0.4 | n |  | TRUE
110 | bus_LV_1010-7_0_4_node_95 | 0.4 | n |  | TRUE
111 | bus_LV_1010-7_0_4_node_97 | 0.4 | n |  | TRUE
112 | bus_LV_1010-7_0_4_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_1010-7_0_4_node_102 | 0.4 | n |  | TRUE
114 | bus_LV_1010-7_0_4_node_107 | 0.4 | n |  | TRUE
115 | bus_LV_1010-7_0_4_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_1010-7_0_4_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_1010-7_0_4_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_1010-7_0_4_node_110 | 0.4 | n |  | TRUE
119 | bus_LV_1010-7_0_4_node_111 | 0.4 | n |  | TRUE
120 | bus_LV_1010-7_0_4_node_113 | 0.4 | n |  | TRUE
121 | bus_LV_1010-7_0_4_node_116 | 0.4 | n |  | TRUE
122 | bus_LV_1010-7_0_4_node_115 | 0.4 | n |  | TRUE
123 | bus_MV_126_0_node_42 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1010-7_0_4_load_0 | 0 | 0.00018352 | 4.5994e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1010-7_0_4_load_2 | 2 | 0.00072053 | 0.00018058 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1010-7_0_4_load_119 | 4 | 0.00011714 | 2.9359e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1010-7_0_4_load_4 | 9 | 0.00026578 | 6.6612e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1010-7_0_4_load_20 | 11 | 0.0005811 | 0.00014564 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1010-7_0_4_load_5 | 12 | 0.00062189 | 0.00015586 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1010-7_0_4_load_25 | 14 | 0.00036273 | 9.0908e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1010-7_0_4_load_19 | 15 | 0.00020106 | 5.0391e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1010-7_0_4_load_7 | 16 | 0.00024457 | 6.1294e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1010-7_0_4_load_123 | 22 | 0.0005312 | 0.00013313 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1010-7_0_4_load_121 | 23 | 0.00024457 | 6.1294e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1010-7_0_4_load_29 | 24 | 0.00015161 | 3.7997e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1010-7_0_4_load_125 | 25 | 0.00029656 | 7.4324e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1010-7_0_4_load_126 | 26 | 0.0012455 | 0.00031214 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1010-7_0_4_load_122 | 27 | 0.00031337 | 7.8539e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1010-7_0_4_load_13 | 29 | 0.00010355 | 2.5952e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1010-7_0_4_load_124 | 31 | 0.00012303 | 3.0835e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1010-7_0_4_load_30 | 33 | 0.00034458 | 8.636e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1010-7_0_4_load_22 | 35 | 0.00046276 | 0.00011598 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1010-7_0_4_load_31 | 36 | 0.00098676 | 0.0002473 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1010-7_0_4_load_21 | 38 | 8.7435e-05 | 2.1913e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1010-7_0_4_load_28 | 39 | 0.00015464 | 3.8755e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1010-7_0_4_load_117 | 40 | 0.00064124 | 0.00016071 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1010-7_0_4_load_24 | 41 | 0.00037981 | 9.5189e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1010-7_0_4_load_26 | 42 | 0.00096102 | 0.00024086 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1010-7_0_4_load_32 | 44 | 0.0038743 | 0.00097098 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1010-7_0_4_load_38 | 46 | 0.011215 | 0.0028109 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1010-7_0_4_load_39 | 47 | 0.0033093 | 0.00082939 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1010-7_0_4_load_53 | 49 | 0.0052529 | 0.0013165 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1010-7_0_4_load_75 | 53 | 0.0046171 | 0.0011571 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1010-7_0_4_load_57 | 56 | 0.0062269 | 0.0015606 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1010-7_0_4_load_103 | 57 | 0.0072588 | 0.0018192 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1010-7_0_4_load_40 | 59 | 0.0022231 | 0.00055715 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1010-7_0_4_load_78 | 64 | 0.0027707 | 0.0006944 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1010-7_0_4_load_77 | 65 | 0.0025541 | 0.00064013 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1010-7_0_4_load_87 | 67 | 0.0045842 | 0.0011489 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1010-7_0_4_load_71 | 68 | 0.0067141 | 0.0016827 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1010-7_0_4_load_46 | 69 | 0.0017792 | 0.0004459 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1010-7_0_4_load_48 | 71 | 0.0029996 | 0.00075176 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1010-7_0_4_load_49 | 72 | 0.0023451 | 0.00058773 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1010-7_0_4_load_50 | 73 | 0.0019303 | 0.00048379 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1010-7_0_4_load_72 | 74 | 0.0042757 | 0.0010716 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1010-7_0_4_load_69 | 75 | 0.0063361 | 0.001588 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1010-7_0_4_load_70 | 76 | 0.0025912 | 0.00064942 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1010-7_0_4_load_52 | 77 | 0.0026975 | 0.00067606 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1010-7_0_4_load_83 | 78 | 0.00058961 | 0.00014777 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1010-7_0_4_load_82 | 79 | 0.0029374 | 0.00073619 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1010-7_0_4_load_54 | 80 | 0.0050323 | 0.0012612 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1010-7_0_4_load_55 | 81 | 0.0030872 | 0.00077373 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1010-7_0_4_load_56 | 82 | 0.0027174 | 0.00068105 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1010-7_0_4_load_76 | 84 | 0.0018811 | 0.00047145 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1010-7_0_4_load_86 | 85 | 0.0018909 | 0.00047391 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1010-7_0_4_load_59 | 86 | 0.014845 | 0.0037206 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1010-7_0_4_load_60 | 87 | 0.0049779 | 0.0012476 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1010-7_0_4_load_62 | 89 | 0.0017329 | 0.0004343 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1010-7_0_4_load_63 | 90 | 0.0057326 | 0.0014367 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1010-7_0_4_load_64 | 91 | 0.0044933 | 0.0011261 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1010-7_0_4_load_79 | 92 | 0.0026865 | 0.00067329 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1010-7_0_4_load_65 | 93 | 0.0077998 | 0.0019548 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1010-7_0_4_load_66 | 94 | 0.0050352 | 0.0012619 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1010-7_0_4_load_80 | 96 | 0.00224 | 0.00056141 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1010-7_0_4_load_81 | 97 | 0.0039303 | 0.00098502 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1010-7_0_4_load_93 | 98 | 0.0016934 | 0.00042442 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1010-7_0_4_load_106 | 101 | 0.0049001 | 0.0012281 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1010-7_0_4_load_100 | 102 | 0.0043419 | 0.0010882 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1010-7_0_4_load_99 | 104 | 0.0023933 | 0.00059983 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1010-7_0_4_load_88 | 105 | 0.0028716 | 0.0007197 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1010-7_0_4_load_89 | 106 | 0.0023472 | 0.00058826 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1010-7_0_4_load_90 | 107 | 0.0029324 | 0.00073493 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1010-7_0_4_load_92 | 108 | 0.0014796 | 0.00037083 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1010-7_0_4_load_96 | 109 | 0.0030826 | 0.00077258 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1010-7_0_4_load_95 | 110 | 0.0053217 | 0.0013338 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1010-7_0_4_load_97 | 111 | 0.00094163 | 0.000236 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1010-7_0_4_load_102 | 113 | 0.00098814 | 0.00024765 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1010-7_0_4_load_107 | 114 | 0.00022525 | 5.6454e-05 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1010-7_0_4_load_111 | 119 | 0.00030052 | 7.5318e-05 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1010-7_0_4_load_113 | 120 | 0.00035768 | 8.9644e-05 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1010-7_0_4_load_116 | 121 | 0.0018548 | 0.00046486 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1010-7_0_4_load_115 | 122 | 0.0022187 | 0.00055605 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 106 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1010-7_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1010-7_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.020195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1010-7_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.34086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1010-7_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.36589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1010-7_0_4_line_4 | NAYY 4x150 SE | 3 | 8 | 0.033204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1010-7_0_4_line_5 | NAYY 4x150 SE | 3 | 9 | 0.33377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1010-7_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.53396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1010-7_0_4_line_7 | NAYY 4x150 SE | 5 | 7 | 0.05434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1010-7_0_4_line_8 | NAYY 4x150 SE | 6 | 122 | 0.068424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1010-7_0_4_line_9 | NAYY 4x150 SE | 7 | 111 | 0.026305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1010-7_0_4_line_10 | NAYY 4x150 SE | 8 | 10 | 0.18035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1010-7_0_4_line_11 | NAYY 4x150 SE | 8 | 11 | 0.018403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1010-7_0_4_line_12 | NAYY 4x150 SE | 9 | 12 | 0.0026175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1010-7_0_4_line_13 | NAYY 4x150 SE | 10 | 13 | 0.056764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1010-7_0_4_line_14 | NAYY 4x150 SE | 10 | 14 | 0.034117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1010-7_0_4_line_15 | NAYY 4x150 SE | 11 | 15 | 0.012302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1010-7_0_4_line_16 | NAYY 4x150 SE | 13 | 31 | 0.15069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1010-7_0_4_line_17 | NAYY 4x150 SE | 14 | 37 | 0.032552 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1010-7_0_4_line_18 | NAYY 4x150 SE | 15 | 38 | 0.30489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1010-7_0_4_line_19 | NAYY 4x150 SE | 16 | 17 | 0.011613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1010-7_0_4_line_20 | NAYY 4x150 SE | 16 | 18 | 0.019448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1010-7_0_4_line_21 | NAYY 4x150 SE | 17 | 19 | 0.025038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1010-7_0_4_line_22 | NAYY 4x150 SE | 18 | 20 | 0.003801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1010-7_0_4_line_23 | NAYY 4x150 SE | 18 | 21 | 0.040172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1010-7_0_4_line_24 | NAYY 4x150 SE | 19 | 22 | 0.010047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1010-7_0_4_line_25 | NAYY 4x150 SE | 19 | 23 | 0.0092387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1010-7_0_4_line_26 | NAYY 4x150 SE | 20 | 25 | 0.008985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1010-7_0_4_line_27 | NAYY 4x150 SE | 20 | 26 | 0.018849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1010-7_0_4_line_28 | NAYY 4x150 SE | 21 | 24 | 0.18994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1010-7_0_4_line_29 | NAYY 4x150 SE | 23 | 27 | 0.021903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1010-7_0_4_line_30 | NAYY 4x150 SE | 24 | 28 | 0.12041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1010-7_0_4_line_31 | NAYY 4x150 SE | 28 | 34 | 0.17544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1010-7_0_4_line_32 | NAYY 4x150 SE | 28 | 30 | 0.10905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1010-7_0_4_line_33 | NAYY 4x150 SE | 28 | 32 | 0.015868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1010-7_0_4_line_34 | NAYY 4x150 SE | 29 | 30 | 0.011541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1010-7_0_4_line_35 | NAYY 4x150 SE | 32 | 33 | 0.021266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1010-7_0_4_line_36 | NAYY 4x150 SE | 33 | 36 | 0.023971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1010-7_0_4_line_37 | NAYY 4x150 SE | 34 | 35 | 0.04152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1010-7_0_4_line_38 | NAYY 4x150 SE | 35 | 37 | 0.0085857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1010-7_0_4_line_39 | NAYY 4x150 SE | 37 | 41 | 0.011601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1010-7_0_4_line_40 | NAYY 4x150 SE | 38 | 39 | 0.25866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_1010-7_0_4_line_41 | NAYY 4x150 SE | 39 | 40 | 0.37829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1010-7_0_4_line_42 | NAYY 4x150 SE | 40 | 43 | 0.050431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_1010-7_0_4_line_43 | NAYY 4x150 SE | 41 | 42 | 0.051764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1010-7_0_4_line_44 | NAYY 4x150 SE | 43 | 118 | 0.38145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
45 | LV_1010-7_0_4_line_45 | NAYY 4x150 SE | 44 | 45 | 0.022326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1010-7_0_4_line_46 | NAYY 4x150 SE | 45 | 46 | 0.00068522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1010-7_0_4_line_47 | NAYY 4x150 SE | 45 | 47 | 0.024967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1010-7_0_4_line_48 | NAYY 4x150 SE | 46 | 48 | 0.011255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1010-7_0_4_line_49 | NAYY 4x150 SE | 47 | 55 | 0.0080692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1010-7_0_4_line_50 | NAYY 4x150 SE | 48 | 49 | 0.013868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1010-7_0_4_line_51 | NAYY 4x150 SE | 49 | 50 | 0.012949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1010-7_0_4_line_52 | NAYY 4x150 SE | 50 | 51 | 0.015735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1010-7_0_4_line_53 | NAYY 4x150 SE | 51 | 53 | 0.022925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1010-7_0_4_line_54 | NAYY 4x150 SE | 51 | 56 | 0.011556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_1010-7_0_4_line_55 | NAYY 4x150 SE | 52 | 53 | 0.012948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1010-7_0_4_line_56 | NAYY 4x150 SE | 52 | 54 | 0.009319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1010-7_0_4_line_57 | NAYY 4x150 SE | 54 | 57 | 0.017358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1010-7_0_4_line_58 | NAYY 4x150 SE | 54 | 58 | 0.013337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1010-7_0_4_line_59 | NAYY 4x150 SE | 55 | 59 | 0.023329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1010-7_0_4_line_60 | NAYY 4x150 SE | 56 | 81 | 0.0076002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
61 | LV_1010-7_0_4_line_61 | NAYY 4x150 SE | 57 | 91 | 0.0014077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1010-7_0_4_line_62 | NAYY 4x150 SE | 58 | 94 | 0.011457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1010-7_0_4_line_63 | NAYY 4x150 SE | 59 | 60 | 0.020089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1010-7_0_4_line_64 | NAYY 4x150 SE | 60 | 61 | 0.013736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1010-7_0_4_line_65 | NAYY 4x150 SE | 61 | 65 | 0.010952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1010-7_0_4_line_66 | NAYY 4x150 SE | 62 | 63 | 0.006995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1010-7_0_4_line_67 | NAYY 4x150 SE | 62 | 64 | 0.012003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1010-7_0_4_line_68 | NAYY 4x150 SE | 63 | 68 | 0.017993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1010-7_0_4_line_69 | NAYY 4x150 SE | 63 | 66 | 0.039858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1010-7_0_4_line_70 | NAYY 4x150 SE | 64 | 65 | 0.0014316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1010-7_0_4_line_71 | NAYY 4x150 SE | 66 | 67 | 0.021912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1010-7_0_4_line_72 | NAYY 4x150 SE | 68 | 74 | 0.0012063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1010-7_0_4_line_73 | NAYY 4x150 SE | 69 | 70 | 0.01101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1010-7_0_4_line_74 | NAYY 4x150 SE | 70 | 71 | 0.015061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1010-7_0_4_line_75 | NAYY 4x150 SE | 70 | 72 | 0.036043 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1010-7_0_4_line_76 | NAYY 4x150 SE | 70 | 73 | 0.012991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1010-7_0_4_line_77 | NAYY 4x150 SE | 73 | 74 | 0.033422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1010-7_0_4_line_78 | NAYY 4x150 SE | 75 | 76 | 0.0020408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1010-7_0_4_line_79 | NAYY 4x150 SE | 76 | 83 | 0.023302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1010-7_0_4_line_80 | NAYY 4x150 SE | 77 | 78 | 0.017367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1010-7_0_4_line_81 | NAYY 4x150 SE | 78 | 79 | 0.022891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1010-7_0_4_line_82 | NAYY 4x150 SE | 79 | 95 | 0.022368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1010-7_0_4_line_83 | NAYY 4x150 SE | 80 | 81 | 0.012191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
84 | LV_1010-7_0_4_line_84 | NAYY 4x150 SE | 80 | 82 | 0.014064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
85 | LV_1010-7_0_4_line_85 | NAYY 4x150 SE | 82 | 83 | 0.01348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
86 | LV_1010-7_0_4_line_86 | NAYY 4x150 SE | 83 | 84 | 0.0006718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
87 | LV_1010-7_0_4_line_87 | NAYY 4x150 SE | 84 | 85 | 0.019864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
88 | LV_1010-7_0_4_line_88 | NAYY 4x150 SE | 85 | 95 | 0.022211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_1010-7_0_4_line_89 | NAYY 4x150 SE | 86 | 87 | 0.0081836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1010-7_0_4_line_90 | NAYY 4x150 SE | 86 | 88 | 0.01364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1010-7_0_4_line_91 | NAYY 4x150 SE | 87 | 89 | 0.052771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1010-7_0_4_line_92 | NAYY 4x150 SE | 88 | 90 | 0.0087899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1010-7_0_4_line_93 | NAYY 4x150 SE | 88 | 91 | 0.012986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1010-7_0_4_line_94 | NAYY 4x150 SE | 90 | 92 | 0.0067102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1010-7_0_4_line_95 | NAYY 4x150 SE | 93 | 94 | 0.0074056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1010-7_0_4_line_96 | NAYY 4x150 SE | 95 | 100 | 0.005484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
97 | LV_1010-7_0_4_line_97 | NAYY 4x150 SE | 96 | 97 | 0.001765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1010-7_0_4_line_98 | NAYY 4x150 SE | 97 | 98 | 0.018949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1010-7_0_4_line_99 | NAYY 4x150 SE | 98 | 99 | 0.0091403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1010-7_0_4_line_100 | NAYY 4x150 SE | 99 | 110 | 0.027924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1010-7_0_4_line_101 | NAYY 4x150 SE | 99 | 103 | 0.010823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1010-7_0_4_line_102 | NAYY 4x150 SE | 100 | 101 | 0.016257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
103 | LV_1010-7_0_4_line_103 | NAYY 4x150 SE | 100 | 102 | 0.022117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1010-7_0_4_line_104 | NAYY 4x150 SE | 101 | 103 | 0.014039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
105 | LV_1010-7_0_4_line_105 | NAYY 4x150 SE | 102 | 104 | 0.0048886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1010-7_0_4_line_106 | NAYY 4x150 SE | 103 | 106 | 0.0092074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
107 | LV_1010-7_0_4_line_107 | NAYY 4x150 SE | 104 | 112 | 0.0052148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1010-7_0_4_line_108 | NAYY 4x150 SE | 105 | 106 | 0.015094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
109 | LV_1010-7_0_4_line_109 | NAYY 4x150 SE | 105 | 107 | 0.014585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
110 | LV_1010-7_0_4_line_110 | NAYY 4x150 SE | 107 | 108 | 0.0064188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
111 | LV_1010-7_0_4_line_111 | NAYY 4x150 SE | 108 | 109 | 0.003527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
112 | LV_1010-7_0_4_line_112 | NAYY 4x150 SE | 109 | 111 | 0.02287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
113 | LV_1010-7_0_4_line_113 | NAYY 4x150 SE | 112 | 113 | 0.013898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1010-7_0_4_line_114 | NAYY 4x150 SE | 114 | 115 | 0.0086428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1010-7_0_4_line_115 | NAYY 4x150 SE | 115 | 116 | 0.012468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1010-7_0_4_line_116 | NAYY 4x150 SE | 116 | 120 | 0.0030362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1010-7_0_4_line_117 | NAYY 4x150 SE | 117 | 118 | 0.19845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
118 | LV_1010-7_0_4_line_118 | NAYY 4x150 SE | 117 | 119 | 0.0899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1010-7_0_4_line_119 | NAYY 4x150 SE | 117 | 120 | 0.17352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
120 | LV_1010-7_0_4_line_120 | NAYY 4x150 SE | 119 | 121 | 0.33518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
121 | LV_1010-7_0_4_line_121 | NAYY 4x150 SE | 120 | 122 | 0.17755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1010-7_0_4_trafo_89 | 0.25 MVA 20/0.4 kV | 123 | 106 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36
0 | 2636095.8804 | 1196676.8999 | 2636090.5367 | 1196697.7903 | 2636079.9665 | 1196741.6284 | 2636079.8361 | 1196775.9736
1 | 2636079.7595 | 1196796.1683 | 2636079.8361 | 1196775.9736
2 | 2636095.8804 | 1196676.8999 | 2636109.3668 | 1196614.3691 | 2636143.2082 | 1196559.1763 | 2636171.6522 | 1196449.3656 | 2636207.5984 | 1196412.9073 | 2636212.7755 | 1196404.5451 | 2636224.4438 | 1196379.6576 | 2636230.8382 | 1196371.5585
3 | 2636095.8804 | 1196676.8999 | 2635744.301 | 1196575.5784
4 | 2636230.8382 | 1196371.5585 | 2636235.2965 | 1196367.4388 | 2636242.5372 | 1196363.0024 | 2636250.3691 | 1196360.3039 | 2636260.4482 | 1196357.6079
5 | 2636230.8382 | 1196371.5585 | 2636217.3669 | 1196409.898 | 2636210.2155 | 1196423.5289 | 2636201.2839 | 1196438.0273 | 2636191.7422 | 1196452.6555 | 2636187.5224 | 1196462.7021 | 2636186.3649 | 1196473.968 | 2636184.8859 | 1196500.6292 | 2636187.0697 | 1196511.1038 | 2636191.6618 | 1196520.1031 | 2636198.2643 | 1196526.6911 | 2636211.5104 | 1196533.0525 | 2636229.6205 | 1196537.4533 | 2636244.1576 | 1196538.1639 | 2636253.2216 | 1196539.5196 | 2636258.8229 | 1196541.5991 | 2636262.6854 | 1196545.28 | 2636266.6235 | 1196552.8414 | 2636268.0313 | 1196556.8299 | 2636270.5425 | 1196568.5515 | 2636272.6627 | 1196573.1558 | 2636277.0493 | 1196577.0845 | 2636285.2071 | 1196579.6354 | 2636298.9672 | 1196584.099 | 2636307.6259 | 1196588.2204 | 2636314.6561 | 1196593.3103 | 2636325.261 | 1196604.3251 | 2636327.4232 | 1196607.1493
6 | 2637610.5692 | 1196177.4933 | 2637353.2529 | 1196645.3621
7 | 2637614.0135 | 1196136.1255 | 2637595.913 | 1196154.3886 | 2637607.8084 | 1196165.8696 | 2637609.0897 | 1196168.0566 | 2637609.7706 | 1196171.2293 | 2637610.5692 | 1196177.4933
8 | 2637353.2529 | 1196645.3621 | 2637334.3578 | 1196643.6433 | 2637322.2134 | 1196642.856 | 2637312.677 | 1196642.7965 | 2637298.6516 | 1196644.3767 | 2637297.011 | 1196644.8334 | 2637291.4723 | 1196648.6677 | 2637287.4817 | 1196651.9881
9 | 2637614.0135 | 1196136.1255 | 2637613.2479 | 1196129.4504 | 2637613.0832 | 1196125.3582 | 2637613.4574 | 1196122.7925 | 2637614.6974 | 1196119.4318 | 2637619.0982 | 1196111.2212
10 | 2636414.7409 | 1196265.0045 | 2636401.7943 | 1196271.963 | 2636390.4424 | 1196279.7427 | 2636370.7063 | 1196295.8538 | 2636352.5535 | 1196308.3949 | 2636339.1894 | 1196315.1397 | 2636317.3945 | 1196325.3575 | 2636300.7662 | 1196335.251 | 2636286.8613 | 1196344.5274 | 2636277.662 | 1196350.3637 | 2636268.8139 | 1196354.8125 | 2636260.4482 | 1196357.6079
11 | 2636260.4482 | 1196357.6079 | 2636264.2756 | 1196368.3592 | 2636266.2917 | 1196375.0528 | 2636266.2917 | 1196375.0528
12 | 2636329.0144 | 1196609.2276 | 2636327.4232 | 1196607.1493
13 | 2636414.7409 | 1196265.0045 | 2636408.7511 | 1196257.8753 | 2636405.2798 | 1196253.7408 | 2636400.969 | 1196248.6007 | 2636382.6032 | 1196229.7454 | 2636375.6995 | 1196223.8224
14 | 2636414.7409 | 1196265.0045 | 2636421.0025 | 1196262.519 | 2636432.0692 | 1196259.0511 | 2636447.5183 | 1196255.8204
15 | 2636276.9101 | 1196380.0875 | 2636272.2994 | 1196379.2471 | 2636268.3322 | 1196377.7333 | 2636266.2917 | 1196375.0528
16 | 2636375.6995 | 1196223.8224 | 2636371.8966 | 1196222.8321 | 2636366.7712 | 1196222.623 | 2636362.3186 | 1196224.5193 | 2636351.6139 | 1196229.835 | 2636345.0795 | 1196232.0854 | 2636338.047 | 1196233.5546 | 2636326.858 | 1196234.5984 | 2636312.817 | 1196234.8579 | 2636297.1008 | 1196232.5057 | 2636287.8852 | 1196230.949 | 2636281.611 | 1196230.4885 | 2636271.4745 | 1196231.3164 | 2636240.7716 | 1196235.6885 | 2636238.4926 | 1196235.9081 | 2636235.8153 | 1196236.47 | 2636227.7197 | 1196237.4104
17 | 2636479.2259 | 1196248.488 | 2636463.4254 | 1196252.494 | 2636447.5183 | 1196255.8204
18 | 2636531.352 | 1196409.7277 | 2636527.7792 | 1196409.7504 | 2636524.5287 | 1196408.1519 | 2636522.3539 | 1196406.282 | 2636517.2698 | 1196400.5812 | 2636512.4346 | 1196394.0259 | 2636502.4714 | 1196385.2048 | 2636500.458 | 1196381.8573 | 2636499.1542 | 1196377.0467 | 2636498.7975 | 1196371.8417 | 2636500.8907 | 1196362.1158 | 2636500.5718 | 1196356.9554 | 2636499.0748 | 1196353.8557 | 2636496.331 | 1196350.3482 | 2636490.8457 | 1196347.969 | 2636484.6843 | 1196346.5195 | 2636477.4427 | 1196346.0752 | 2636468.3293 | 1196346.5421 | 2636457.5806 | 1196347.8552 | 2636444.9414 | 1196350.6353 | 2636426.6449 | 1196356.7607 | 2636396.7996 | 1196364.2388 | 2636386.4065 | 1196364.7092 | 2636376.4238 | 1196365.3267 | 2636364.9403 | 1196368.4698 | 2636360.6866 | 1196368.9776 | 2636356.7061 | 1196368.4197 | 2636350.5338 | 1196367.5151 | 2636347.3165 | 1196367.9514 | 2636343.2765 | 1196369.6611 | 2636338.7019 | 1196372.8351 | 2636331.7722 | 1196378.7518 | 2636324.678 | 1196382.9 | 2636317.2276 | 1196385.4784 | 2636312.3054 | 1196385.6931 | 2636307.3772 | 1196385.641 | 2636276.9101 | 1196380.0875
19 | 2637040.6897 | 1196251.6258 | 2637040.3243 | 1196254.0471 | 2637039.1207 | 1196256.5188 | 2637036.8671 | 1196258.7727 | 2637034.054 | 1196260.3562
20 | 2637014.7903 | 1196258.9141 | 2637019.6519 | 1196259.8891 | 2637029.9675 | 1196260.909 | 2637034.054 | 1196260.3562
21 | 2637057.1968 | 1196270.1492 | 2637055.9579 | 1196267.2288 | 2637053.5716 | 1196263.8678 | 2637046.598 | 1196257.0431 | 2637040.6897 | 1196251.6258
22 | 2637014.7903 | 1196258.9141 | 2637011.6008 | 1196260.9955
23 | 2637004.586 | 1196222.6422 | 2637007.5155 | 1196251.4983 | 2637008.3276 | 1196254.4494 | 2637009.2999 | 1196256.1341 | 2637011.3335 | 1196257.4141 | 2637014.7903 | 1196258.9141
24 | 2637057.1968 | 1196270.1492 | 2637061.299 | 1196267.0507 | 2637064.3623 | 1196263.2009
25 | 2637057.1968 | 1196270.1492 | 2637057.1734 | 1196273.9178 | 2637056.0518 | 1196279.2716
26 | 2637011.6008 | 1196260.9955 | 2637011.4386 | 1196269.9772
27 | 2636992.7427 | 1196261.7127 | 2637007.514 | 1196261.6039 | 2637011.6008 | 1196260.9955
28 | 2637004.586 | 1196222.6422 | 2636957.5286 | 1196223.0962 | 2636941.0259 | 1196222.3161 | 2636922.9832 | 1196220.4816 | 2636815.667 | 1196206.4795
29 | 2637051.5609 | 1196300.7089 | 2637056.0518 | 1196279.2716
30 | 2636695.8802 | 1196197.5173 | 2636726.5788 | 1196196.4271 | 2636751.6459 | 1196198.1263 | 2636815.667 | 1196206.4795
31 | 2636524.4607 | 1196227.0965 | 2636551.0864 | 1196215.5748 | 2636565.0778 | 1196210.9577 | 2636578.7171 | 1196207.8838 | 2636597.6516 | 1196204.6533 | 2636623.3006 | 1196202.1532 | 2636673.7913 | 1196198.3602 | 2636677.1899 | 1196198.1809 | 2636695.8802 | 1196197.5173
32 | 2636672.0985 | 1196119.0729 | 2636672.658 | 1196119.7656 | 2636673.0934 | 1196120.8022 | 2636673.1771 | 1196122.0701 | 2636672.96 | 1196123.9253 | 2636672.4064 | 1196126.0119 | 2636670.0926 | 1196133.1461 | 2636666.4937 | 1196142.3847 | 2636662.8955 | 1196150.2559 | 2636659.1699 | 1196157.8039 | 2636658.2333 | 1196160.2217 | 2636657.5083 | 1196162.9299 | 2636657.3392 | 1196165.6637 | 2636657.5497 | 1196168.611 | 2636658.2112 | 1196171.3054 | 2636659.6747 | 1196174.883 | 2636667.6036 | 1196188.7614 | 2636669.8194 | 1196192.6438 | 2636673.7913 | 1196198.3602 | 2636677.1899 | 1196198.1809 | 2636695.8802 | 1196197.5173
33 | 2636695.8802 | 1196197.5173 | 2636691.0596 | 1196207.2264 | 2636690.0543 | 1196212.1563
34 | 2636672.0985 | 1196119.0729 | 2636673.5765 | 1196109.0987 | 2636673.3301 | 1196107.6622
35 | 2636690.0543 | 1196212.1563 | 2636693.0736 | 1196216.6995 | 2636698.0116 | 1196221.3879 | 2636701.9369 | 1196223.502 | 2636706.3329 | 1196224.6518
36 | 2636730.0415 | 1196221.7956 | 2636711.4658 | 1196224.8945 | 2636706.3329 | 1196224.6518
37 | 2636524.4607 | 1196227.0965 | 2636507.3337 | 1196236.2415 | 2636492.4428 | 1196243.4658 | 2636487.264 | 1196245.4712
38 | 2636479.2259 | 1196248.488 | 2636485.4332 | 1196246.1801 | 2636487.264 | 1196245.4712
39 | 2636479.2259 | 1196248.488 | 2636484.4245 | 1196257.9471 | 2636484.9229 | 1196258.5826
40 | 2636531.352 | 1196409.7277 | 2636605.9103 | 1196657.4138
41 | 2636605.9103 | 1196657.4138 | 2636553.3864 | 1197032.0377
42 | 2636573.2052 | 1197077.217 | 2636565.48 | 1197068.8096 | 2636561.3238 | 1197053.4535 | 2636559.6601 | 1197044.0159 | 2636553.3864 | 1197032.0377
43 | 2636533.7263 | 1196252.8894 | 2636529.9652 | 1196253.8114 | 2636517.6095 | 1196253.7916 | 2636512.9066 | 1196254.2409 | 2636506.1843 | 1196256.0676 | 2636492.5911 | 1196261.61 | 2636490.1731 | 1196262.1289 | 2636488.2933 | 1196261.8506 | 2636486.9567 | 1196261.1754 | 2636484.9229 | 1196258.5826
44 | 2636912.1124 | 1196902.1562 | 2636573.2052 | 1197077.217
45 | 2637791.804 | 1196036.3125 | 2637810.2569 | 1196023.7448
46 | 2637791.804 | 1196036.3125 | 2637791.3869 | 1196035.7688
47 | 2637791.804 | 1196036.3125 | 2637806.9314 | 1196056.1746
48 | 2637784.5354 | 1196026.8391 | 2637791.3869 | 1196035.7688
49 | 2637811.7261 | 1196062.6638 | 2637809.2794 | 1196059.2576 | 2637806.9314 | 1196056.1746
50 | 2637784.5354 | 1196026.8391 | 2637777.7579 | 1196017.9915 | 2637776.1086 | 1196015.8252
51 | 2637768.2608 | 1196005.5247 | 2637769.5679 | 1196007.2339 | 2637776.1086 | 1196015.8252
52 | 2637758.6648 | 1195993.0351 | 2637768.2608 | 1196005.5247
53 | 2637758.6648 | 1195993.0351 | 2637752.6719 | 1195985.3931 | 2637747.0388 | 1195978.6761 | 2637744.0297 | 1195975.402
54 | 2637758.6648 | 1195993.0351 | 2637749.2594 | 1195999.7492
55 | 2637735.2276 | 1195965.9058 | 2637740.7287 | 1195971.8104 | 2637744.0297 | 1195975.402
56 | 2637735.2276 | 1195965.9058 | 2637728.8256 | 1195959.1172
57 | 2637728.8256 | 1195959.1172 | 2637718.3726 | 1195972.9748
58 | 2637719.2167 | 1195949.8405 | 2637728.8256 | 1195959.1172
59 | 2637811.7261 | 1196062.6638 | 2637817.1004 | 1196060.8746 | 2637819.5547 | 1196060.6677 | 2637822.8593 | 1196060.9221 | 2637830.8721 | 1196062.3179 | 2637834.5169 | 1196063.2143
60 | 2637749.2594 | 1195999.7492 | 2637746.1453 | 1196001.9722 | 2637743.4213 | 1196004.5843
61 | 2637718.3726 | 1195972.9748 | 2637717.5249 | 1195974.0986
62 | 2637719.2167 | 1195949.8405 | 2637710.9315 | 1195941.9267
63 | 2637854.025 | 1196068.0118 | 2637834.5169 | 1196063.2143
64 | 2637848.8026 | 1196080.7192 | 2637854.025 | 1196068.0118
65 | 2637848.8026 | 1196080.7192 | 2637847.2299 | 1196082.4546 | 2637844.4287 | 1196084.5158 | 2637839.7775 | 1196086.6857
66 | 2637829.6875 | 1196097.8633 | 2637827.1768 | 1196091.3328
67 | 2637827.1768 | 1196091.3328 | 2637838.4737 | 1196087.2756
68 | 2637829.6875 | 1196097.8633 | 2637812.6546 | 1196103.661
69 | 2637829.6875 | 1196097.8633 | 2637831.763 | 1196104.5468 | 2637834.6067 | 1196115.0483 | 2637836.9788 | 1196126.6252 | 2637838.6142 | 1196136.6522
70 | 2637839.7775 | 1196086.6857 | 2637838.6449 | 1196087.2141 | 2637838.4737 | 1196087.2756
71 | 2637838.6142 | 1196136.6522 | 2637830.7871 | 1196138.4148 | 2637830.7095 | 1196141.0602 | 2637830.3462 | 1196143.0924 | 2637829.2041 | 1196145.4087 | 2637826.7263 | 1196146.9383 | 2637823.1388 | 1196147.7742
72 | 2637812.6546 | 1196103.661 | 2637811.5126 | 1196104.0497
73 | 2637767.575 | 1196119.0051 | 2637770.8414 | 1196129.5197
74 | 2637767.575 | 1196119.0051 | 2637753.3804 | 1196124.039
75 | 2637767.575 | 1196119.0051 | 2637755.69 | 1196084.9783
76 | 2637767.575 | 1196119.0051 | 2637779.8728 | 1196114.8192
77 | 2637811.5126 | 1196104.0497 | 2637779.8728 | 1196114.8192
78 | 2637733.9015 | 1196052.5684 | 2637732.5162 | 1196051.0698
79 | 2637716.6982 | 1196033.9598 | 2637732.5162 | 1196051.0698
80 | 2637705.1638 | 1196108.414 | 2637707.6942 | 1196114.892 | 2637710.5908 | 1196124.8932
81 | 2637696.8351 | 1196087.0916 | 2637705.1638 | 1196108.414
82 | 2637688.6969 | 1196066.2568 | 2637696.8351 | 1196087.0916
83 | 2637734.8748 | 1196013.2654 | 2637737.7835 | 1196009.9906 | 2637743.4213 | 1196004.5843
84 | 2637734.8748 | 1196013.2654 | 2637728.9755 | 1196019.9072 | 2637725.5669 | 1196023.8087
85 | 2637716.6982 | 1196033.9598 | 2637725.5669 | 1196023.8087
86 | 2637716.6982 | 1196033.9598 | 2637716.255 | 1196034.4646
87 | 2637716.255 | 1196034.4646 | 2637703.1501 | 1196049.3921
88 | 2637688.6969 | 1196066.2568 | 2637698.7126 | 1196054.4467 | 2637703.1501 | 1196049.3921
89 | 2637698.6513 | 1195976.4743 | 2637694.9849 | 1195973.8233 | 2637693.7003 | 1195973.3816 | 2637692.6788 | 1195973.4864 | 2637691.495 | 1195973.957 | 2637691.495 | 1195973.957
90 | 2637709.7045 | 1195984.4663 | 2637698.6513 | 1195976.4743
91 | 2637656.7857 | 1196012.9894 | 2637657.4238 | 1196012.0191 | 2637658.774 | 1196010.5267 | 2637660.343 | 1196009.3582 | 2637663.6298 | 1196007.6112 | 2637667.1348 | 1196005.0652 | 2637669.8884 | 1196002.092 | 2637688.7897 | 1195976.5191 | 2637690.3619 | 1195974.8614 | 2637691.495 | 1195973.957
92 | 2637709.7045 | 1195984.4663 | 2637704.4094 | 1195991.4823
93 | 2637709.7045 | 1195984.4663 | 2637717.5249 | 1195974.0986
94 | 2637700.3672 | 1195996.8383 | 2637704.4094 | 1195991.4823
95 | 2637705.5763 | 1195936.8115 | 2637710.9315 | 1195941.9267
96 | 2637688.6969 | 1196066.2568 | 2637684.689 | 1196070.0114
97 | 2637683.4939 | 1196019.3129 | 2637682.4596 | 1196020.7431
98 | 2637671.3074 | 1196036.0627 | 2637673.7249 | 1196032.8219 | 2637682.4596 | 1196020.7431
99 | 2637665.8423 | 1196043.3893 | 2637671.3074 | 1196036.0627
100 | 2637665.8423 | 1196043.3893 | 2637658.1888 | 1196039.3611 | 2637655.6036 | 1196038.5778 | 2637652.9455 | 1196038.4943 | 2637649.9267 | 1196038.82 | 2637639.4622 | 1196042.0448
101 | 2637659.9725 | 1196052.4907 | 2637665.8423 | 1196043.3893
102 | 2637684.689 | 1196070.0114 | 2637671.4261 | 1196060.6097
103 | 2637684.689 | 1196070.0114 | 2637668.5351 | 1196085.1187
104 | 2637659.9725 | 1196052.4907 | 2637671.4261 | 1196060.6097
105 | 2637664.9646 | 1196088.4579 | 2637668.5351 | 1196085.1187
106 | 2637659.9725 | 1196052.4907 | 2637654.1988 | 1196059.6629
107 | 2637661.1559 | 1196092.0199 | 2637664.9646 | 1196088.4579
108 | 2637644.9115 | 1196071.5585 | 2637648.8242 | 1196066.3393 | 2637654.1988 | 1196059.6629
109 | 2637644.9115 | 1196071.5585 | 2637638.5298 | 1196080.071 | 2637636.2684 | 1196083.3044
110 | 2637636.2684 | 1196083.3044 | 2637635.2397 | 1196084.7751 | 2637633.4339 | 1196087.2652 | 2637632.5853 | 1196088.5599
111 | 2637630.6519 | 1196091.5098 | 2637632.5853 | 1196088.5599
112 | 2637630.6519 | 1196091.5098 | 2637625.2269 | 1196099.7871 | 2637619.0982 | 1196111.2212
113 | 2637661.1559 | 1196092.0199 | 2637669.2336 | 1196103.3289
114 | 2637102.9065 | 1196630.7084 | 2637098.4071 | 1196626.6338 | 2637096.2634 | 1196625.2114
115 | 2637102.9065 | 1196630.7084 | 2637108.6879 | 1196641.7614
116 | 2637108.6879 | 1196641.7614 | 2637110.093 | 1196644.4529
117 | 2637029.4464 | 1196798.0902 | 2637027.1916 | 1196801.8116 | 2637024.2886 | 1196804.4284 | 2636991.2375 | 1196813.2178 | 2636965.1431 | 1196817.9481 | 2636938.1923 | 1196819.5049 | 2636932.2074 | 1196820.424 | 2636929.8466 | 1196821.5879 | 2636929.0611 | 1196824.2067 | 2636929.8564 | 1196827.3911 | 2636936.0322 | 1196836.2897 | 2636940.0869 | 1196849.4442 | 2636941.642 | 1196857.8806 | 2636941.0107 | 1196863.9023 | 2636939.3558 | 1196869.1616 | 2636936.0697 | 1196874.6221 | 2636929.7583 | 1196880.3196 | 2636921.9954 | 1196886.6975 | 2636917.0528 | 1196892.7481 | 2636912.1124 | 1196902.1562
118 | 2637029.4464 | 1196798.0902 | 2637059.5136 | 1196844.335 | 2637066.8396 | 1196854.4081 | 2637074.0248 | 1196861.3787 | 2637079.5791 | 1196867.283 | 2637082.0258 | 1196870.6563
119 | 2637029.4464 | 1196798.0902 | 2637110.093 | 1196644.4529
120 | 2637082.0258 | 1196870.6563 | 2637141.892 | 1197200.4456
121 | 2637110.093 | 1196644.4529 | 2637287.4817 | 1196651.9881

## bus_geodata
| x | y | coords
0 | 2636079.8361 | 1196775.9736
1 | 2636095.8804 | 1196676.8999
2 | 2636079.7595 | 1196796.1683
3 | 2636230.8382 | 1196371.5585
4 | 2635744.301 | 1196575.5784
5 | 2637610.5692 | 1196177.4933
6 | 2637353.2529 | 1196645.3621
7 | 2637614.0135 | 1196136.1255
8 | 2636260.4482 | 1196357.6079
9 | 2636327.4232 | 1196607.1493
10 | 2636414.7409 | 1196265.0045
11 | 2636266.2917 | 1196375.0528
12 | 2636329.0144 | 1196609.2276
13 | 2636375.6995 | 1196223.8224
14 | 2636447.5183 | 1196255.8204
15 | 2636276.9101 | 1196380.0875
16 | 2637034.054 | 1196260.3562
17 | 2637040.6897 | 1196251.6258
18 | 2637014.7903 | 1196258.9141
19 | 2637057.1968 | 1196270.1492
20 | 2637011.6008 | 1196260.9955
21 | 2637004.586 | 1196222.6422
22 | 2637064.3623 | 1196263.2009
23 | 2637056.0518 | 1196279.2716
24 | 2636815.667 | 1196206.4795
25 | 2637011.4386 | 1196269.9772
26 | 2636992.7427 | 1196261.7127
27 | 2637051.5609 | 1196300.7089
28 | 2636695.8802 | 1196197.5173
29 | 2636673.3301 | 1196107.6622
30 | 2636672.0985 | 1196119.0729
31 | 2636227.7197 | 1196237.4104
32 | 2636690.0543 | 1196212.1563
33 | 2636706.3329 | 1196224.6518
34 | 2636524.4607 | 1196227.0965
35 | 2636487.264 | 1196245.4712
36 | 2636730.0415 | 1196221.7956
37 | 2636479.2259 | 1196248.488
38 | 2636531.352 | 1196409.7277
39 | 2636605.9103 | 1196657.4138
40 | 2636553.3864 | 1197032.0377
41 | 2636484.9229 | 1196258.5826
42 | 2636533.7263 | 1196252.8894
43 | 2636573.2052 | 1197077.217
44 | 2637810.2569 | 1196023.7448
45 | 2637791.804 | 1196036.3124
46 | 2637791.3869 | 1196035.7688
47 | 2637806.9314 | 1196056.1746
48 | 2637784.5354 | 1196026.8391
49 | 2637776.1086 | 1196015.8252
50 | 2637768.2608 | 1196005.5247
51 | 2637758.6648 | 1195993.0351
52 | 2637735.2276 | 1195965.9058
53 | 2637744.0297 | 1195975.402
54 | 2637728.8256 | 1195959.1172
55 | 2637811.7261 | 1196062.6638
56 | 2637749.2594 | 1195999.7492
57 | 2637718.3726 | 1195972.9748
58 | 2637719.2167 | 1195949.8405
59 | 2637834.5169 | 1196063.2143
60 | 2637854.025 | 1196068.0118
61 | 2637848.8026 | 1196080.7192
62 | 2637827.1768 | 1196091.3328
63 | 2637829.6875 | 1196097.8633
64 | 2637838.4737 | 1196087.2756
65 | 2637839.7775 | 1196086.6857
66 | 2637838.6142 | 1196136.6522
67 | 2637823.1388 | 1196147.7742
68 | 2637812.6546 | 1196103.661
69 | 2637770.8414 | 1196129.5197
70 | 2637767.575 | 1196119.0051
71 | 2637753.3804 | 1196124.039
72 | 2637755.69 | 1196084.9783
73 | 2637779.8728 | 1196114.8192
74 | 2637811.5126 | 1196104.0497
75 | 2637733.9015 | 1196052.5684
76 | 2637732.5162 | 1196051.0698
77 | 2637710.5908 | 1196124.8932
78 | 2637705.1638 | 1196108.414
79 | 2637696.8351 | 1196087.0916
80 | 2637734.8748 | 1196013.2654
81 | 2637743.4213 | 1196004.5843
82 | 2637725.5669 | 1196023.8087
83 | 2637716.6982 | 1196033.9598
84 | 2637716.255 | 1196034.4646
85 | 2637703.1501 | 1196049.3921
86 | 2637698.6513 | 1195976.4743
87 | 2637691.495 | 1195973.957
88 | 2637709.7045 | 1195984.4663
89 | 2637656.7857 | 1196012.9894
90 | 2637704.4094 | 1195991.4823
91 | 2637717.5249 | 1195974.0986
92 | 2637700.3672 | 1195996.8383
93 | 2637705.5763 | 1195936.8115
94 | 2637710.9315 | 1195941.9267
95 | 2637688.6969 | 1196066.2568
96 | 2637683.4939 | 1196019.3129
97 | 2637682.4596 | 1196020.7431
98 | 2637671.3074 | 1196036.0627
99 | 2637665.8423 | 1196043.3893
100 | 2637684.689 | 1196070.0114
101 | 2637671.4261 | 1196060.6097
102 | 2637668.5351 | 1196085.1187
103 | 2637659.9725 | 1196052.4907
104 | 2637664.9646 | 1196088.4579
105 | 2637644.9115 | 1196071.5585
106 | 2637654.1988 | 1196059.6629
107 | 2637636.2684 | 1196083.3044
108 | 2637632.5853 | 1196088.5599
109 | 2637630.6519 | 1196091.5098
110 | 2637639.4622 | 1196042.0448
111 | 2637619.0982 | 1196111.2212
112 | 2637661.1559 | 1196092.0199
113 | 2637669.2336 | 1196103.3289
114 | 2637096.2634 | 1196625.2114
115 | 2637102.9065 | 1196630.7084
116 | 2637108.6879 | 1196641.7614
117 | 2637029.4464 | 1196798.0902
118 | 2636912.1124 | 1196902.1562
119 | 2637082.0258 | 1196870.6563
120 | 2637110.093 | 1196644.4529
121 | 2637141.892 | 1197200.4456
122 | 2637287.4817 | 1196651.9881
123 | 2637659.9725 | 1196052.4907

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97573 | -0.17771 | 0.00018352 | 4.5994e-05
1 | 0.97586 | -0.17675 | 0 | 0
2 | 0.97571 | -0.17786 | 0.00072053 | 0.00018058
3 | 0.97637 | -0.17288 | 0 | 0
4 | 0.9758 | -0.17726 | 0.00011714 | 2.9359e-05
5 | 0.99815 | -0.013321 | 0 | 0
6 | 0.99222 | -0.056366 | 0 | 0
7 | 0.99875 | -0.0089529 | 0 | 0
8 | 0.97646 | -0.17218 | 0 | 0
9 | 0.97594 | -0.17604 | 0.00026578 | 6.6612e-05
10 | 0.97468 | -0.18518 | 0 | 0
11 | 0.97669 | -0.17047 | 0.0005811 | 0.00014564
12 | 0.97593 | -0.17606 | 0.00062189 | 0.00015586
13 | 0.97467 | -0.18526 | 0 | 0
14 | 0.97435 | -0.18759 | 0.00036273 | 9.0908e-05
15 | 0.97686 | -0.16925 | 0.00020106 | 5.0391e-05
16 | 0.97102 | -0.21181 | 0.00024457 | 6.1294e-05
17 | 0.971 | -0.21194 | 0 | 0
18 | 0.97106 | -0.21153 | 0 | 0
19 | 0.97096 | -0.21223 | 0 | 0
20 | 0.97105 | -0.21159 | 0 | 0
21 | 0.97123 | -0.2103 | 0 | 0
22 | 0.97096 | -0.21229 | 0.0005312 | 0.00013313
23 | 0.97096 | -0.21229 | 0.00024457 | 6.1294e-05
24 | 0.97203 | -0.20448 | 0.00015161 | 3.7997e-05
25 | 0.97105 | -0.21162 | 0.00029656 | 7.4324e-05
26 | 0.97102 | -0.21184 | 0.0012455 | 0.00031214
27 | 0.97095 | -0.21236 | 0.00031337 | 7.8539e-05
28 | 0.97257 | -0.20058 | 0 | 0
29 | 0.97255 | -0.20072 | 0.00010355 | 2.5952e-05
30 | 0.97255 | -0.20071 | 0 | 0
31 | 0.97464 | -0.18547 | 0.00012303 | 3.0835e-05
32 | 0.97254 | -0.2008 | 0 | 0
33 | 0.97249 | -0.2011 | 0.00034458 | 8.636e-05
34 | 0.97371 | -0.1922 | 0 | 0
35 | 0.97399 | -0.19022 | 0.00046276 | 0.00011598
36 | 0.97246 | -0.20135 | 0.00098676 | 0.0002473
37 | 0.97405 | -0.18977 | 0 | 0
38 | 0.97897 | -0.15379 | 8.7435e-05 | 2.1913e-05
39 | 0.98077 | -0.14054 | 0.00015464 | 3.8755e-05
40 | 0.98344 | -0.12083 | 0.00064124 | 0.00016071
41 | 0.97403 | -0.18993 | 0.00037981 | 9.5189e-05
42 | 0.97395 | -0.19045 | 0.00096102 | 0.00024086
43 | 0.98383 | -0.11803 | 0 | 0
44 | 0.98049 | -0.13656 | 0.0038743 | 0.00097098
45 | 0.98062 | -0.13566 | 0 | 0
46 | 0.98066 | -0.13538 | 0.011215 | 0.0028109
47 | 0.97933 | -0.14488 | 0.0033093 | 0.00082939
48 | 0.98149 | -0.12948 | 0 | 0
49 | 0.98251 | -0.12221 | 0.0052529 | 0.0013165
50 | 0.98357 | -0.11474 | 0 | 0
51 | 0.98485 | -0.10569 | 0 | 0
52 | 0.98185 | -0.12699 | 0 | 0
53 | 0.98288 | -0.11968 | 0.0046171 | 0.0011571
54 | 0.98111 | -0.13226 | 0 | 0
55 | 0.97895 | -0.14758 | 0 | 0
56 | 0.98582 | -0.098851 | 0.0062269 | 0.0015606
57 | 0.98005 | -0.13978 | 0.0072588 | 0.0018192
58 | 0.98086 | -0.13403 | 0 | 0
59 | 0.97785 | -0.15541 | 0.0022231 | 0.00055715
60 | 0.97697 | -0.16171 | 0 | 0
61 | 0.97637 | -0.16601 | 0 | 0
62 | 0.9754 | -0.17297 | 0 | 0
63 | 0.97515 | -0.17477 | 0 | 0
64 | 0.97583 | -0.16986 | 0.0027707 | 0.0006944
65 | 0.97589 | -0.16945 | 0.0025541 | 0.00064013
66 | 0.97488 | -0.17669 | 0 | 0
67 | 0.97473 | -0.17775 | 0.0045842 | 0.0011489
68 | 0.97462 | -0.17856 | 0.0067141 | 0.0016827
69 | 0.97399 | -0.1831 | 0.0017792 | 0.0004459
70 | 0.97402 | -0.18289 | 0 | 0
71 | 0.97395 | -0.18337 | 0.0029996 | 0.00075176
72 | 0.97389 | -0.18378 | 0.0023451 | 0.00058773
73 | 0.97415 | -0.18192 | 0.0019303 | 0.00048379
74 | 0.97459 | -0.17873 | 0.0042757 | 0.0010716
75 | 0.98989 | -0.070228 | 0.0063361 | 0.001588
76 | 0.98991 | -0.070096 | 0.0025912 | 0.00064942
77 | 0.9943 | -0.03945 | 0.0026975 | 0.00067606
78 | 0.99437 | -0.038977 | 0.00058961 | 0.00014777
79 | 0.99448 | -0.038217 | 0.0029374 | 0.00073619
80 | 0.98759 | -0.086354 | 0.0050323 | 0.0012612
81 | 0.98649 | -0.094121 | 0.0030872 | 0.00077373
82 | 0.98891 | -0.077054 | 0.0027174 | 0.00068105
83 | 0.99021 | -0.067978 | 0 | 0
84 | 0.99028 | -0.067495 | 0.0018811 | 0.00047145
85 | 0.99234 | -0.053076 | 0.0018909 | 0.00047391
86 | 0.97899 | -0.14739 | 0.014845 | 0.0037206
87 | 0.97891 | -0.14796 | 0.0049779 | 0.0012476
88 | 0.97942 | -0.14433 | 0 | 0
89 | 0.97878 | -0.14892 | 0.0017329 | 0.0004343
90 | 0.97931 | -0.1451 | 0.0057326 | 0.0014367
91 | 0.97998 | -0.14028 | 0.0044933 | 0.0011261
92 | 0.97928 | -0.14529 | 0.0026865 | 0.00067329
93 | 0.98056 | -0.13616 | 0.0077998 | 0.0019548
94 | 0.98065 | -0.13556 | 0.0050352 | 0.0012619
95 | 0.99468 | -0.036811 | 0 | 0
96 | 0.99834 | -0.011496 | 0.00224 | 0.00056141
97 | 0.99835 | -0.011457 | 0.0039303 | 0.00098502
98 | 0.99851 | -0.010286 | 0.0016934 | 0.00042442
99 | 0.99862 | -0.0095664 | 0 | 0
100 | 0.99528 | -0.032635 | 0 | 0
101 | 0.99715 | -0.019654 | 0.0049001 | 0.0012281
102 | 0.99504 | -0.034357 | 0.0043419 | 0.0010882
103 | 0.99882 | -0.0081378 | 0 | 0
104 | 0.99501 | -0.034524 | 0.0023933 | 0.00059983
105 | 0.99971 | -0.0020634 | 0.0028716 | 0.0007197
106 | 1 | 0 | -0.20739 | -0.052084
107 | 0.99946 | -0.0038488 | 0.0029324 | 0.00073493
108 | 0.99936 | -0.0045407 | 0.0014796 | 0.00037083
109 | 0.99932 | -0.0048949 | 0.0030826 | 0.00077258
110 | 0.9984 | -0.011054 | 0.0053217 | 0.0013338
111 | 0.99905 | -0.0068395 | 0.00094163 | 0.000236
112 | 0.995 | -0.034576 | 0 | 0
113 | 0.99498 | -0.034715 | 0.00098814 | 0.00024765
114 | 0.98977 | -0.074324 | 0.00022525 | 5.6454e-05
115 | 0.98977 | -0.074304 | 0 | 0
116 | 0.98977 | -0.074275 | 0 | 0
117 | 0.9882 | -0.085848 | 0 | 0
118 | 0.9867 | -0.096866 | 0 | 0
119 | 0.98792 | -0.087862 | 0.00030052 | 7.5318e-05
120 | 0.98977 | -0.074268 | 0.00035768 | 8.9644e-05
121 | 0.98702 | -0.09428 | 0.0018548 | 0.00046486
122 | 0.99146 | -0.061899 | 0.0022187 | 0.00055605
123 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00090407 | -0.00022633 | 0.00090419 | 0.00022511 | 1.1975e-07 | -1.2157e-06 | 0.0013786 | 0.0013782 | 0.0013786 | 0.97573 | -0.17771 | 0.97586 | -0.17675 | 0.51061
1 | 0.00072055 | 0.00018034 | -0.00072053 | -0.00018058 | 1.5215e-08 | -2.4638e-07 | 0.0010988 | 0.0010989 | 0.0010989 | 0.97573 | -0.17771 | 0.97571 | -0.17786 | 0.40699
2 | -0.0010213 | -0.00024991 | 0.0010219 | 0.00024584 | 5.1395e-07 | -4.0632e-06 | 0.0015552 | 0.0015537 | 0.0015552 | 0.97586 | -0.17675 | 0.97637 | -0.17288 | 0.576
3 | 0.00011715 | 2.4791e-05 | -0.00011714 | -2.9359e-05 | 7.2212e-09 | -4.5682e-06 | 0.00017711 | 0.00017864 | 0.00017864 | 0.97586 | -0.17675 | 0.9758 | -0.17726 | 0.066161
4 | -0.0019099 | -0.00046426 | 0.0019101 | 0.00046391 | 1.7492e-07 | -3.4803e-07 | 0.0029056 | 0.0029055 | 0.0029056 | 0.97637 | -0.17288 | 0.97646 | -0.17218 | 1.0762
5 | 0.00088805 | 0.00021841 | -0.00088767 | -0.00022244 | 3.8109e-07 | -4.0259e-06 | 0.0013519 | 0.0013534 | 0.0013534 | 0.97637 | -0.17288 | 0.97594 | -0.17604 | 0.50127
6 | 0.015571 | 0.0038381 | -0.015482 | -0.0038176 | 8.9616e-05 | 2.0592e-05 | 0.023191 | 0.023196 | 0.023196 | 0.99815 | -0.013321 | 0.99222 | -0.056366 | 4.2955
7 | -0.015571 | -0.0038381 | 0.01558 | 0.0038402 | 9.1179e-06 | 2.0855e-06 | 0.023191 | 0.02319 | 0.023191 | 0.99815 | -0.013321 | 0.99875 | -0.0089529 | 4.2946
8 | 0.015482 | 0.0038176 | -0.01547 | -0.0038149 | 1.1487e-05 | 2.6517e-06 | 0.023196 | 0.023196 | 0.023196 | 0.99222 | -0.056366 | 0.99146 | -0.061899 | 4.2956
9 | -0.01558 | -0.0038402 | 0.015585 | 0.0038412 | 4.4137e-06 | 1.0089e-06 | 0.02319 | 0.02319 | 0.02319 | 0.99875 | -0.0089529 | 0.99905 | -0.0068395 | 4.2945
10 | 0.0067791 | 0.0016852 | -0.0067671 | -0.0016829 | 1.2e-05 | 2.3634e-06 | 0.010326 | 0.010326 | 0.010326 | 0.97646 | -0.17218 | 0.97468 | -0.18518 | 3.8246
11 | -0.0086891 | -0.0021491 | 0.0086912 | 0.0021497 | 2.0103e-06 | 5.4293e-07 | 0.013231 | 0.013231 | 0.013231 | 0.97646 | -0.17218 | 0.97669 | -0.17047 | 4.9004
12 | 0.00062189 | 0.00015583 | -0.00062189 | -0.00015586 | 1.4685e-09 | -3.2142e-08 | 0.00094818 | 0.0009482 | 0.0009482 | 0.97594 | -0.17604 | 0.97593 | -0.17606 | 0.35118
13 | 0.00012304 | 2.8251e-05 | -0.00012303 | -2.8958e-05 | 1.2394e-09 | -7.0698e-07 | 0.00018694 | 0.00018718 | 0.00018718 | 0.97468 | -0.18518 | 0.97467 | -0.18526 | 0.069326
14 | 0.006644 | 0.0016546 | -0.0066418 | -0.0016542 | 2.1888e-06 | 4.1676e-07 | 0.010139 | 0.01014 | 0.01014 | 0.97468 | -0.18518 | 0.97435 | -0.18759 | 3.7554
15 | -0.0092723 | -0.0022953 | 0.0092738 | 0.0022957 | 1.5296e-06 | 4.3434e-07 | 0.014116 | 0.014116 | 0.014116 | 0.97669 | -0.17047 | 0.97686 | -0.16925 | 5.2283
16 | 0.00012303 | 2.8958e-05 | -0.00012303 | -3.0835e-05 | 3.3059e-09 | -1.8768e-06 | 0.00018718 | 0.00018784 | 0.00018784 | 0.97467 | -0.18526 | 0.97464 | -0.18547 | 0.069569
17 | 0.0062791 | 0.0015633 | -0.0062772 | -0.001563 | 1.8664e-06 | 3.1255e-07 | 0.0095857 | 0.0095858 | 0.0095858 | 0.97435 | -0.18759 | 0.97405 | -0.18977 | 3.5503
18 | -0.0094748 | -0.0023461 | 0.0094946 | 0.0023461 | 1.9783e-05 | -4.1475e-08 | 0.014423 | 0.01442 | 0.014423 | 0.97686 | -0.16925 | 0.97897 | -0.15379 | 2.6708
19 | 0.0010892 | 0.00027203 | -0.0010892 | -0.00027217 | 2.0182e-08 | -1.3589e-07 | 0.0016688 | 0.0016688 | 0.0016688 | 0.97102 | -0.21181 | 0.971 | -0.21194 | 0.61809
20 | -0.0013338 | -0.00033332 | 0.0013338 | 0.0003331 | 5.0678e-08 | -2.2109e-07 | 0.0020436 | 0.0020435 | 0.0020436 | 0.97102 | -0.21181 | 0.97106 | -0.21153 | 0.75688
21 | 0.0010892 | 0.00027217 | -0.0010891 | -0.00027246 | 4.3515e-08 | -2.9296e-07 | 0.0016688 | 0.001669 | 0.001669 | 0.971 | -0.21194 | 0.97096 | -0.21223 | 0.61813
22 | 0.0015421 | 0.0003861 | -0.0015421 | -0.00038614 | 1.3242e-08 | -4.1928e-08 | 0.0023629 | 0.0023629 | 0.0023629 | 0.97106 | -0.21153 | 0.97105 | -0.21159 | 0.87514
23 | -0.0028759 | -0.0007192 | 0.0028764 | 0.00071889 | 4.8669e-07 | -3.0987e-07 | 0.0044063 | 0.0044062 | 0.0044063 | 0.97106 | -0.21153 | 0.97123 | -0.2103 | 1.632
24 | 0.0005312 | 0.00013301 | -0.0005312 | -0.00013313 | 4.1546e-09 | -1.2267e-07 | 0.00081403 | 0.00081408 | 0.00081408 | 0.97096 | -0.21223 | 0.97096 | -0.21229 | 0.30151
25 | 0.00055795 | 0.00013945 | -0.00055794 | -0.00013956 | 4.2137e-09 | -1.1265e-07 | 0.00085492 | 0.00085496 | 0.00085496 | 0.97096 | -0.21223 | 0.97096 | -0.21229 | 0.31665
26 | 0.00029656 | 7.4214e-05 | -0.00029656 | -7.4324e-05 | 1.1577e-09 | -1.1071e-07 | 0.0004544 | 0.00045444 | 0.00045444 | 0.97105 | -0.21159 | 0.97105 | -0.21162 | 0.16831
27 | 0.0012455 | 0.00031192 | -0.0012455 | -0.00031214 | 4.2842e-08 | -2.1669e-07 | 0.0019085 | 0.0019086 | 0.0019086 | 0.97105 | -0.21159 | 0.97102 | -0.21184 | 0.70688
28 | -0.0028764 | -0.00071889 | 0.0028787 | 0.00071742 | 2.3006e-06 | -1.4677e-06 | 0.0044062 | 0.0044053 | 0.0044062 | 0.97123 | -0.2103 | 0.97203 | -0.20448 | 1.6319
29 | 0.00031338 | 7.8269e-05 | -0.00031337 | -7.8539e-05 | 3.1517e-09 | -2.6968e-07 | 0.00048016 | 0.00048026 | 0.00048026 | 0.97096 | -0.21229 | 0.97095 | -0.21236 | 0.17787
30 | -0.0030303 | -0.00075542 | 0.0030319 | 0.00075455 | 1.6156e-06 | -8.7196e-07 | 0.0046374 | 0.0046369 | 0.0046374 | 0.97203 | -0.20448 | 0.97257 | -0.20058 | 1.7176
31 | -0.0044669 | -0.001112 | 0.004472 | 0.0011117 | 5.1088e-06 | -2.1477e-07 | 0.0068316 | 0.0068309 | 0.0068316 | 0.97257 | -0.20058 | 0.97371 | -0.1922 | 2.5302
32 | 0.00010355 | 2.4457e-05 | -0.00010355 | -2.5809e-05 | 1.7018e-09 | -1.3526e-06 | 0.00015791 | 0.00015838 | 0.00015838 | 0.97257 | -0.20058 | 0.97255 | -0.20071 | 0.05866
33 | 0.0013315 | 0.00033296 | -0.0013314 | -0.00033314 | 4.1081e-08 | -1.811e-07 | 0.0020369 | 0.0020369 | 0.0020369 | 0.97257 | -0.20058 | 0.97254 | -0.2008 | 0.75442
34 | -0.00010355 | -2.5952e-05 | 0.00010355 | 2.5809e-05 | 1.807e-10 | -1.4314e-07 | 0.00015843 | 0.00015838 | 0.00015843 | 0.97255 | -0.20072 | 0.97255 | -0.20071 | 0.058679
35 | 0.0013314 | 0.00033314 | -0.0013314 | -0.00033338 | 5.5062e-08 | -2.427e-07 | 0.0020369 | 0.002037 | 0.002037 | 0.97254 | -0.2008 | 0.97249 | -0.2011 | 0.75445
36 | 0.00098679 | 0.00024702 | -0.00098676 | -0.0002473 | 3.4098e-08 | -2.843e-07 | 0.0015098 | 0.0015099 | 0.0015099 | 0.97249 | -0.2011 | 0.97246 | -0.20135 | 0.55922
37 | -0.004472 | -0.0011117 | 0.0044733 | 0.0011117 | 1.2089e-06 | -5.1646e-08 | 0.0068309 | 0.0068307 | 0.0068309 | 0.97371 | -0.1922 | 0.97399 | -0.19022 | 2.5299
38 | -0.004936 | -0.0012277 | 0.0049363 | 0.0012277 | 3.0439e-07 | 1.0212e-08 | 0.0075377 | 0.0075376 | 0.0075377 | 0.97399 | -0.19022 | 0.97405 | -0.18977 | 2.7917
39 | 0.0013409 | 0.00033529 | -0.0013409 | -0.00033543 | 3.037e-08 | -1.3272e-07 | 0.0020482 | 0.0020483 | 0.0020483 | 0.97405 | -0.18977 | 0.97403 | -0.18993 | 0.75862
40 | -0.0095821 | -0.002368 | 0.0095991 | 0.0023681 | 1.7089e-05 | 5.6122e-08 | 0.014553 | 0.01455 | 0.014553 | 0.97897 | -0.15379 | 0.98077 | -0.14054 | 2.6949
41 | -0.0097538 | -0.0024068 | 0.0097796 | 0.0024072 | 2.5794e-05 | 3.471e-07 | 0.014785 | 0.014782 | 0.014785 | 0.98077 | -0.14054 | 0.98344 | -0.12083 | 2.738
42 | -0.010421 | -0.0025679 | 0.010425 | 0.0025681 | 3.904e-06 | 2.2124e-07 | 0.015752 | 0.015751 | 0.015752 | 0.98344 | -0.12083 | 0.98383 | -0.11803 | 2.917
43 | 0.00096109 | 0.00024024 | -0.00096102 | -0.00024086 | 6.9623e-08 | -6.1746e-07 | 0.001468 | 0.0014683 | 0.0014683 | 0.97403 | -0.18993 | 0.97395 | -0.19045 | 0.5438
44 | -0.010425 | -0.0025681 | 0.010454 | 0.0025697 | 2.9521e-05 | 1.6385e-06 | 0.015751 | 0.015748 | 0.015751 | 0.98383 | -0.11803 | 0.9867 | -0.096866 | 2.9169
45 | -0.0038743 | -0.00097098 | 0.0038748 | 0.00097089 | 4.8161e-07 | -9.6389e-08 | 0.0058797 | 0.0058796 | 0.0058797 | 0.98049 | -0.13656 | 0.98062 | -0.13566 | 2.1777
46 | -0.039548 | -0.0099327 | 0.03955 | 0.0099333 | 1.5402e-06 | 5.8375e-07 | 0.060019 | 0.060019 | 0.060019 | 0.98062 | -0.13566 | 0.98066 | -0.13538 | 22.2291
47 | 0.035673 | 0.0089619 | -0.035628 | -0.0089446 | 4.5664e-05 | 1.7248e-05 | 0.054139 | 0.054139 | 0.054139 | 0.98062 | -0.13566 | 0.97933 | -0.14488 | 20.0516
48 | -0.050765 | -0.012744 | 0.050807 | 0.01276 | 4.1681e-05 | 1.5889e-05 | 0.077037 | 0.077037 | 0.077037 | 0.98066 | -0.13538 | 0.98149 | -0.12948 | 28.5321
49 | 0.032318 | 0.0081152 | -0.032306 | -0.0081107 | 1.2144e-05 | 4.5694e-06 | 0.049111 | 0.049111 | 0.049111 | 0.97933 | -0.14488 | 0.97895 | -0.14758 | 18.1893
50 | -0.050807 | -0.01276 | 0.050858 | 0.01278 | 5.1356e-05 | 1.9577e-05 | 0.077037 | 0.077037 | 0.077037 | 0.98149 | -0.12948 | 0.98251 | -0.12221 | 28.5321
51 | -0.056111 | -0.014096 | 0.056169 | 0.014118 | 5.837e-05 | 2.2286e-05 | 0.084992 | 0.084992 | 0.084992 | 0.98251 | -0.12221 | 0.98357 | -0.11474 | 31.4785
52 | -0.056169 | -0.014118 | 0.05624 | 0.014146 | 7.0926e-05 | 2.7079e-05 | 0.084992 | 0.084992 | 0.084992 | 0.98357 | -0.11474 | 0.98485 | -0.10569 | 31.4785
53 | 0.05947 | 0.014941 | -0.059355 | -0.014897 | 0.00011553 | 4.4143e-05 | 0.089867 | 0.089867 | 0.089867 | 0.98485 | -0.10569 | 0.98288 | -0.11968 | 33.2842
54 | -0.11571 | -0.029087 | 0.11582 | 0.029129 | 0.00011024 | 4.2105e-05 | 0.17486 | 0.17486 | 0.17486 | 0.98485 | -0.10569 | 0.98582 | -0.098851 | 32.3813
55 | -0.054682 | -0.013719 | 0.054738 | 0.01374 | 5.5497e-05 | 2.1181e-05 | 0.082877 | 0.082877 | 0.082877 | 0.98185 | -0.12699 | 0.98288 | -0.11968 | 30.6954
56 | 0.054682 | 0.013719 | -0.054642 | -0.013703 | 3.9942e-05 | 1.5244e-05 | 0.082877 | 0.082877 | 0.082877 | 0.98185 | -0.12699 | 0.98111 | -0.13226 | 30.6954
57 | 0.041801 | 0.010485 | -0.041757 | -0.010468 | 4.3538e-05 | 1.6527e-05 | 0.063401 | 0.063401 | 0.063401 | 0.98111 | -0.13226 | 0.98005 | -0.13978 | 23.4819
58 | 0.012842 | 0.0032189 | -0.012838 | -0.0032178 | 3.157e-06 | 1.0458e-06 | 0.019477 | 0.019477 | 0.019477 | 0.98111 | -0.13226 | 0.98086 | -0.13403 | 7.2136
59 | 0.032306 | 0.0081107 | -0.032271 | -0.0080974 | 3.511e-05 | 1.3211e-05 | 0.049111 | 0.049111 | 0.049111 | 0.97895 | -0.14758 | 0.97785 | -0.15541 | 18.1893
60 | -0.12205 | -0.030689 | 0.12213 | 0.03072 | 8.0506e-05 | 3.077e-05 | 0.18426 | 0.18426 | 0.18426 | 0.98582 | -0.098851 | 0.98649 | -0.094121 | 34.1218
61 | 0.034498 | 0.0086488 | -0.034496 | -0.0086479 | 2.41e-06 | 9.0917e-07 | 0.05238 | 0.05238 | 0.05238 | 0.98005 | -0.13978 | 0.97998 | -0.14028 | 19.4
62 | 0.012838 | 0.0032178 | -0.012836 | -0.0032169 | 2.7121e-06 | 8.9852e-07 | 0.019477 | 0.019477 | 0.019477 | 0.98086 | -0.13403 | 0.98065 | -0.13556 | 7.2136
63 | 0.030048 | 0.0075403 | -0.030022 | -0.0075305 | 2.6213e-05 | 9.8302e-06 | 0.045728 | 0.045728 | 0.045728 | 0.97785 | -0.15541 | 0.97697 | -0.16171 | 16.9364
64 | 0.030022 | 0.0075305 | -0.030004 | -0.0075237 | 1.7923e-05 | 6.7216e-06 | 0.045728 | 0.045728 | 0.045728 | 0.97697 | -0.16171 | 0.97637 | -0.16601 | 16.9364
65 | 0.030004 | 0.0075237 | -0.02999 | -0.0075184 | 1.4291e-05 | 5.3597e-06 | 0.045728 | 0.045728 | 0.045728 | 0.97637 | -0.16601 | 0.97589 | -0.16945 | 16.9365
66 | 0.024653 | 0.0061793 | -0.024646 | -0.006177 | 6.1739e-06 | 2.2873e-06 | 0.037609 | 0.037609 | 0.037609 | 0.9754 | -0.17297 | 0.97515 | -0.17477 | 13.9293
67 | -0.024653 | -0.0061793 | 0.024663 | 0.0061833 | 1.0594e-05 | 3.9248e-06 | 0.037609 | 0.037609 | 0.037609 | 0.9754 | -0.17297 | 0.97583 | -0.16986 | 13.9293
68 | 0.02006 | 0.0050282 | -0.02005 | -0.0050244 | 1.0521e-05 | 3.822e-06 | 0.030611 | 0.030611 | 0.030611 | 0.97515 | -0.17477 | 0.97462 | -0.17856 | 11.3375
69 | 0.0045861 | 0.0011489 | -0.0045849 | -0.0011489 | 1.218e-06 | -2.863e-08 | 0.006998 | 0.0069982 | 0.0069982 | 0.97515 | -0.17477 | 0.97488 | -0.17669 | 2.5919
70 | -0.027434 | -0.0068777 | 0.027435 | 0.0068782 | 1.5634e-06 | 5.8343e-07 | 0.041834 | 0.041834 | 0.041834 | 0.97583 | -0.16986 | 0.97589 | -0.16945 | 15.494
71 | 0.0045849 | 0.0011489 | -0.0045842 | -0.0011489 | 6.6964e-07 | -1.5613e-08 | 0.0069982 | 0.0069983 | 0.0069983 | 0.97488 | -0.17669 | 0.97473 | -0.17775 | 2.5919
72 | 0.013336 | 0.0033416 | -0.013335 | -0.0033415 | 3.1205e-07 | 1.0498e-07 | 0.02036 | 0.02036 | 0.02036 | 0.97462 | -0.17856 | 0.97459 | -0.17873 | 7.5408
73 | -0.0017792 | -0.0004459 | 0.0017792 | 0.00044578 | 5.0759e-08 | -1.1751e-07 | 0.0027181 | 0.0027181 | 0.0027181 | 0.97399 | -0.1831 | 0.97402 | -0.18289 | 1.0067
74 | 0.0029998 | 0.00075165 | -0.0029996 | -0.00075176 | 1.9737e-07 | -1.1153e-07 | 0.0045827 | 0.0045828 | 0.0045828 | 0.97402 | -0.18289 | 0.97395 | -0.18337 | 1.6973
75 | 0.0023453 | 0.00058739 | -0.0023451 | -0.00058773 | 2.8872e-07 | -3.375e-07 | 0.0035829 | 0.003583 | 0.003583 | 0.97402 | -0.18289 | 0.97389 | -0.18378 | 1.327
76 | -0.0071243 | -0.0017848 | 0.0071253 | 0.001785 | 9.602e-07 | 2.076e-07 | 0.010884 | 0.010884 | 0.010884 | 0.97402 | -0.18289 | 0.97415 | -0.18192 | 4.031
77 | -0.0090556 | -0.0022688 | 0.0090596 | 0.0022699 | 3.9902e-06 | 1.1184e-06 | 0.013832 | 0.013832 | 0.013832 | 0.97415 | -0.18192 | 0.97459 | -0.17873 | 5.123
78 | -0.0063361 | -0.001588 | 0.0063362 | 0.001588 | 1.1552e-07 | 1.8195e-08 | 0.0095244 | 0.0095244 | 0.0095244 | 0.98989 | -0.070228 | 0.98991 | -0.070096 | 3.5276
79 | -0.0089274 | -0.0022374 | 0.00893 | 0.0022381 | 2.6184e-06 | 7.0743e-07 | 0.01342 | 0.013419 | 0.01342 | 0.98991 | -0.070096 | 0.99021 | -0.067978 | 4.9702
80 | -0.0026975 | -0.00067606 | 0.0026977 | 0.0006759 | 1.766e-07 | -1.5734e-07 | 0.0040369 | 0.0040369 | 0.0040369 | 0.9943 | -0.03945 | 0.99437 | -0.038977 | 1.4952
81 | -0.0032873 | -0.00082368 | 0.0032877 | 0.00082351 | 3.4565e-07 | -1.6404e-07 | 0.0049192 | 0.0049191 | 0.0049192 | 0.99437 | -0.038977 | 0.99448 | -0.038217 | 1.8219
82 | -0.0062251 | -0.0015597 | 0.0062263 | 0.0015599 | 1.2109e-06 | 1.7545e-07 | 0.0093143 | 0.0093142 | 0.0093143 | 0.99448 | -0.038217 | 0.99468 | -0.036811 | 3.4497
83 | 0.12535 | 0.031546 | -0.12522 | -0.031494 | 0.00013575 | 5.1899e-05 | 0.18891 | 0.18891 | 0.18891 | 0.98759 | -0.086354 | 0.98649 | -0.094121 | 34.9842
84 | -0.13038 | -0.032807 | 0.13055 | 0.032872 | 0.00016943 | 6.4804e-05 | 0.1965 | 0.1965 | 0.1965 | 0.98759 | -0.086354 | 0.98891 | -0.077054 | 36.3883
85 | -0.13327 | -0.033553 | 0.13344 | 0.033618 | 0.00016921 | 6.4735e-05 | 0.20059 | 0.20059 | 0.20059 | 0.98891 | -0.077054 | 0.99021 | -0.067978 | 37.1455
86 | -0.14237 | -0.035856 | 0.14238 | 0.035859 | 9.5994e-06 | 3.6748e-06 | 0.214 | 0.214 | 0.214 | 0.99021 | -0.067978 | 0.99028 | -0.067495 | 39.6305
87 | -0.14426 | -0.036331 | 0.14455 | 0.036442 | 0.00029138 | 0.00011156 | 0.21683 | 0.21683 | 0.21683 | 0.99028 | -0.067495 | 0.99234 | -0.053076 | 40.154
88 | -0.14644 | -0.036916 | 0.14678 | 0.037044 | 0.00033439 | 0.00012804 | 0.21967 | 0.21967 | 0.21967 | 0.99234 | -0.053076 | 0.99468 | -0.036811 | 40.679
89 | 0.0067115 | 0.0016814 | -0.006711 | -0.0016813 | 5.3139e-07 | 1.0149e-07 | 0.010201 | 0.010201 | 0.010201 | 0.97899 | -0.14739 | 0.97891 | -0.14796 | 3.7782
90 | -0.021557 | -0.005402 | 0.021566 | 0.0054053 | 9.1372e-06 | 3.3427e-06 | 0.032765 | 0.032765 | 0.032765 | 0.97899 | -0.14739 | 0.97942 | -0.14433 | 12.1352
91 | 0.0017331 | 0.00043372 | -0.0017329 | -0.0004343 | 2.2852e-07 | -5.7544e-07 | 0.0026342 | 0.0026345 | 0.0026345 | 0.97891 | -0.14796 | 0.97878 | -0.14892 | 0.97573
92 | 0.00842 | 0.0021102 | -0.0084191 | -0.0021099 | 8.9757e-07 | 2.3461e-07 | 0.012792 | 0.012792 | 0.012792 | 0.97942 | -0.14433 | 0.97931 | -0.1451 | 4.7379
93 | -0.029986 | -0.0075155 | 0.030003 | 0.0075218 | 1.6819e-05 | 6.3052e-06 | 0.045557 | 0.045557 | 0.045557 | 0.97942 | -0.14433 | 0.97998 | -0.14028 | 16.8731
94 | 0.0026865 | 0.00067323 | -0.0026865 | -0.00067329 | 6.9771e-08 | -5.759e-08 | 0.004082 | 0.0040821 | 0.0040821 | 0.97931 | -0.1451 | 0.97928 | -0.14529 | 1.5119
95 | -0.0077998 | -0.0019548 | 0.0078005 | 0.001955 | 6.4741e-07 | 1.5558e-07 | 0.011836 | 0.011836 | 0.011836 | 0.98056 | -0.13616 | 0.98065 | -0.13556 | 4.3838
96 | -0.153 | -0.038604 | 0.15309 | 0.038639 | 8.9712e-05 | 3.4362e-05 | 0.22898 | 0.22898 | 0.22898 | 0.99468 | -0.036811 | 0.99528 | -0.032635 | 42.4038
97 | -0.00224 | -0.00056141 | 0.0022401 | 0.00056139 | 1.2277e-08 | -1.8357e-08 | 0.0033388 | 0.0033388 | 0.0033388 | 0.99834 | -0.011496 | 0.99835 | -0.011457 | 1.2366
98 | -0.0061703 | -0.0015464 | 0.0061713 | 0.0015465 | 1.0001e-06 | 1.3683e-07 | 0.0091967 | 0.0091966 | 0.0091967 | 0.99835 | -0.011457 | 0.99851 | -0.010286 | 3.4062
99 | -0.0078648 | -0.001971 | 0.0078656 | 0.0019711 | 7.8346e-07 | 1.8176e-07 | 0.01172 | 0.01172 | 0.01172 | 0.99851 | -0.010286 | 0.99862 | -0.0095664 | 4.3408
100 | 0.0053228 | 0.0013338 | -0.0053217 | -0.0013338 | 1.0961e-06 | 5.6336e-08 | 0.0079313 | 0.0079315 | 0.0079315 | 0.99862 | -0.0095664 | 0.9984 | -0.011054 | 2.9376
101 | -0.013188 | -0.0033049 | 0.013191 | 0.0033058 | 2.6081e-06 | 8.6149e-07 | 0.019652 | 0.019652 | 0.019652 | 0.99862 | -0.0095664 | 0.99882 | -0.0081378 | 7.2784
102 | -0.16082 | -0.040574 | 0.16111 | 0.040687 | 0.00029345 | 0.00011244 | 0.24053 | 0.24053 | 0.24053 | 0.99528 | -0.032635 | 0.99715 | -0.019654 | 44.5427
103 | 0.0077253 | 0.0019358 | -0.0077235 | -0.0019354 | 1.8411e-06 | 4.2074e-07 | 0.01155 | 0.01155 | 0.01155 | 0.99528 | -0.032635 | 0.99504 | -0.034357 | 4.2777
104 | -0.16601 | -0.041915 | 0.16628 | 0.042018 | 0.00026906 | 0.00010312 | 0.24784 | 0.24784 | 0.24784 | 0.99715 | -0.019654 | 0.99882 | -0.0081378 | 45.8968
105 | 0.0033816 | 0.00084721 | -0.0033815 | -0.00084724 | 7.8007e-08 | -3.3496e-08 | 0.0050569 | 0.0050569 | 0.0050569 | 0.99504 | -0.034357 | 0.99501 | -0.034524 | 1.8729
106 | -0.17947 | -0.045324 | 0.17968 | 0.045403 | 0.00020555 | 7.8817e-05 | 0.26749 | 0.26749 | 0.26749 | 0.99882 | -0.0081378 | 1 | 0 | 49.5359
107 | 0.00098817 | 0.00024741 | -0.00098816 | -0.00024748 | 7.1055e-09 | -6.5e-08 | 0.0014777 | 0.0014777 | 0.0014777 | 0.99501 | -0.034524 | 0.995 | -0.034576 | 0.5473
108 | -0.026906 | -0.0066791 | 0.026913 | 0.0066816 | 7.5444e-06 | 2.5058e-06 | 0.040025 | 0.040025 | 0.040025 | 0.99971 | -0.0020634 | 1 | 0 | 7.4121
109 | 0.024034 | 0.0059593 | -0.024028 | -0.0059575 | 5.8161e-06 | 1.8546e-06 | 0.035751 | 0.035751 | 0.035751 | 0.99971 | -0.0020634 | 0.99946 | -0.0038488 | 6.6206
110 | 0.021096 | 0.0052226 | -0.021094 | -0.005222 | 1.9727e-06 | 5.9052e-07 | 0.031385 | 0.031386 | 0.031386 | 0.99946 | -0.0038488 | 0.99936 | -0.0045407 | 5.8121
111 | 0.019614 | 0.0048511 | -0.019613 | -0.0048509 | 9.3714e-07 | 2.6802e-07 | 0.029182 | 0.029182 | 0.029182 | 0.99936 | -0.0045407 | 0.99932 | -0.0048949 | 5.4042
112 | 0.016531 | 0.0040783 | -0.016526 | -0.0040772 | 4.3154e-06 | 1.0607e-06 | 0.024592 | 0.024593 | 0.024593 | 0.99932 | -0.0048949 | 0.99905 | -0.0068395 | 4.5542
113 | 0.00098816 | 0.00024748 | -0.00098814 | -0.00024765 | 1.8938e-08 | -1.7322e-07 | 0.0014777 | 0.0014778 | 0.0014778 | 0.995 | -0.034576 | 0.99498 | -0.034715 | 0.54733
114 | -0.00022525 | -5.6454e-05 | 0.00022525 | 5.6343e-05 | 6.1841e-10 | -1.1084e-07 | 0.00033864 | 0.00033861 | 0.00033864 | 0.98977 | -0.074324 | 0.98977 | -0.074304 | 0.12542
115 | -0.00022525 | -5.6343e-05 | 0.00022525 | 5.6183e-05 | 8.9186e-10 | -1.599e-07 | 0.00033861 | 0.00033855 | 0.00033861 | 0.98977 | -0.074304 | 0.98977 | -0.074275 | 0.12541
116 | -0.00022525 | -5.6183e-05 | 0.00022525 | 5.6144e-05 | 2.1713e-10 | -3.8938e-08 | 0.00033855 | 0.00033853 | 0.00033855 | 0.98977 | -0.074275 | 0.98977 | -0.074268 | 0.12539
117 | 0.01047 | 0.0025706 | -0.010454 | -0.0025697 | 1.5354e-05 | 8.2806e-07 | 0.015746 | 0.015748 | 0.015748 | 0.9882 | -0.085848 | 0.9867 | -0.096866 | 2.9163
118 | 0.0021576 | 0.0005356 | -0.002157 | -0.00053652 | 5.9152e-07 | -9.2391e-07 | 0.003247 | 0.0032474 | 0.0032474 | 0.9882 | -0.085848 | 0.98792 | -0.087862 | 1.2028
119 | -0.012627 | -0.0031062 | 0.012647 | 0.0031092 | 1.9528e-05 | 3.0577e-06 | 0.018993 | 0.018992 | 0.018993 | 0.9882 | -0.085848 | 0.98977 | -0.074268 | 3.5173
120 | 0.0018565 | 0.0004612 | -0.0018548 | -0.00046486 | 1.6345e-06 | -3.6591e-06 | 0.0027948 | 0.0027963 | 0.0027963 | 0.98792 | -0.087862 | 0.98702 | -0.09428 | 1.0357
121 | -0.01323 | -0.003255 | 0.013252 | 0.0032588 | 2.1865e-05 | 3.8379e-06 | 0.019868 | 0.019866 | 0.019868 | 0.98977 | -0.074268 | 0.99146 | -0.061899 | 3.6793

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20974 | 0.052673

## res_load
| p_mw | q_mvar
0 | 0.00018352 | 4.5994e-05
1 | 0.00072053 | 0.00018058
2 | 0.00011714 | 2.9359e-05
3 | 0.00026578 | 6.6612e-05
4 | 0.0005811 | 0.00014564
5 | 0.00062189 | 0.00015586
6 | 0.00036273 | 9.0908e-05
7 | 0.00020106 | 5.0391e-05
8 | 0.00024457 | 6.1294e-05
9 | 0.0005312 | 0.00013313
10 | 0.00024457 | 6.1294e-05
11 | 0.00015161 | 3.7997e-05
12 | 0.00029656 | 7.4324e-05
13 | 0.0012455 | 0.00031214
14 | 0.00031337 | 7.8539e-05
15 | 0.00010355 | 2.5952e-05
16 | 0.00012303 | 3.0835e-05
17 | 0.00034458 | 8.636e-05
18 | 0.00046276 | 0.00011598
19 | 0.00098676 | 0.0002473
20 | 8.7435e-05 | 2.1913e-05
21 | 0.00015464 | 3.8755e-05
22 | 0.00064124 | 0.00016071
23 | 0.00037981 | 9.5189e-05
24 | 0.00096102 | 0.00024086
25 | 0.0038743 | 0.00097098
26 | 0.011215 | 0.0028109
27 | 0.0033093 | 0.00082939
28 | 0.0052529 | 0.0013165
29 | 0.0046171 | 0.0011571
30 | 0.0062269 | 0.0015606
31 | 0.0072588 | 0.0018192
32 | 0.0022231 | 0.00055715
33 | 0.0027707 | 0.0006944
34 | 0.0025541 | 0.00064013
35 | 0.0045842 | 0.0011489
36 | 0.0067141 | 0.0016827
37 | 0.0017792 | 0.0004459
38 | 0.0029996 | 0.00075176
39 | 0.0023451 | 0.00058773
40 | 0.0019303 | 0.00048379
41 | 0.0042757 | 0.0010716
42 | 0.0063361 | 0.001588
43 | 0.0025912 | 0.00064942
44 | 0.0026975 | 0.00067606
45 | 0.00058961 | 0.00014777
46 | 0.0029374 | 0.00073619
47 | 0.0050323 | 0.0012612
48 | 0.0030872 | 0.00077373
49 | 0.0027174 | 0.00068105
50 | 0.0018811 | 0.00047145
51 | 0.0018909 | 0.00047391
52 | 0.014845 | 0.0037206
53 | 0.0049779 | 0.0012476
54 | 0.0017329 | 0.0004343
55 | 0.0057326 | 0.0014367
56 | 0.0044933 | 0.0011261
57 | 0.0026865 | 0.00067329
58 | 0.0077998 | 0.0019548
59 | 0.0050352 | 0.0012619
60 | 0.00224 | 0.00056141
61 | 0.0039303 | 0.00098502
62 | 0.0016934 | 0.00042442
63 | 0.0049001 | 0.0012281
64 | 0.0043419 | 0.0010882
65 | 0.0023933 | 0.00059983
66 | 0.0028716 | 0.0007197
67 | 0.0023472 | 0.00058826
68 | 0.0029324 | 0.00073493
69 | 0.0014796 | 0.00037083
70 | 0.0030826 | 0.00077258
71 | 0.0053217 | 0.0013338
72 | 0.00094163 | 0.000236
73 | 0.00098814 | 0.00024765
74 | 0.00022525 | 5.6454e-05
75 | 0.00030052 | 7.5318e-05
76 | 0.00035768 | 8.9644e-05
77 | 0.0018548 | 0.00046486
78 | 0.0022187 | 0.00055605

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1