## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1010-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1010-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1010-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1010-8_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1010-8_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1010-8_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1010-8_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1010-8_0_4_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_1010-8_0_4_node_51 | 0.4 | n |  | TRUE
9 | bus_LV_1010-8_0_4_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_1010-8_0_4_node_47 | 0.4 | n |  | TRUE
11 | bus_LV_1010-8_0_4_node_20 | 0.4 | n |  | TRUE
12 | bus_LV_1010-8_0_4_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_1010-8_0_4_node_53 | 0.4 | n |  | TRUE
14 | bus_LV_1010-8_0_4_node_26 | 0.4 | n |  | TRUE
15 | bus_LV_1010-8_0_4_node_48 | 0.4 | n |  | TRUE
16 | bus_LV_1010-8_0_4_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1010-8_0_4_node_8 | 0.4 | n |  | TRUE
18 | bus_LV_1010-8_0_4_node_9 | 0.4 | n |  | TRUE
19 | bus_LV_1010-8_0_4_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1010-8_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1010-8_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1010-8_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1010-8_0_4_node_81 | 0.4 | n |  | TRUE
24 | bus_LV_1010-8_0_4_node_80 | 0.4 | n |  | TRUE
25 | bus_LV_1010-8_0_4_node_79 | 0.4 | n |  | TRUE
26 | bus_LV_1010-8_0_4_node_78 | 0.4 | n |  | TRUE
27 | bus_LV_1010-8_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1010-8_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1010-8_0_4_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_1010-8_0_4_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1010-8_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1010-8_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1010-8_0_4_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_1010-8_0_4_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_1010-8_0_4_node_41 | 0.4 | n |  | TRUE
36 | bus_LV_1010-8_0_4_node_38 | 0.4 | n |  | TRUE
37 | bus_LV_1010-8_0_4_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_1010-8_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1010-8_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_1010-8_0_4_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_1010-8_0_4_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_1010-8_0_4_node_55 | 0.4 | n |  | TRUE
43 | bus_LV_1010-8_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_1010-8_0_4_node_56 | 0.4 | n |  | TRUE
45 | bus_LV_1010-8_0_4_node_46 | 0.4 | n |  | TRUE
46 | bus_LV_1010-8_0_4_node_66 | 0.4 | n |  | TRUE
47 | bus_LV_1010-8_0_4_node_31 | 0.4 | n |  | TRUE
48 | bus_LV_1010-8_0_4_node_32 | 0.4 | n |  | TRUE
49 | bus_LV_1010-8_0_4_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_1010-8_0_4_node_33 | 0.4 | n |  | TRUE
51 | bus_LV_1010-8_0_4_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_1010-8_0_4_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_1010-8_0_4_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_1010-8_0_4_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_1010-8_0_4_node_45 | 0.4 | n |  | TRUE
56 | bus_LV_1010-8_0_4_node_57 | 0.4 | n |  | TRUE
57 | bus_LV_1010-8_0_4_node_44 | 0.4 | n |  | TRUE
58 | bus_LV_1010-8_0_4_node_58 | 0.4 | n |  | TRUE
59 | bus_LV_1010-8_0_4_node_59 | 0.4 | n |  | TRUE
60 | bus_LV_1010-8_0_4_node_67 | 0.4 | n |  | TRUE
61 | bus_LV_1010-8_0_4_node_49 | 0.4 | n |  | TRUE
62 | bus_LV_1010-8_0_4_node_50 | 0.4 | n |  | TRUE
63 | bus_LV_1010-8_0_4_node_62 | 0.4 | n |  | TRUE
64 | bus_LV_1010-8_0_4_node_65 | 0.4 | n |  | TRUE
65 | bus_LV_1010-8_0_4_node_60 | 0.4 | n |  | TRUE
66 | bus_LV_1010-8_0_4_node_74 | 0.4 | n |  | TRUE
67 | bus_LV_1010-8_0_4_node_75 | 0.4 | n |  | TRUE
68 | bus_LV_1010-8_0_4_node_61 | 0.4 | n |  | TRUE
69 | bus_LV_1010-8_0_4_node_63 | 0.4 | n |  | TRUE
70 | bus_LV_1010-8_0_4_node_64 | 0.4 | n |  | TRUE
71 | bus_LV_1010-8_0_4_node_70 | 0.4 | n |  | TRUE
72 | bus_LV_1010-8_0_4_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_1010-8_0_4_node_71 | 0.4 | n |  | TRUE
74 | bus_LV_1010-8_0_4_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_1010-8_0_4_node_72 | 0.4 | n |  | TRUE
76 | bus_LV_1010-8_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_1010-8_0_4_node_76 | 0.4 | n |  | TRUE
78 | bus_LV_1010-8_0_4_node_77 | 0.4 | n |  | TRUE
79 | bus_MV_126_0_node_43 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1010-8_0_4_load_0 | 0 | 0.00089182 | 0.00022351 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1010-8_0_4_load_1 | 1 | 0.0021084 | 0.00052842 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1010-8_0_4_load_3 | 3 | 0.0021346 | 0.00053497 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1010-8_0_4_load_4 | 4 | 0.0060763 | 0.0015229 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1010-8_0_4_load_5 | 5 | 0.0028921 | 0.00072482 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1010-8_0_4_load_21 | 7 | 0.0012232 | 0.00030657 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1010-8_0_4_load_51 | 8 | 0.0017817 | 0.00044654 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1010-8_0_4_load_28 | 9 | 0.0026159 | 0.0006556 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1010-8_0_4_load_47 | 10 | 0.0025957 | 0.00065055 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1010-8_0_4_load_52 | 12 | 0.0013115 | 0.0003287 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1010-8_0_4_load_53 | 13 | 0.015649 | 0.0039219 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1010-8_0_4_load_26 | 14 | 0.0038523 | 0.00096547 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1010-8_0_4_load_48 | 15 | 0.0020814 | 0.00052164 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1010-8_0_4_load_7 | 16 | 0.0010356 | 0.00025955 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1010-8_0_4_load_8 | 17 | 0.0012298 | 0.00030822 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1010-8_0_4_load_9 | 18 | 0.0013169 | 0.00033004 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1010-8_0_4_load_10 | 19 | 0.0013702 | 0.0003434 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1010-8_0_4_load_11 | 20 | 0.0014049 | 0.00035211 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1010-8_0_4_load_12 | 21 | 0.0013156 | 0.00032973 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1010-8_0_4_load_19 | 22 | 0.0021409 | 0.00053657 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1010-8_0_4_load_81 | 23 | 0.0034442 | 0.00086321 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1010-8_0_4_load_80 | 24 | 0.0020826 | 0.00052195 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1010-8_0_4_load_79 | 25 | 0.00061539 | 0.00015423 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1010-8_0_4_load_78 | 26 | 0.0034326 | 0.0008603 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1010-8_0_4_load_18 | 27 | 0.00097288 | 0.00024383 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1010-8_0_4_load_14 | 28 | 0.0026044 | 0.00065274 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1010-8_0_4_load_15 | 29 | 0.0017221 | 0.0004316 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1010-8_0_4_load_17 | 30 | 0.0020206 | 0.0005064 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1010-8_0_4_load_23 | 31 | 0.0020421 | 0.0005118 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1010-8_0_4_load_24 | 32 | 0.0015653 | 0.00039231 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1010-8_0_4_load_22 | 33 | 0.0022906 | 0.00057408 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1010-8_0_4_load_42 | 34 | 0.0024477 | 0.00061345 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1010-8_0_4_load_41 | 35 | 0.0020405 | 0.00051141 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1010-8_0_4_load_38 | 36 | 0.005863 | 0.0014694 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1010-8_0_4_load_37 | 37 | 0.007175 | 0.0017982 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1010-8_0_4_load_25 | 38 | 0.002562 | 0.0006421 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1010-8_0_4_load_29 | 40 | 0.0019962 | 0.00050029 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1010-8_0_4_load_39 | 43 | 0.0028018 | 0.00070219 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1010-8_0_4_load_56 | 44 | 0.0036854 | 0.00092365 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1010-8_0_4_load_46 | 45 | 0.0034906 | 0.00087482 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1010-8_0_4_load_31 | 47 | 0.0042282 | 0.0010597 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1010-8_0_4_load_32 | 48 | 0.0016655 | 0.00041742 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1010-8_0_4_load_35 | 51 | 0.0013382 | 0.0003354 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1010-8_0_4_load_36 | 52 | 0.0018771 | 0.00047046 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1010-8_0_4_load_43 | 53 | 0.0029476 | 0.00073874 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1010-8_0_4_load_40 | 54 | 0.0086335 | 0.0021637 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1010-8_0_4_load_44 | 57 | 0.0023566 | 0.00059061 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1010-8_0_4_load_58 | 58 | 0.0022184 | 0.00055598 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1010-8_0_4_load_59 | 59 | 0.0040647 | 0.0010187 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1010-8_0_4_load_67 | 60 | 0.0035096 | 0.00087959 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1010-8_0_4_load_49 | 61 | 0.0021858 | 0.00054782 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1010-8_0_4_load_50 | 62 | 0.0021656 | 0.00054275 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1010-8_0_4_load_65 | 64 | 0.0013461 | 0.00033736 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1010-8_0_4_load_60 | 65 | 0.0013407 | 0.00033602 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1010-8_0_4_load_74 | 66 | 0.00047287 | 0.00011851 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1010-8_0_4_load_75 | 67 | 0.0019146 | 0.00047985 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1010-8_0_4_load_63 | 69 | 0.0043993 | 0.0011026 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1010-8_0_4_load_64 | 70 | 0.0040305 | 0.0010101 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1010-8_0_4_load_70 | 71 | 0.0041048 | 0.0010287 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1010-8_0_4_load_69 | 72 | 0.0036954 | 0.00092616 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1010-8_0_4_load_68 | 74 | 0.0017366 | 0.00043524 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1010-8_0_4_load_72 | 75 | 0.0038366 | 0.00096154 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1010-8_0_4_load_73 | 76 | 0.0023847 | 0.00059767 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1010-8_0_4_load_76 | 77 | 0.0060688 | 0.001521 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1010-8_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0093402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1010-8_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.014899 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1010-8_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.027412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1010-8_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.040819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1010-8_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.031825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1010-8_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.010497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1010-8_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0093543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1010-8_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0056754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1010-8_0_4_line_8 | NAYY 4x150 SE | 6 | 9 | 0.025159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1010-8_0_4_line_9 | NAYY 4x150 SE | 6 | 10 | 0.015933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1010-8_0_4_line_10 | NAYY 4x150 SE | 7 | 11 | 0.029754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1010-8_0_4_line_11 | NAYY 4x150 SE | 8 | 12 | 0.019041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1010-8_0_4_line_12 | NAYY 4x150 SE | 9 | 13 | 0.013545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1010-8_0_4_line_13 | NAYY 4x150 SE | 9 | 14 | 0.01865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1010-8_0_4_line_14 | NAYY 4x150 SE | 10 | 15 | 0.0045169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1010-8_0_4_line_15 | NAYY 4x150 SE | 11 | 33 | 0.023402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1010-8_0_4_line_16 | NAYY 4x150 SE | 11 | 27 | 0.0076407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1010-8_0_4_line_17 | NAYY 4x150 SE | 14 | 38 | 0.030128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
18 | LV_1010-8_0_4_line_18 | NAYY 4x150 SE | 15 | 61 | 0.016598 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1010-8_0_4_line_19 | NAYY 4x150 SE | 16 | 17 | 0.0051776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1010-8_0_4_line_20 | NAYY 4x150 SE | 16 | 18 | 0.023708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1010-8_0_4_line_21 | NAYY 4x150 SE | 17 | 19 | 0.019313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1010-8_0_4_line_22 | NAYY 4x150 SE | 18 | 20 | 0.0016639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1010-8_0_4_line_23 | NAYY 4x150 SE | 19 | 21 | 0.0088989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1010-8_0_4_line_24 | NAYY 4x150 SE | 20 | 22 | 0.023247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1010-8_0_4_line_25 | NAYY 4x150 SE | 21 | 23 | 0.41518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1010-8_0_4_line_26 | NAYY 4x150 SE | 22 | 27 | 0.0018835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1010-8_0_4_line_27 | NAYY 4x150 SE | 23 | 25 | 0.034289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1010-8_0_4_line_28 | NAYY 4x150 SE | 24 | 25 | 0.035254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1010-8_0_4_line_29 | NAYY 4x150 SE | 24 | 26 | 0.20879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1010-8_0_4_line_30 | NAYY 4x150 SE | 26 | 78 | 0.0070797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1010-8_0_4_line_31 | NAYY 4x150 SE | 28 | 29 | 0.025311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1010-8_0_4_line_32 | NAYY 4x150 SE | 29 | 30 | 0.023138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1010-8_0_4_line_33 | NAYY 4x150 SE | 30 | 31 | 0.0038377 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1010-8_0_4_line_34 | NAYY 4x150 SE | 31 | 32 | 0.023778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1010-8_0_4_line_35 | NAYY 4x150 SE | 32 | 36 | 0.02831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1010-8_0_4_line_36 | NAYY 4x150 SE | 33 | 34 | 0.037018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_1010-8_0_4_line_37 | NAYY 4x150 SE | 34 | 35 | 0.00050009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1010-8_0_4_line_38 | NAYY 4x150 SE | 35 | 54 | 0.0038379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1010-8_0_4_line_39 | NAYY 4x150 SE | 36 | 37 | 0.026066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1010-8_0_4_line_40 | NAYY 4x150 SE | 37 | 41 | 0.02726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1010-8_0_4_line_41 | NAYY 4x150 SE | 38 | 39 | 0.012086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1010-8_0_4_line_42 | NAYY 4x150 SE | 39 | 40 | 0.021187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1010-8_0_4_line_43 | NAYY 4x150 SE | 39 | 41 | 0.050187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1010-8_0_4_line_44 | NAYY 4x150 SE | 40 | 42 | 0.019717 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1010-8_0_4_line_45 | NAYY 4x150 SE | 41 | 43 | 0.02666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1010-8_0_4_line_46 | NAYY 4x150 SE | 42 | 44 | 0.019445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1010-8_0_4_line_47 | NAYY 4x150 SE | 42 | 45 | 0.0067425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1010-8_0_4_line_48 | NAYY 4x150 SE | 43 | 46 | 0.042182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1010-8_0_4_line_49 | NAYY 4x150 SE | 44 | 63 | 0.0064856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1010-8_0_4_line_50 | NAYY 4x150 SE | 45 | 55 | 0.0057093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1010-8_0_4_line_51 | NAYY 4x150 SE | 46 | 60 | 0.033919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1010-8_0_4_line_52 | NAYY 4x150 SE | 47 | 48 | 0.011256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1010-8_0_4_line_53 | NAYY 4x150 SE | 48 | 49 | 0.01955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1010-8_0_4_line_54 | NAYY 4x150 SE | 49 | 53 | 0.035484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1010-8_0_4_line_55 | NAYY 4x150 SE | 49 | 54 | 0.012144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
56 | LV_1010-8_0_4_line_56 | NAYY 4x150 SE | 50 | 51 | 0.027015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1010-8_0_4_line_57 | NAYY 4x150 SE | 50 | 52 | 0.0028895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1010-8_0_4_line_58 | NAYY 4x150 SE | 51 | 55 | 0.031532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1010-8_0_4_line_59 | NAYY 4x150 SE | 52 | 56 | 0.039871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1010-8_0_4_line_60 | NAYY 4x150 SE | 53 | 57 | 0.010902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1010-8_0_4_line_61 | NAYY 4x150 SE | 56 | 58 | 0.0057837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1010-8_0_4_line_62 | NAYY 4x150 SE | 56 | 59 | 0.029303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1010-8_0_4_line_63 | NAYY 4x150 SE | 58 | 66 | 0.027313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1010-8_0_4_line_64 | NAYY 4x150 SE | 59 | 67 | 0.017066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1010-8_0_4_line_65 | NAYY 4x150 SE | 61 | 62 | 0.0070128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1010-8_0_4_line_66 | NAYY 4x150 SE | 63 | 64 | 0.011749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1010-8_0_4_line_67 | NAYY 4x150 SE | 63 | 65 | 0.014161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1010-8_0_4_line_68 | NAYY 4x150 SE | 65 | 68 | 0.023879 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1010-8_0_4_line_69 | NAYY 4x150 SE | 68 | 69 | 0.010852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1010-8_0_4_line_70 | NAYY 4x150 SE | 68 | 70 | 0.01584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1010-8_0_4_line_71 | NAYY 4x150 SE | 69 | 71 | 0.030916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1010-8_0_4_line_72 | NAYY 4x150 SE | 70 | 72 | 0.018414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1010-8_0_4_line_73 | NAYY 4x150 SE | 71 | 73 | 0.00075637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1010-8_0_4_line_74 | NAYY 4x150 SE | 72 | 74 | 0.018204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1010-8_0_4_line_75 | NAYY 4x150 SE | 73 | 75 | 0.016097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1010-8_0_4_line_76 | NAYY 4x150 SE | 75 | 76 | 0.02815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1010-8_0_4_line_77 | NAYY 4x150 SE | 77 | 78 | 0.10153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1010-8_0_4_trafo_43 | 0.25 MVA 20/0.4 kV | 79 | 53 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2637873.0263 | 1196499.1069 | 2637880.1002 | 1196505.2061
1 | 2637860.6878 | 1196491.0536 | 2637864.8291 | 1196492.6584 | 2637867.2801 | 1196494.1525 | 2637873.0263 | 1196499.1069
2 | 2637880.1002 | 1196505.2061 | 2637889.8035 | 1196513.5724 | 2637894.0883 | 1196511.7652 | 2637896.9414 | 1196512.3057 | 2637902.5806 | 1196516.5297
3 | 2637860.6878 | 1196491.0536 | 2637860.8396 | 1196492.3441 | 2637860.6546 | 1196493.8994 | 2637860.0327 | 1196495.8743 | 2637858.7474 | 1196497.9562 | 2637836.0933 | 1196522.5479
4 | 2637860.6878 | 1196491.0536 | 2637860.4203 | 1196489.9846 | 2637859.4263 | 1196488.1773 | 2637857.6579 | 1196485.9538 | 2637841.0607 | 1196472.5304 | 2637837.9474 | 1196469.3188
5 | 2637910.9821 | 1196522.8227 | 2637902.5806 | 1196516.5297
6 | 2637836.0933 | 1196522.5479 | 2637829.7554 | 1196529.4278
7 | 2637837.9474 | 1196469.3188 | 2637833.9971 | 1196465.2439
8 | 2637910.9821 | 1196522.8227 | 2637913.9966 | 1196524.3315 | 2637919.3157 | 1196526.3996 | 2637927.019 | 1196528.4496 | 2637935.0849 | 1196529.7903
9 | 2637910.9821 | 1196522.8227 | 2637905.858 | 1196532.062 | 2637902.9577 | 1196536.5794 | 2637902.9577 | 1196536.5794
10 | 2637807.9301 | 1196548.8742 | 2637809.6609 | 1196548.6072 | 2637811.4633 | 1196547.8738 | 2637813.0082 | 1196546.883 | 2637815.596 | 1196544.7982 | 2637829.7554 | 1196529.4278
11 | 2637833.9971 | 1196465.2439 | 2637833.0689 | 1196464.2864 | 2637824.9046 | 1196454.3849 | 2637822.2082 | 1196450.325
12 | 2637935.0849 | 1196529.7903 | 2637937.234 | 1196516.4188
13 | 2637935.0849 | 1196529.7903 | 2637948.2858 | 1196532.1753 | 2637953.436 | 1196533.1169
14 | 2637902.9577 | 1196536.5794 | 2637900.1122 | 1196540.0874
15 | 2637807.9301 | 1196548.8742 | 2637810.1366 | 1196554.1021 | 2637819.7888 | 1196562.3565 | 2637823.5443 | 1196565.6991
16 | 2637807.9301 | 1196548.8742 | 2637806.1123 | 1196548.4403 | 2637801.4876 | 1196544.9869
17 | 2637981.3343 | 1196543.4663 | 2637979.3103 | 1196541.9218 | 2637974.3553 | 1196538.911 | 2637965.054 | 1196535.3945 | 2637960.254 | 1196534.3635 | 2637953.436 | 1196533.1169
18 | 2637900.1122 | 1196540.0874 | 2637889.6564 | 1196552.9775
19 | 2637767.9645 | 1196507.2958 | 2637764.8699 | 1196503.1448
20 | 2637767.9645 | 1196507.2958 | 2637770.3902 | 1196510.5495 | 2637783.2153 | 1196525.4364
21 | 2637764.8699 | 1196503.1448 | 2637753.3263 | 1196487.6608
22 | 2637784.3013 | 1196526.697 | 2637783.2153 | 1196525.4364
23 | 2637748.1762 | 1196480.4058 | 2637751.0459 | 1196484.6021 | 2637753.3263 | 1196487.6608
24 | 2637800.1171 | 1196543.695 | 2637793.8775 | 1196537.8127 | 2637784.3013 | 1196526.697
25 | 2637748.1762 | 1196480.4058 | 2637396.5958 | 1196701.2412
26 | 2637800.1171 | 1196543.695 | 2637801.4876 | 1196544.9869
27 | 2637383.8363 | 1196733.068 | 2637396.5958 | 1196701.2412
28 | 2637383.8363 | 1196733.068 | 2637380.3707 | 1196754.9917 | 2637379.6622 | 1196762.3358 | 2637380.1143 | 1196767.9973
29 | 2637546.2942 | 1196894.3931 | 2637380.1143 | 1196767.9973
30 | 2637547.7661 | 1196901.3088 | 2637547.4676 | 1196899.1057 | 2637546.2942 | 1196894.3931
31 | 2637942.6208 | 1196425.4445 | 2637933.456 | 1196408.2463 | 2637930.6952 | 1196403.1188
32 | 2637942.6208 | 1196425.4445 | 2637947.6988 | 1196434.9735 | 2637953.7739 | 1196445.7152
33 | 2637955.6631 | 1196449.0557 | 2637953.7739 | 1196445.7152
34 | 2637968.5903 | 1196468.9889 | 2637966.1062 | 1196465.6071 | 2637961.8566 | 1196459.4657 | 2637956.1733 | 1196449.9578 | 2637955.6631 | 1196449.0557
35 | 2637968.5903 | 1196468.9889 | 2637971.5211 | 1196472.9789 | 2637977.1814 | 1196480.0965 | 2637986.6073 | 1196490.8046
36 | 2637823.5443 | 1196565.6991 | 2637830.507 | 1196571.8962 | 2637836.3141 | 1196566.6411 | 2637841.044 | 1196569.1168 | 2637852.8303 | 1196577.6076
37 | 2637852.8303 | 1196577.6076 | 2637853.2361 | 1196577.8999
38 | 2637856.3501 | 1196580.1432 | 2637853.2361 | 1196577.8999
39 | 2638004.3718 | 1196509.8781 | 2638000.2529 | 1196505.5235 | 2637987.5046 | 1196491.824 | 2637986.6073 | 1196490.8046
40 | 2638023.1038 | 1196529.682 | 2638004.3718 | 1196509.8781
41 | 2637990.6931 | 1196551.1102 | 2637983.5706 | 1196545.1729 | 2637981.3343 | 1196543.4663
42 | 2637990.6931 | 1196551.1102 | 2637985.003 | 1196571.5187
43 | 2637990.6931 | 1196551.1102 | 2637995.0802 | 1196552.3943 | 2637998.4984 | 1196552.694 | 2638002.5617 | 1196552.1861 | 2638006.7662 | 1196551.0233 | 2638009.8447 | 1196549.6532 | 2638012.4289 | 1196548.1466 | 2638016.0563 | 1196545.5015 | 2638027.8325 | 1196534.7481 | 2638023.1038 | 1196529.682
44 | 2637974.0324 | 1196587.3801 | 2637976.7264 | 1196585.3738 | 2637979.1711 | 1196583.0436 | 2637981.1931 | 1196580.1104 | 2637982.557 | 1196577.651 | 2637983.8012 | 1196574.8351 | 2637985.003 | 1196571.5187
45 | 2638023.1038 | 1196529.682 | 2638032.4758 | 1196520.8811 | 2638035.0354 | 1196519.6522 | 2638037.7427 | 1196519.158 | 2638040.2395 | 1196519.4185 | 2638042.7327 | 1196520.257 | 2638045.3505 | 1196521.8634
46 | 2637974.0324 | 1196587.3801 | 2637982.8751 | 1196598.3311 | 2637986.1878 | 1196602.5564
47 | 2637974.0324 | 1196587.3801 | 2637970.0273 | 1196589.5336 | 2637968.0197 | 1196590.4213
48 | 2638078.3907 | 1196543.9968 | 2638076.8883 | 1196544.2874 | 2638074.3818 | 1196544.3493 | 2638071.8461 | 1196544.2108 | 2638068.5597 | 1196543.5451 | 2638065.6034 | 1196542.4591 | 2638063.5385 | 1196541.3676 | 2638060.235 | 1196538.5895 | 2638057.2671 | 1196535.7357 | 2638047.7824 | 1196523.9467 | 2638045.3505 | 1196521.8634
49 | 2637990.1894 | 1196607.6604 | 2637986.1878 | 1196602.5564
50 | 2637962.6214 | 1196592.2437 | 2637966.2844 | 1196591.1886 | 2637968.0197 | 1196590.4213
51 | 2638078.3907 | 1196543.9968 | 2638086.2766 | 1196552.0625 | 2638089.802 | 1196554.6753 | 2638092.3775 | 1196555.7478 | 2638094.6458 | 1196556.0068 | 2638096.8795 | 1196555.7209 | 2638099.5907 | 1196554.6042 | 2638104.3622 | 1196551.733 | 2638106.2002 | 1196550.1516
52 | 2637892.6155 | 1196603.0699 | 2637882.7707 | 1196597.6125
53 | 2637866.2034 | 1196587.2414 | 2637880.3069 | 1196596.2467 | 2637882.7707 | 1196597.6125
54 | 2637866.2034 | 1196587.2414 | 2637877.3205 | 1196578.2735 | 2637880.1727 | 1196576.535 | 2637882.7511 | 1196575.9399 | 2637885.324 | 1196576.223 | 2637889.0056 | 1196577.0245 | 2637897.625 | 1196579.0652
55 | 2637866.2034 | 1196587.2414 | 2637856.3501 | 1196580.1432
56 | 2637924.9227 | 1196635.6509 | 2637933.3712 | 1196619.8735 | 2637936.4035 | 1196614.9567 | 2637938.4902 | 1196612.3464
57 | 2637924.9227 | 1196635.6509 | 2637923.3003 | 1196638.042
58 | 2637962.6214 | 1196592.2437 | 2637957.4413 | 1196597.1024 | 2637953.1364 | 1196600.8883 | 2637942.5869 | 1196608.0365 | 2637939.4364 | 1196611.1627 | 2637938.4902 | 1196612.3464
59 | 2637932.4176 | 1196668.1608 | 2637920.6871 | 1196657.3583 | 2637917.8348 | 1196654.2941 | 2637916.2046 | 1196651.9158 | 2637915.5028 | 1196649.6768 | 2637915.4227 | 1196647.8864 | 2637916.0428 | 1196646.2005 | 2637923.3003 | 1196638.042
60 | 2637908.2339 | 1196581.5769 | 2637897.625 | 1196579.0652
61 | 2637932.4176 | 1196668.1608 | 2637934.0407 | 1196673.7121
62 | 2637932.4176 | 1196668.1608 | 2637939.3652 | 1196666.8374 | 2637959.0373 | 1196677.1903
63 | 2637934.0407 | 1196673.7121 | 2637935.2507 | 1196677.8507 | 2637936.0869 | 1196685.3268 | 2637928.1452 | 1196698.6127
64 | 2637974.1396 | 1196685.1383 | 2637959.0373 | 1196677.1903
65 | 2637885.2386 | 1196558.4238 | 2637889.6564 | 1196552.9775
66 | 2637990.1894 | 1196607.6604 | 2637988.7941 | 1196607.8739 | 2637979.3069 | 1196612.0493
67 | 2637990.1894 | 1196607.6604 | 2637992.039 | 1196607.8723 | 2637996.3075 | 1196609.8227 | 2638002.7075 | 1196613.9332
68 | 2638022.1222 | 1196627.8187 | 2638007.7931 | 1196617.1996 | 2638002.7075 | 1196613.9332
69 | 2638022.1222 | 1196627.8187 | 2638030.1254 | 1196635.1481
70 | 2638022.1222 | 1196627.8187 | 2638033.4672 | 1196616.7646
71 | 2638052.0588 | 1196656.9189 | 2638037.488 | 1196641.8907 | 2638030.1254 | 1196635.1481
72 | 2638033.4672 | 1196616.7646 | 2638044.4878 | 1196606.0266 | 2638045.3569 | 1196604.7091 | 2638045.8454 | 1196603.3448
73 | 2638052.0588 | 1196656.9189 | 2638052.5853 | 1196657.4619
74 | 2638035.2706 | 1196589.0527 | 2638044.5464 | 1196599.2009 | 2638045.3678 | 1196600.5958 | 2638045.884 | 1196602.0777 | 2638045.8454 | 1196603.3448 | 2638045.8454 | 1196603.3448
75 | 2638052.5853 | 1196657.4619 | 2638064.2891 | 1196646.4099
76 | 2638084.7555 | 1196627.0831 | 2638064.2891 | 1196646.4099
77 | 2637547.7661 | 1196901.3088 | 2637538.2012 | 1197002.3829

## bus_geodata
| x | y | coords
0 | 2637873.0263 | 1196499.1069
1 | 2637880.1002 | 1196505.2061
2 | 2637860.6878 | 1196491.0535
3 | 2637902.5806 | 1196516.5297
4 | 2637836.0933 | 1196522.5479
5 | 2637837.9474 | 1196469.3188
6 | 2637910.9821 | 1196522.8227
7 | 2637829.7554 | 1196529.4278
8 | 2637833.9971 | 1196465.2439
9 | 2637935.0849 | 1196529.7903
10 | 2637902.9577 | 1196536.5794
11 | 2637807.9301 | 1196548.8742
12 | 2637822.2082 | 1196450.325
13 | 2637937.234 | 1196516.4188
14 | 2637953.436 | 1196533.1169
15 | 2637900.1122 | 1196540.0874
16 | 2637767.9645 | 1196507.2958
17 | 2637764.8699 | 1196503.1448
18 | 2637783.2153 | 1196525.4364
19 | 2637753.3263 | 1196487.6608
20 | 2637784.3013 | 1196526.697
21 | 2637748.1762 | 1196480.4058
22 | 2637800.1171 | 1196543.695
23 | 2637396.5958 | 1196701.2412
24 | 2637380.1143 | 1196767.9973
25 | 2637383.8363 | 1196733.068
26 | 2637546.2942 | 1196894.3931
27 | 2637801.4876 | 1196544.9869
28 | 2637930.6952 | 1196403.1188
29 | 2637942.6208 | 1196425.4445
30 | 2637953.7739 | 1196445.7152
31 | 2637955.6631 | 1196449.0557
32 | 2637968.5903 | 1196468.9889
33 | 2637823.5443 | 1196565.6991
34 | 2637852.8303 | 1196577.6076
35 | 2637853.2361 | 1196577.8999
36 | 2637986.6073 | 1196490.8046
37 | 2638004.3718 | 1196509.8781
38 | 2637981.3343 | 1196543.4663
39 | 2637990.6931 | 1196551.1102
40 | 2637985.003 | 1196571.5187
41 | 2638023.1038 | 1196529.682
42 | 2637974.0324 | 1196587.3801
43 | 2638045.3505 | 1196521.8634
44 | 2637986.1878 | 1196602.5564
45 | 2637968.0197 | 1196590.4213
46 | 2638078.3907 | 1196543.9968
47 | 2637892.6155 | 1196603.0699
48 | 2637882.7707 | 1196597.6125
49 | 2637866.2034 | 1196587.2414
50 | 2637924.9227 | 1196635.6509
51 | 2637938.4902 | 1196612.3464
52 | 2637923.3003 | 1196638.042
53 | 2637897.625 | 1196579.0652
54 | 2637856.3501 | 1196580.1432
55 | 2637962.6214 | 1196592.2437
56 | 2637932.4176 | 1196668.1608
57 | 2637908.2339 | 1196581.5769
58 | 2637934.0407 | 1196673.7121
59 | 2637959.0373 | 1196677.1903
60 | 2638106.2002 | 1196550.1516
61 | 2637889.6564 | 1196552.9775
62 | 2637885.2386 | 1196558.4238
63 | 2637990.1894 | 1196607.6604
64 | 2637979.3069 | 1196612.0493
65 | 2638002.7075 | 1196613.9332
66 | 2637928.1452 | 1196698.6127
67 | 2637974.1396 | 1196685.1383
68 | 2638022.1222 | 1196627.8187
69 | 2638030.1254 | 1196635.1481
70 | 2638033.4672 | 1196616.7646
71 | 2638052.0588 | 1196656.9189
72 | 2638045.8454 | 1196603.3448
73 | 2638052.5853 | 1196657.4619
74 | 2638035.2706 | 1196589.0527
75 | 2638064.2891 | 1196646.4099
76 | 2638084.7555 | 1196627.0831
77 | 2637538.2012 | 1197002.3829
78 | 2637547.7661 | 1196901.3088
79 | 2637866.2034 | 1196587.2414

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98527 | -0.10252 | 0.00089182 | 0.00022351
1 | 0.98474 | -0.10622 | 0.0021084 | 0.00052842
2 | 0.98611 | -0.096597 | 0 | 0
3 | 0.98323 | -0.11688 | 0.0021346 | 0.00053497
4 | 0.98853 | -0.079576 | 0.0060763 | 0.0015229
5 | 0.98583 | -0.098554 | 0.0028921 | 0.00072482
6 | 0.98267 | -0.12089 | 0 | 0
7 | 0.98912 | -0.075493 | 0.0012232 | 0.00030657
8 | 0.98581 | -0.098734 | 0.0017817 | 0.00044654
9 | 0.98142 | -0.12974 | 0.0026159 | 0.0006556
10 | 0.98246 | -0.12238 | 0.0025957 | 0.00065055
11 | 0.99099 | -0.062416 | 0 | 0
12 | 0.98577 | -0.098991 | 0.0013115 | 0.0003287
13 | 0.98111 | -0.13194 | 0.015649 | 0.0039219
14 | 0.98065 | -0.13514 | 0.0038523 | 0.00096547
15 | 0.98241 | -0.12268 | 0.0020814 | 0.00052164
16 | 0.98907 | -0.075871 | 0.0010356 | 0.00025955
17 | 0.98892 | -0.076908 | 0.0012298 | 0.00030822
18 | 0.98978 | -0.070874 | 0.0013169 | 0.00033004
19 | 0.98841 | -0.080538 | 0.0013702 | 0.0003434
20 | 0.98984 | -0.070501 | 0.0014049 | 0.00035211
21 | 0.98819 | -0.082087 | 0.0013156 | 0.00032973
22 | 0.99062 | -0.064964 | 0.0021409 | 0.00053657
23 | 0.9787 | -0.14935 | 0.0034442 | 0.00086321
24 | 0.97749 | -0.158 | 0.0020826 | 0.00052195
25 | 0.97809 | -0.15372 | 0.00061539 | 0.00015423
26 | 0.97459 | -0.17882 | 0.0034326 | 0.0008603
27 | 0.99069 | -0.064475 | 0.00097288 | 0.00024383
28 | 0.97287 | -0.19081 | 0.0026044 | 0.00065274
29 | 0.97297 | -0.19011 | 0.0017221 | 0.0004316
30 | 0.97311 | -0.18906 | 0.0020206 | 0.0005064
31 | 0.97315 | -0.1888 | 0.0020421 | 0.0005118
32 | 0.97344 | -0.1867 | 0.0015653 | 0.00039231
33 | 0.99276 | -0.050069 | 0.0022906 | 0.00057408
34 | 0.9956 | -0.030343 | 0.0024477 | 0.00061345
35 | 0.99564 | -0.030073 | 0.0020405 | 0.00051141
36 | 0.97385 | -0.18373 | 0.005863 | 0.0014694
37 | 0.97446 | -0.17939 | 0.007175 | 0.0017982
38 | 0.97889 | -0.14765 | 0.002562 | 0.0006421
39 | 0.97753 | -0.1574 | 0 | 0
40 | 0.97604 | -0.16803 | 0.0019962 | 0.00050029
41 | 0.97537 | -0.1728 | 0 | 0
42 | 0.97471 | -0.17754 | 0 | 0
43 | 0.97513 | -0.17457 | 0.0028018 | 0.00070219
44 | 0.97384 | -0.18379 | 0.0036854 | 0.00092365
45 | 0.97456 | -0.17863 | 0.0034906 | 0.00087482
46 | 0.97491 | -0.17613 | 0 | 0
47 | 0.99672 | -0.022636 | 0.0042282 | 0.0010597
48 | 0.99679 | -0.022158 | 0.0016655 | 0.00041742
49 | 0.99695 | -0.021 | 0 | 0
50 | 0.97349 | -0.18629 | 0 | 0
51 | 0.97391 | -0.18329 | 0.0013382 | 0.0003354
52 | 0.97345 | -0.18661 | 0.0018771 | 0.00047046
53 | 1 | 0 | -0.18377 | -0.046292
54 | 0.99594 | -0.027976 | 0.0086335 | 0.0021637
55 | 0.97446 | -0.17934 | 0 | 0
56 | 0.97294 | -0.19026 | 0 | 0
57 | 0.99996 | -0.00025648 | 0.0023566 | 0.00059061
58 | 0.97292 | -0.19042 | 0.0022184 | 0.00055598
59 | 0.97269 | -0.19211 | 0.0040647 | 0.0010187
60 | 0.97474 | -0.17738 | 0.0035096 | 0.00087959
61 | 0.98231 | -0.12343 | 0.0021858 | 0.00054782
62 | 0.98229 | -0.12358 | 0.0021656 | 0.00054275
63 | 0.97358 | -0.18562 | 0 | 0
64 | 0.97356 | -0.18579 | 0.0013461 | 0.00033736
65 | 0.97305 | -0.18944 | 0.0013407 | 0.00033602
66 | 0.9729 | -0.19056 | 0.00047287 | 0.00011851
67 | 0.97264 | -0.19245 | 0.0019146 | 0.00047985
68 | 0.97221 | -0.19553 | 0 | 0
69 | 0.97197 | -0.19722 | 0.0043993 | 0.0011026
70 | 0.97199 | -0.19712 | 0.0040305 | 0.0010101
71 | 0.9715 | -0.2006 | 0.0041048 | 0.0010287
72 | 0.97184 | -0.19817 | 0.0036954 | 0.00092616
73 | 0.9715 | -0.20065 | 0 | 0
74 | 0.97179 | -0.19851 | 0.0017366 | 0.00043524
75 | 0.97135 | -0.20171 | 0.0038366 | 0.00096154
76 | 0.97125 | -0.20242 | 0.0023847 | 0.00059767
77 | 0.97362 | -0.18576 | 0.0060688 | 0.001521
78 | 0.97452 | -0.17928 | 0 | 0
79 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.11626 | 0.029266 | -0.1162 | -0.029243 | 5.9924e-05 | 2.2691e-05 | 0.17563 | 0.17563 | 0.17563 | 0.98527 | -0.10252 | 0.98474 | -0.10622 | 21.6823
1 | -0.11715 | -0.029489 | 0.11725 | 0.029526 | 9.7059e-05 | 3.6761e-05 | 0.17697 | 0.17697 | 0.17697 | 0.98527 | -0.10252 | 0.98611 | -0.096597 | 21.8486
2 | 0.11409 | 0.028715 | -0.11392 | -0.028651 | 0.00016954 | 6.4165e-05 | 0.17244 | 0.17244 | 0.17244 | 0.98474 | -0.10622 | 0.98323 | -0.11688 | 21.289
3 | -0.12323 | -0.031026 | 0.12353 | 0.031138 | 0.00029375 | 0.00011142 | 0.18601 | 0.18601 | 0.18601 | 0.98611 | -0.096597 | 0.98853 | -0.079576 | 22.9639
4 | 0.005987 | 0.0015 | -0.0059854 | -0.0014998 | 1.6208e-06 | 2.175e-07 | 0.0090341 | 0.0090343 | 0.0090343 | 0.98611 | -0.096597 | 0.98583 | -0.098554 | 3.346
5 | 0.11179 | 0.028116 | -0.11172 | -0.028092 | 6.2515e-05 | 2.3645e-05 | 0.16921 | 0.16921 | 0.16921 | 0.98323 | -0.11688 | 0.98267 | -0.12089 | 20.8902
6 | -0.1296 | -0.03266 | 0.12968 | 0.032689 | 7.4101e-05 | 2.814e-05 | 0.19515 | 0.19515 | 0.19515 | 0.98853 | -0.079576 | 0.98912 | -0.075493 | 24.093
7 | 0.0030934 | 0.00077497 | -0.0030933 | -0.00077501 | 7.7202e-08 | -4.2667e-08 | 0.004669 | 0.004669 | 0.004669 | 0.98583 | -0.098554 | 0.98581 | -0.098734 | 1.7293
8 | 0.10269 | 0.025829 | -0.10257 | -0.025781 | 0.00012659 | 4.7735e-05 | 0.15554 | 0.15554 | 0.15554 | 0.98267 | -0.12089 | 0.98142 | -0.12974 | 19.2019
9 | 0.0090311 | 0.0022632 | -0.0090293 | -0.0022627 | 1.8594e-06 | 5.1336e-07 | 0.013675 | 0.013676 | 0.013676 | 0.98267 | -0.12089 | 0.98246 | -0.12238 | 5.065
10 | -0.1309 | -0.032995 | 0.13114 | 0.033086 | 0.00024016 | 9.1223e-05 | 0.19699 | 0.19699 | 0.19699 | 0.98912 | -0.075493 | 0.99099 | -0.062416 | 24.3202
11 | 0.0013116 | 0.00032848 | -0.0013115 | -0.0003287 | 4.6567e-08 | -2.2484e-07 | 0.0019797 | 0.0019798 | 0.0019798 | 0.98581 | -0.098734 | 0.98577 | -0.098991 | 0.73324
12 | 0.015653 | 0.0039235 | -0.015649 | -0.0039219 | 4.7609e-06 | 1.66e-06 | 0.023734 | 0.023734 | 0.023734 | 0.98142 | -0.12974 | 0.98111 | -0.13194 | 8.7902
13 | 0.084296 | 0.021202 | -0.084232 | -0.021178 | 6.3395e-05 | 2.3676e-05 | 0.12784 | 0.12784 | 0.12784 | 0.98142 | -0.12974 | 0.98065 | -0.13514 | 15.7822
14 | 0.0064335 | 0.0016121 | -0.0064333 | -0.0016121 | 2.6761e-07 | 4.5733e-08 | 0.0097441 | 0.0097441 | 0.0097441 | 0.98246 | -0.12238 | 0.98241 | -0.12268 | 3.6089
15 | -0.15783 | -0.039797 | 0.1581 | 0.039901 | 0.00027357 | 0.00010431 | 0.23707 | 0.23707 | 0.23707 | 0.99099 | -0.062416 | 0.99276 | -0.050069 | 29.2678
16 | 0.026685 | 0.0067106 | -0.026677 | -0.0067078 | 7.6577e-06 | 2.8468e-06 | 0.040077 | 0.040077 | 0.040077 | 0.99099 | -0.062416 | 0.99069 | -0.064475 | 14.8432
17 | 0.08038 | 0.020213 | -0.08024 | -0.02016 | 0.00013989 | 5.3045e-05 | 0.12199 | 0.12199 | 0.12199 | 0.98065 | -0.13514 | 0.97889 | -0.14765 | 22.5909
18 | 0.0043519 | 0.0010905 | -0.0043514 | -0.0010905 | 4.4999e-07 | -3.706e-08 | 0.0065915 | 0.0065916 | 0.0065916 | 0.98241 | -0.12268 | 0.98231 | -0.12343 | 2.4413
19 | 0.01977 | 0.0049726 | -0.019767 | -0.0049716 | 2.8595e-06 | 1.0333e-06 | 0.02975 | 0.02975 | 0.02975 | 0.98907 | -0.075871 | 0.98892 | -0.076908 | 11.0185
20 | -0.020806 | -0.0052322 | 0.02082 | 0.0052374 | 1.45e-05 | 5.2726e-06 | 0.031308 | 0.031308 | 0.031308 | 0.98907 | -0.075871 | 0.98978 | -0.070874 | 11.5955
21 | 0.018538 | 0.0046634 | -0.018528 | -0.00466 | 9.3806e-06 | 3.3603e-06 | 0.027899 | 0.027899 | 0.027899 | 0.98892 | -0.076908 | 0.98841 | -0.080538 | 10.3331
22 | -0.022137 | -0.0055675 | 0.022138 | 0.0055679 | 1.1504e-06 | 4.2109e-07 | 0.033288 | 0.033287 | 0.033288 | 0.98978 | -0.070874 | 0.98984 | -0.070501 | 12.3287
23 | 0.017158 | 0.0043166 | -0.017154 | -0.0043153 | 3.7068e-06 | 1.3116e-06 | 0.025837 | 0.025837 | 0.025837 | 0.98841 | -0.080538 | 0.98819 | -0.082087 | 9.5691
24 | -0.023543 | -0.00592 | 0.023562 | 0.0059267 | 1.8178e-05 | 6.6925e-06 | 0.0354 | 0.035399 | 0.0354 | 0.98984 | -0.070501 | 0.99062 | -0.064964 | 13.1109
25 | 0.015839 | 0.0039856 | -0.015691 | -0.0039341 | 0.00014745 | 5.1443e-05 | 0.023856 | 0.023857 | 0.023857 | 0.98819 | -0.082087 | 0.9787 | -0.14935 | 8.8361
26 | -0.025702 | -0.0064633 | 0.025704 | 0.0064639 | 1.7525e-06 | 6.498e-07 | 0.038615 | 0.038615 | 0.038615 | 0.99062 | -0.064964 | 0.99069 | -0.064475 | 14.302
27 | 0.012247 | 0.0030709 | -0.01224 | -0.0030685 | 7.419e-06 | 2.4228e-06 | 0.018621 | 0.018621 | 0.018621 | 0.9787 | -0.14935 | 0.97809 | -0.15372 | 6.8967
28 | -0.011617 | -0.0029121 | 0.011624 | 0.0029143 | 6.8801e-06 | 2.204e-06 | 0.017685 | 0.017685 | 0.017685 | 0.97749 | -0.158 | 0.97809 | -0.15372 | 6.55
29 | 0.0095347 | 0.0023901 | -0.0095072 | -0.0023822 | 2.7449e-05 | 7.9479e-06 | 0.014515 | 0.014516 | 0.014516 | 0.97749 | -0.158 | 0.97459 | -0.17882 | 5.3761
30 | 0.0060746 | 0.0015219 | -0.0060742 | -0.0015218 | 3.8001e-07 | 5.7942e-08 | 0.0092746 | 0.0092746 | 0.0092746 | 0.97459 | -0.17882 | 0.97452 | -0.17928 | 3.435
31 | -0.0026044 | -0.00065274 | 0.0026047 | 0.00065252 | 2.5062e-07 | -2.1793e-07 | 0.0039835 | 0.0039834 | 0.0039835 | 0.97287 | -0.19081 | 0.97297 | -0.19011 | 1.4754
32 | -0.0043268 | -0.0010841 | 0.0043274 | 0.0010841 | 6.3219e-07 | -4.4258e-08 | 0.0066171 | 0.006617 | 0.0066171 | 0.97297 | -0.19011 | 0.97311 | -0.18906 | 2.4508
33 | -0.006348 | -0.0015905 | 0.0063482 | 0.0015905 | 2.2563e-07 | 3.9103e-08 | 0.0097067 | 0.0097067 | 0.0097067 | 0.97311 | -0.18906 | 0.97315 | -0.1888 | 3.5951
34 | -0.0083903 | -0.0021023 | 0.0083928 | 0.002103 | 2.4421e-06 | 6.4374e-07 | 0.012829 | 0.012829 | 0.012829 | 0.97315 | -0.1888 | 0.97344 | -0.1867 | 4.7516
35 | -0.0099581 | -0.0024953 | 0.0099622 | 0.0024965 | 4.0932e-06 | 1.2222e-06 | 0.015222 | 0.015222 | 0.015222 | 0.97344 | -0.1867 | 0.97385 | -0.18373 | 5.6378
36 | -0.16039 | -0.040475 | 0.16084 | 0.040645 | 0.00044536 | 0.00016985 | 0.2405 | 0.2405 | 0.2405 | 0.99276 | -0.050069 | 0.9956 | -0.030343 | 29.6917
37 | -0.16328 | -0.041259 | 0.16329 | 0.041261 | 6.201e-06 | 2.3655e-06 | 0.24416 | 0.24416 | 0.24416 | 0.9956 | -0.030343 | 0.99564 | -0.030073 | 30.1432
38 | -0.16533 | -0.041772 | 0.16538 | 0.041791 | 4.8785e-05 | 1.8614e-05 | 0.24721 | 0.24721 | 0.24721 | 0.99564 | -0.030073 | 0.99594 | -0.027976 | 30.5197
39 | -0.015825 | -0.0039659 | 0.015835 | 0.0039692 | 9.5098e-06 | 3.3331e-06 | 0.02418 | 0.02418 | 0.02418 | 0.97385 | -0.18373 | 0.97446 | -0.17939 | 8.9557
40 | -0.02301 | -0.0057675 | 0.023031 | 0.0057752 | 2.1e-05 | 7.737e-06 | 0.035137 | 0.035136 | 0.035137 | 0.97446 | -0.17939 | 0.97537 | -0.1728 | 13.0135
41 | 0.077678 | 0.019518 | -0.077573 | -0.019477 | 0.00010518 | 4.0302e-05 | 0.1181 | 0.1181 | 0.1181 | 0.97889 | -0.14765 | 0.97753 | -0.1574 | 43.7395
42 | 0.048165 | 0.012097 | -0.048094 | -0.01207 | 7.1087e-05 | 2.7076e-05 | 0.073328 | 0.073328 | 0.073328 | 0.97753 | -0.1574 | 0.97604 | -0.16803 | 27.1584
43 | 0.029408 | 0.0073803 | -0.029345 | -0.0073568 | 6.2767e-05 | 2.3513e-05 | 0.044769 | 0.044769 | 0.044769 | 0.97753 | -0.1574 | 0.97537 | -0.1728 | 16.5811
44 | 0.046098 | 0.01157 | -0.046037 | -0.011546 | 6.0778e-05 | 2.313e-05 | 0.070285 | 0.070285 | 0.070285 | 0.97604 | -0.16803 | 0.97471 | -0.17754 | 26.0313
45 | 0.0063143 | 0.0015816 | -0.0063128 | -0.0015814 | 1.5436e-06 | 2.6104e-07 | 0.0096327 | 0.0096328 | 0.0096328 | 0.97537 | -0.1728 | 0.97513 | -0.17457 | 3.5677
46 | 0.03064 | 0.0076871 | -0.030613 | -0.0076771 | 2.6551e-05 | 9.9696e-06 | 0.046778 | 0.046779 | 0.046779 | 0.97471 | -0.17754 | 0.97384 | -0.18379 | 17.3254
47 | 0.015397 | 0.0038594 | -0.015395 | -0.0038586 | 2.3247e-06 | 8.101e-07 | 0.023506 | 0.023506 | 0.023506 | 0.97471 | -0.17754 | 0.97456 | -0.17863 | 8.706
48 | 0.003511 | 0.00087917 | -0.0035102 | -0.00087941 | 7.555e-07 | -2.3552e-07 | 0.0053574 | 0.0053576 | 0.0053576 | 0.97513 | -0.17457 | 0.97491 | -0.17613 | 1.9843
49 | 0.026928 | 0.0067535 | -0.026921 | -0.0067509 | 6.852e-06 | 2.5547e-06 | 0.041147 | 0.041147 | 0.041147 | 0.97384 | -0.18379 | 0.97358 | -0.18562 | 15.2397
50 | 0.011905 | 0.0029837 | -0.011903 | -0.0029834 | 1.177e-06 | 3.8158e-07 | 0.018177 | 0.018177 | 0.018177 | 0.97456 | -0.17863 | 0.97446 | -0.17934 | 6.7321
51 | 0.0035102 | 0.00087941 | -0.0035096 | -0.00087959 | 6.0754e-07 | -1.892e-07 | 0.0053576 | 0.0053577 | 0.0053577 | 0.97491 | -0.17613 | 0.97474 | -0.17738 | 1.9843
52 | -0.0042282 | -0.0010597 | 0.0042285 | 0.0010597 | 2.7987e-07 | -3.9074e-08 | 0.0063124 | 0.0063123 | 0.0063124 | 0.99672 | -0.022636 | 0.99679 | -0.022158 | 2.3379
53 | -0.005894 | -0.0014771 | 0.0058949 | 0.0014772 | 9.4441e-07 | 1.0835e-07 | 0.0087986 | 0.0087985 | 0.0087986 | 0.99679 | -0.022158 | 0.99695 | -0.021 | 3.2587
54 | -0.18008 | -0.045497 | 0.18061 | 0.045701 | 0.0005337 | 0.00020388 | 0.26891 | 0.26891 | 0.26891 | 0.99695 | -0.021 | 1 | 0 | 33.1984
55 | 0.17418 | 0.04402 | -0.17401 | -0.043955 | 0.0001709 | 6.5255e-05 | 0.26011 | 0.26011 | 0.26011 | 0.99695 | -0.021 | 0.99594 | -0.027976 | 32.1122
56 | -0.010554 | -0.0026445 | 0.010559 | 0.0026459 | 4.3872e-06 | 1.3513e-06 | 0.016132 | 0.016132 | 0.016132 | 0.97349 | -0.18629 | 0.97391 | -0.18329 | 5.9749
57 | 0.010554 | 0.0026445 | -0.010554 | -0.0026444 | 4.6924e-07 | 1.4455e-07 | 0.016132 | 0.016132 | 0.016132 | 0.97349 | -0.18629 | 0.97345 | -0.18661 | 5.9749
58 | -0.011897 | -0.0029812 | 0.011903 | 0.0029834 | 6.5008e-06 | 2.1077e-06 | 0.018177 | 0.018177 | 0.018177 | 0.97391 | -0.18329 | 0.97446 | -0.17934 | 6.7322
59 | 0.0086766 | 0.0021739 | -0.0086723 | -0.0021727 | 4.3764e-06 | 1.1878e-06 | 0.013263 | 0.013263 | 0.013263 | 0.97345 | -0.18661 | 0.97294 | -0.19026 | 4.9122
60 | 0.0023566 | 0.0005905 | -0.0023566 | -0.00059061 | 8.3655e-08 | -1.1085e-07 | 0.0035067 | 0.0035067 | 0.0035067 | 1 | 0 | 0.99996 | -0.00025648 | 1.2988
61 | 0.0026913 | 0.00067411 | -0.0026913 | -0.00067415 | 6.1142e-08 | -4.831e-08 | 0.0041159 | 0.004116 | 0.004116 | 0.97294 | -0.19026 | 0.97292 | -0.19042 | 1.5244
62 | 0.0059809 | 0.0014986 | -0.0059794 | -0.0014984 | 1.5299e-06 | 2.2461e-07 | 0.0091471 | 0.0091472 | 0.0091472 | 0.97294 | -0.19026 | 0.97269 | -0.19211 | 3.3879
63 | 0.00047288 | 0.00011818 | -0.00047287 | -0.00011851 | 8.9136e-09 | -3.3575e-07 | 0.00072312 | 0.00072324 | 0.00072324 | 0.97292 | -0.19042 | 0.9729 | -0.19056 | 0.26787
64 | 0.0019147 | 0.00047967 | -0.0019146 | -0.00047985 | 9.1367e-08 | -1.7668e-07 | 0.0029291 | 0.0029291 | 0.0029291 | 0.97269 | -0.19211 | 0.97264 | -0.19245 | 1.0849
65 | 0.0021656 | 0.00054268 | -0.0021656 | -0.00054275 | 4.7093e-08 | -7.0661e-08 | 0.0032805 | 0.0032805 | 0.0032805 | 0.98231 | -0.12343 | 0.98229 | -0.12358 | 1.215
66 | 0.0013461 | 0.00033723 | -0.0013461 | -0.00033736 | 3.1032e-08 | -1.3416e-07 | 0.0020573 | 0.0020574 | 0.0020574 | 0.97358 | -0.18562 | 0.97356 | -0.18579 | 0.762
67 | 0.025575 | 0.0064137 | -0.025561 | -0.0064087 | 1.3502e-05 | 5.0172e-06 | 0.03909 | 0.03909 | 0.03909 | 0.97358 | -0.18562 | 0.97305 | -0.18944 | 14.4778
68 | 0.024221 | 0.0060727 | -0.0242 | -0.0060651 | 2.0443e-05 | 7.5663e-06 | 0.03704 | 0.03704 | 0.03704 | 0.97305 | -0.18944 | 0.97221 | -0.19553 | 13.7185
69 | 0.014735 | 0.0036931 | -0.014731 | -0.0036919 | 3.4442e-06 | 1.1902e-06 | 0.022552 | 0.022553 | 0.022553 | 0.97221 | -0.19553 | 0.97197 | -0.19722 | 8.3528
70 | 0.0094655 | 0.002372 | -0.0094634 | -0.0023714 | 2.0745e-06 | 6.0152e-07 | 0.014487 | 0.014487 | 0.014487 | 0.97221 | -0.19553 | 0.97199 | -0.19712 | 5.3657
71 | 0.010332 | 0.0025893 | -0.010327 | -0.0025879 | 4.8267e-06 | 1.4734e-06 | 0.015818 | 0.015818 | 0.015818 | 0.97197 | -0.19722 | 0.9715 | -0.2006 | 5.8584
72 | 0.0054329 | 0.0013613 | -0.0054321 | -0.0013612 | 7.9487e-07 | 7.7517e-08 | 0.0083172 | 0.0083173 | 0.0083173 | 0.97199 | -0.19712 | 0.97184 | -0.19817 | 3.0805
73 | 0.0062225 | 0.0015591 | -0.0062225 | -0.0015591 | 4.2871e-08 | 7.1233e-09 | 0.0095306 | 0.0095306 | 0.0095306 | 0.9715 | -0.2006 | 0.9715 | -0.20065 | 3.5299
74 | 0.0017367 | 0.00043505 | -0.0017366 | -0.00043524 | 8.0322e-08 | -1.9466e-07 | 0.0026591 | 0.0026592 | 0.0026592 | 0.97184 | -0.19817 | 0.97179 | -0.19851 | 0.98487
75 | 0.0062225 | 0.0015591 | -0.0062215 | -0.0015589 | 9.124e-07 | 1.5163e-07 | 0.0095306 | 0.0095307 | 0.0095307 | 0.9715 | -0.20065 | 0.97135 | -0.20171 | 3.5299
76 | 0.0023849 | 0.00059741 | -0.0023847 | -0.00059767 | 2.3446e-07 | -2.5823e-07 | 0.0036534 | 0.0036535 | 0.0036535 | 0.97135 | -0.20171 | 0.97125 | -0.20242 | 1.3532
77 | -0.0060688 | -0.001521 | 0.0060742 | 0.0015218 | 5.4497e-06 | 8.3227e-07 | 0.0092751 | 0.0092746 | 0.0092751 | 0.97362 | -0.18576 | 0.97452 | -0.17928 | 3.4352

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18672 | 0.04703

## res_load
| p_mw | q_mvar
0 | 0.00089182 | 0.00022351
1 | 0.0021084 | 0.00052842
2 | 0.0021346 | 0.00053497
3 | 0.0060763 | 0.0015229
4 | 0.0028921 | 0.00072482
5 | 0.0012232 | 0.00030657
6 | 0.0017817 | 0.00044654
7 | 0.0026159 | 0.0006556
8 | 0.0025957 | 0.00065055
9 | 0.0013115 | 0.0003287
10 | 0.015649 | 0.0039219
11 | 0.0038523 | 0.00096547
12 | 0.0020814 | 0.00052164
13 | 0.0010356 | 0.00025955
14 | 0.0012298 | 0.00030822
15 | 0.0013169 | 0.00033004
16 | 0.0013702 | 0.0003434
17 | 0.0014049 | 0.00035211
18 | 0.0013156 | 0.00032973
19 | 0.0021409 | 0.00053657
20 | 0.0034442 | 0.00086321
21 | 0.0020826 | 0.00052195
22 | 0.00061539 | 0.00015423
23 | 0.0034326 | 0.0008603
24 | 0.00097288 | 0.00024383
25 | 0.0026044 | 0.00065274
26 | 0.0017221 | 0.0004316
27 | 0.0020206 | 0.0005064
28 | 0.0020421 | 0.0005118
29 | 0.0015653 | 0.00039231
30 | 0.0022906 | 0.00057408
31 | 0.0024477 | 0.00061345
32 | 0.0020405 | 0.00051141
33 | 0.005863 | 0.0014694
34 | 0.007175 | 0.0017982
35 | 0.002562 | 0.0006421
36 | 0.0019962 | 0.00050029
37 | 0.0028018 | 0.00070219
38 | 0.0036854 | 0.00092365
39 | 0.0034906 | 0.00087482
40 | 0.0042282 | 0.0010597
41 | 0.0016655 | 0.00041742
42 | 0.0013382 | 0.0003354
43 | 0.0018771 | 0.00047046
44 | 0.0029476 | 0.00073874
45 | 0.0086335 | 0.0021637
46 | 0.0023566 | 0.00059061
47 | 0.0022184 | 0.00055598
48 | 0.0040647 | 0.0010187
49 | 0.0035096 | 0.00087959
50 | 0.0021858 | 0.00054782
51 | 0.0021656 | 0.00054275
52 | 0.0013461 | 0.00033736
53 | 0.0013407 | 0.00033602
54 | 0.00047287 | 0.00011851
55 | 0.0019146 | 0.00047985
56 | 0.0043993 | 0.0011026
57 | 0.0040305 | 0.0010101
58 | 0.0041048 | 0.0010287
59 | 0.0036954 | 0.00092616
60 | 0.0017366 | 0.00043524
61 | 0.0038366 | 0.00096154
62 | 0.0023847 | 0.00059767
63 | 0.0060688 | 0.001521

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1