## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1068-10_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1068-10_0_3_node_3 | 0.4 | n |  | TRUE
2 | bus_LV_1068-10_0_3_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_1068-10_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1068-10_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1068-10_0_3_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1068-10_0_3_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1068-10_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1068-10_0_3_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1068-10_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_1068-10_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1068-10_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1068-10_0_3_node_32 | 0.4 | n |  | TRUE
13 | bus_LV_1068-10_0_3_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1068-10_0_3_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_1068-10_0_3_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_1068-10_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1068-10_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1068-10_0_3_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1068-10_0_3_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_1068-10_0_3_node_31 | 0.4 | n |  | TRUE
21 | bus_LV_1068-10_0_3_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_1068-10_0_3_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1068-10_0_3_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_1068-10_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1068-10_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1068-10_0_3_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1068-10_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1068-10_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1068-10_0_3_node_26 | 0.4 | n |  | TRUE
30 | bus_LV_1068-10_0_3_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_1068-10_0_3_node_57 | 0.4 | n |  | TRUE
32 | bus_LV_1068-10_0_3_node_58 | 0.4 | n |  | TRUE
33 | bus_LV_1068-10_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1068-10_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1068-10_0_3_node_27 | 0.4 | n |  | TRUE
36 | bus_LV_1068-10_0_3_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_1068-10_0_3_node_66 | 0.4 | n |  | TRUE
38 | bus_LV_1068-10_0_3_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_1068-10_0_3_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_1068-10_0_3_node_64 | 0.4 | n |  | TRUE
41 | bus_LV_1068-10_0_3_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_1068-10_0_3_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_1068-10_0_3_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_1068-10_0_3_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_1068-10_0_3_node_68 | 0.4 | n |  | TRUE
46 | bus_LV_1068-10_0_3_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_1068-10_0_3_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_1068-10_0_3_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1068-10_0_3_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_1068-10_0_3_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_1068-10_0_3_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_1068-10_0_3_node_71 | 0.4 | n |  | TRUE
53 | bus_LV_1068-10_0_3_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_1068-10_0_3_node_70 | 0.4 | n |  | TRUE
55 | bus_LV_1068-10_0_3_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_1068-10_0_3_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_1068-10_0_3_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_1068-10_0_3_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_1068-10_0_3_node_49 | 0.4 | n |  | TRUE
60 | bus_LV_1068-10_0_3_node_50 | 0.4 | n |  | TRUE
61 | bus_LV_1068-10_0_3_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_1068-10_0_3_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_1068-10_0_3_node_52 | 0.4 | n |  | TRUE
64 | bus_LV_1068-10_0_3_node_79 | 0.4 | n |  | TRUE
65 | bus_LV_1068-10_0_3_node_80 | 0.4 | n |  | TRUE
66 | bus_LV_1068-10_0_3_node_78 | 0.4 | n |  | TRUE
67 | bus_LV_1068-10_0_3_node_77 | 0.4 | n |  | TRUE
68 | bus_LV_1068-10_0_3_node_59 | 0.4 | n |  | TRUE
69 | bus_LV_1068-10_0_3_node_72 | 0.4 | n |  | TRUE
70 | bus_LV_1068-10_0_3_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_1068-10_0_3_node_73 | 0.4 | n |  | TRUE
72 | bus_LV_1068-10_0_3_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_1068-10_0_3_node_61 | 0.4 | n |  | TRUE
74 | bus_LV_1068-10_0_3_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_1068-10_0_3_node_67 | 0.4 | n |  | TRUE
76 | bus_LV_1068-10_0_3_node_65 | 0.4 | n |  | TRUE
77 | bus_LV_1068-10_0_3_node_74 | 0.4 | n |  | TRUE
78 | bus_LV_1068-10_0_3_node_75 | 0.4 | n |  | TRUE
79 | bus_LV_1068-10_0_3_node_76 | 0.4 | n |  | TRUE
80 | bus_MV_127_0_node_0 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1068-10_0_3_load_0 | 0 | 0.0021278 | 0.00053327 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1068-10_0_3_load_1 | 2 | 0.0024793 | 0.00062137 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1068-10_0_3_load_2 | 3 | 0.0027149 | 0.00068042 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1068-10_0_3_load_9 | 5 | 0.0024604 | 0.00061662 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1068-10_0_3_load_7 | 6 | 0.002444 | 0.00061253 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1068-10_0_3_load_6 | 7 | 0.0039903 | 0.0010001 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1068-10_0_3_load_10 | 8 | 0.0095741 | 0.0023995 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1068-10_0_3_load_11 | 9 | 0.0025331 | 0.00063484 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1068-10_0_3_load_8 | 10 | 0.0025147 | 0.00063025 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1068-10_0_3_load_5 | 11 | 0.0015781 | 0.00039551 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1068-10_0_3_load_12 | 13 | 0.0080376 | 0.0020144 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1068-10_0_3_load_33 | 14 | 0.0014969 | 0.00037516 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1068-10_0_3_load_34 | 15 | 0.0021905 | 0.00054899 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1068-10_0_3_load_13 | 16 | 0.0079385 | 0.0019896 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1068-10_0_3_load_14 | 17 | 0.0026928 | 0.00067488 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1068-10_0_3_load_15 | 18 | 0.0038942 | 0.00097597 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1068-10_0_3_load_28 | 21 | 0.0064003 | 0.0016041 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1068-10_0_3_load_16 | 22 | 0.0020472 | 0.00051309 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1068-10_0_3_load_17 | 23 | 0.0040577 | 0.001017 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1068-10_0_3_load_18 | 24 | 0.0052401 | 0.0013133 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1068-10_0_3_load_19 | 25 | 0.0018825 | 0.00047181 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1068-10_0_3_load_24 | 30 | 0.0026979 | 0.00067615 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1068-10_0_3_load_57 | 31 | 0.0022188 | 0.00055607 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1068-10_0_3_load_23 | 33 | 0.0036262 | 0.00090881 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1068-10_0_3_load_25 | 34 | 0.0012202 | 0.00030581 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1068-10_0_3_load_27 | 35 | 0.0021828 | 0.00054706 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1068-10_0_3_load_29 | 36 | 0.0028751 | 0.00072057 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1068-10_0_3_load_66 | 37 | 0.0021424 | 0.00053693 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1068-10_0_3_load_40 | 38 | 0.0022549 | 0.00056513 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1068-10_0_3_load_64 | 40 | 0.0030041 | 0.00075289 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1068-10_0_3_load_35 | 41 | 0.0036769 | 0.00092152 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1068-10_0_3_load_37 | 42 | 0.00089487 | 0.00022428 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1068-10_0_3_load_36 | 43 | 0.025424 | 0.0063718 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1068-10_0_3_load_68 | 45 | 0.0037908 | 0.00095007 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1068-10_0_3_load_44 | 46 | 0.0016773 | 0.00042036 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1068-10_0_3_load_41 | 49 | 0.015867 | 0.0039766 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1068-10_0_3_load_42 | 50 | 0.0020441 | 0.0005123 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1068-10_0_3_load_71 | 52 | 0.0078224 | 0.0019605 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1068-10_0_3_load_70 | 54 | 0.00084819 | 0.00021258 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1068-10_0_3_load_56 | 55 | 0.0041055 | 0.0010289 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1068-10_0_3_load_47 | 57 | 0.001649 | 0.00041327 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1068-10_0_3_load_48 | 58 | 0.0043325 | 0.0010858 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1068-10_0_3_load_51 | 61 | 0.0014728 | 0.00036912 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1068-10_0_3_load_52 | 63 | 0.0036464 | 0.00091386 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1068-10_0_3_load_79 | 64 | 0.0014914 | 0.00037378 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1068-10_0_3_load_80 | 65 | 0.0030452 | 0.00076321 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1068-10_0_3_load_78 | 66 | 0.0064236 | 0.0016099 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1068-10_0_3_load_62 | 70 | 0.0074555 | 0.0018685 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1068-10_0_3_load_73 | 71 | 0.0035507 | 0.00088989 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1068-10_0_3_load_60 | 72 | 0.0030888 | 0.00077413 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1068-10_0_3_load_61 | 73 | 0.0061867 | 0.0015505 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1068-10_0_3_load_67 | 75 | 0.0057666 | 0.0014453 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1068-10_0_3_load_65 | 76 | 0.0013454 | 0.00033718 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1068-10_0_3_load_74 | 77 | 0.0040658 | 0.001019 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1068-10_0_3_load_75 | 78 | 0.0071178 | 0.0017839 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 38 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1068-10_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.024174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1068-10_0_3_line_1 | NAYY 4x150 SE | 1 | 4 | 0.028468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1068-10_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.023558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1068-10_0_3_line_3 | NAYY 4x150 SE | 3 | 5 | 0.029741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1068-10_0_3_line_4 | NAYY 4x150 SE | 4 | 9 | 0.018024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1068-10_0_3_line_5 | NAYY 4x150 SE | 4 | 10 | 0.021953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1068-10_0_3_line_6 | NAYY 4x150 SE | 5 | 8 | 0.023736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1068-10_0_3_line_7 | NAYY 4x150 SE | 5 | 6 | 0.013934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1068-10_0_3_line_8 | NAYY 4x150 SE | 6 | 7 | 0.010825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1068-10_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.0044026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1068-10_0_3_line_10 | NAYY 4x150 SE | 9 | 13 | 0.060542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1068-10_0_3_line_11 | NAYY 4x150 SE | 11 | 12 | 0.013049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1068-10_0_3_line_12 | NAYY 4x150 SE | 12 | 14 | 0.0032578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1068-10_0_3_line_13 | NAYY 4x150 SE | 12 | 15 | 0.032948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1068-10_0_3_line_14 | NAYY 4x150 SE | 13 | 16 | 0.021541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1068-10_0_3_line_15 | NAYY 4x150 SE | 14 | 41 | 0.039612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1068-10_0_3_line_16 | NAYY 4x150 SE | 15 | 42 | 0.005813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1068-10_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.038962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1068-10_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.025818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1068-10_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.016937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1068-10_0_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.018393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1068-10_0_3_line_21 | NAYY 4x150 SE | 19 | 21 | 0.017103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1068-10_0_3_line_22 | NAYY 4x150 SE | 20 | 37 | 0.016716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1068-10_0_3_line_23 | NAYY 4x150 SE | 21 | 29 | 0.008201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1068-10_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.0014975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1068-10_0_3_line_25 | NAYY 4x150 SE | 22 | 24 | 0.017113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1068-10_0_3_line_26 | NAYY 4x150 SE | 23 | 25 | 0.0053313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1068-10_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.03339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1068-10_0_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.026361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1068-10_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.080392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1068-10_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.017533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1068-10_0_3_line_31 | NAYY 4x150 SE | 29 | 30 | 0.011895 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1068-10_0_3_line_32 | NAYY 4x150 SE | 30 | 33 | 0.019658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1068-10_0_3_line_33 | NAYY 4x150 SE | 31 | 32 | 0.030259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1068-10_0_3_line_34 | NAYY 4x150 SE | 32 | 68 | 0.013235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1068-10_0_3_line_35 | NAYY 4x150 SE | 33 | 34 | 0.0056459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1068-10_0_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.021733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1068-10_0_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.0053979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1068-10_0_3_line_38 | NAYY 4x150 SE | 37 | 40 | 0.022671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1068-10_0_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.015456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1068-10_0_3_line_40 | NAYY 4x150 SE | 39 | 44 | 0.002974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1068-10_0_3_line_41 | NAYY 4x150 SE | 39 | 42 | 0.011859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1068-10_0_3_line_42 | NAYY 4x150 SE | 40 | 76 | 0.0090752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1068-10_0_3_line_43 | NAYY 4x150 SE | 41 | 43 | 0.040032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1068-10_0_3_line_44 | NAYY 4x150 SE | 44 | 45 | 0.033436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1068-10_0_3_line_45 | NAYY 4x150 SE | 44 | 46 | 0.019151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1068-10_0_3_line_46 | NAYY 4x150 SE | 45 | 47 | 0.019875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1068-10_0_3_line_47 | NAYY 4x150 SE | 46 | 48 | 0.0059018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1068-10_0_3_line_48 | NAYY 4x150 SE | 47 | 54 | 0.033941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1068-10_0_3_line_49 | NAYY 4x150 SE | 47 | 75 | 0.014207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1068-10_0_3_line_50 | NAYY 4x150 SE | 48 | 49 | 0.029162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1068-10_0_3_line_51 | NAYY 4x150 SE | 49 | 50 | 0.048351 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1068-10_0_3_line_52 | NAYY 4x150 SE | 51 | 52 | 0.032874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1068-10_0_3_line_53 | NAYY 4x150 SE | 51 | 53 | 0.014658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1068-10_0_3_line_54 | NAYY 4x150 SE | 51 | 54 | 0.011613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1068-10_0_3_line_55 | NAYY 4x150 SE | 53 | 55 | 0.0070476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1068-10_0_3_line_56 | NAYY 4x150 SE | 55 | 56 | 0.030314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1068-10_0_3_line_57 | NAYY 4x150 SE | 56 | 63 | 0.026089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1068-10_0_3_line_58 | NAYY 4x150 SE | 57 | 58 | 0.015752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1068-10_0_3_line_59 | NAYY 4x150 SE | 57 | 59 | 0.0036308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1068-10_0_3_line_60 | NAYY 4x150 SE | 58 | 60 | 0.045661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1068-10_0_3_line_61 | NAYY 4x150 SE | 59 | 61 | 0.009683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1068-10_0_3_line_62 | NAYY 4x150 SE | 60 | 62 | 0.010896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1068-10_0_3_line_63 | NAYY 4x150 SE | 60 | 63 | 0.0049937 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1068-10_0_3_line_64 | NAYY 4x150 SE | 62 | 64 | 0.007329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1068-10_0_3_line_65 | NAYY 4x150 SE | 62 | 65 | 0.013898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1068-10_0_3_line_66 | NAYY 4x150 SE | 66 | 67 | 0.023425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1068-10_0_3_line_67 | NAYY 4x150 SE | 67 | 79 | 0.035712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1068-10_0_3_line_68 | NAYY 4x150 SE | 68 | 69 | 0.06008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1068-10_0_3_line_69 | NAYY 4x150 SE | 68 | 70 | 0.015787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1068-10_0_3_line_70 | NAYY 4x150 SE | 69 | 71 | 0.012939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1068-10_0_3_line_71 | NAYY 4x150 SE | 70 | 72 | 0.0087393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1068-10_0_3_line_72 | NAYY 4x150 SE | 71 | 77 | 0.0085012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1068-10_0_3_line_73 | NAYY 4x150 SE | 72 | 73 | 0.019102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1068-10_0_3_line_74 | NAYY 4x150 SE | 73 | 74 | 0.026501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1068-10_0_3_line_75 | NAYY 4x150 SE | 74 | 75 | 0.0031001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
76 | LV_1068-10_0_3_line_76 | NAYY 4x150 SE | 74 | 76 | 0.01664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
77 | LV_1068-10_0_3_line_77 | NAYY 4x150 SE | 77 | 78 | 0.035884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1068-10_0_3_line_78 | NAYY 4x150 SE | 78 | 79 | 0.0079022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1068-10_0_3_trafo_40 | 0.25 MVA 20/0.4 kV | 80 | 38 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2679773.2021 | 1207142.5264 | 2679772.2749 | 1207166.6828
1 | 2679747.7548 | 1207132.9693 | 2679751.4616 | 1207136.7101 | 2679762.4238 | 1207142.6937 | 2679773.2021 | 1207142.5264
2 | 2679738.541 | 1207178.4522 | 2679734.9086 | 1207182.029 | 2679718.8379 | 1207191.1118
3 | 2679709.9129 | 1207162.7414 | 2679718.8379 | 1207191.1118
4 | 2679747.7548 | 1207132.9693 | 2679744.6465 | 1207119.1523 | 2679742.3652 | 1207116.0365
5 | 2679747.7548 | 1207132.9693 | 2679745.7312 | 1207136.4334 | 2679738.7033 | 1207137.6514 | 2679732.7714 | 1207138.2281 | 2679728.6144 | 1207140.7236
6 | 2679691.4673 | 1207177.6796 | 2679709.9129 | 1207162.7414
7 | 2679709.9129 | 1207162.7414 | 2679716.9529 | 1207157.04 | 2679719.742 | 1207153.0417
8 | 2679725.9355 | 1207144.163 | 2679719.742 | 1207153.0417
9 | 2679725.9355 | 1207144.163 | 2679728.1332 | 1207141.0124 | 2679728.6144 | 1207140.7236
10 | 2679687.3796 | 1207117.2133 | 2679692.7413 | 1207114.7454 | 2679700.4278 | 1207113.7585 | 2679708.7497 | 1207114.7369 | 2679729.0076 | 1207108.0142 | 2679736.8942 | 1207108.5643 | 2679742.3652 | 1207116.0365
11 | 2679736.4832 | 1207057.9377 | 2679738.4546 | 1207070.8366
12 | 2679736.4832 | 1207057.9377 | 2679738.6093 | 1207060.4061
13 | 2679736.4832 | 1207057.9377 | 2679720.0395 | 1207029.3861
14 | 2679687.3796 | 1207117.2133 | 2679667.8114 | 1207126.22 | 2679667.8114 | 1207126.22
15 | 2679764.4616 | 1207090.4195 | 2679738.6093 | 1207060.4061
16 | 2679720.0395 | 1207029.3861 | 2679717.1384 | 1207024.3488
17 | 2679667.8114 | 1207126.22 | 2679659.9715 | 1207122.1795 | 2679657.8481 | 1207113.1899 | 2679652.1604 | 1207093.0735
18 | 2679652.1604 | 1207093.0735 | 2679645.1361 | 1207068.2291
19 | 2679640.528 | 1207051.931 | 2679645.1361 | 1207068.2291
20 | 2679655.8219 | 1207041.6507 | 2679640.528 | 1207051.931
21 | 2679640.528 | 1207051.931 | 2679629.8103 | 1207055.5237 | 2679624.0437 | 1207056.1375
22 | 2679655.8219 | 1207041.6507 | 2679650.2049 | 1207025.9064
23 | 2679615.8887 | 1207057.0056 | 2679624.0437 | 1207056.1375
24 | 2679615.5244 | 1207135.6063 | 2679615.5244 | 1207135.6063 | 2679614.1216 | 1207136.1304
25 | 2679615.5244 | 1207135.6063 | 2679611.9579 | 1207120.2045 | 2679610.6579 | 1207120.2982
26 | 2679614.1216 | 1207136.1304 | 2679609.1274 | 1207137.9962
27 | 2679577.5404 | 1207147.9856 | 2679582.4229 | 1207147.9729 | 2679609.1274 | 1207137.9962
28 | 2679577.5404 | 1207147.9856 | 2679576.0662 | 1207121.6714
29 | 2679576.0662 | 1207121.6714 | 2679575.0305 | 1207076.729 | 2679574.3673 | 1207073.4181 | 2679572.6538 | 1207069.0369 | 2679581.7111 | 1207066.2003 | 2679598.6837 | 1207060.623
30 | 2679615.8887 | 1207057.0056 | 2679598.6837 | 1207060.623
31 | 2679615.8887 | 1207057.0056 | 2679617.9758 | 1207068.7161
32 | 2679621.425 | 1207088.0696 | 2679617.9758 | 1207068.7161
33 | 2679589.9495 | 1206986.7818 | 2679590.9172 | 1207017.0251
34 | 2679589.9495 | 1206986.7818 | 2679589.5251 | 1206973.5566
35 | 2679621.425 | 1207088.0696 | 2679622.4156 | 1207093.6279
36 | 2679626.7199 | 1207114.9253 | 2679624.1455 | 1207103.3341 | 2679622.4156 | 1207093.6279
37 | 2679627.8902 | 1207120.1948 | 2679626.7199 | 1207114.9253
38 | 2679649.0095 | 1207003.4959 | 2679648.4481 | 1207019.2047 | 2679649.0704 | 1207022.7263 | 2679650.2049 | 1207025.9064
39 | 2679711.2199 | 1207014.0724 | 2679697.262 | 1207020.7109
40 | 2679713.0988 | 1207011.7627 | 2679711.2199 | 1207014.0724
41 | 2679711.2199 | 1207014.0724 | 2679717.1384 | 1207024.3488
42 | 2679649.0095 | 1207003.4959 | 2679649.1765 | 1206998.8237 | 2679649.887 | 1206994.4814
43 | 2679794.0382 | 1207115.8879 | 2679787.7748 | 1207113.9585 | 2679782.1343 | 1207110.9368 | 2679764.4616 | 1207090.4195
44 | 2679713.0988 | 1207011.7627 | 2679689.069 | 1206988.5139
45 | 2679713.0988 | 1207011.7627 | 2679721.9565 | 1207003.9538 | 2679725.0641 | 1206997.3015
46 | 2679674.7854 | 1206974.6944 | 2679689.069 | 1206988.5139
47 | 2679727.562 | 1206991.9543 | 2679725.0641 | 1206997.3015
48 | 2679674.7854 | 1206974.6944 | 2679694.2097 | 1206963.8023 | 2679705.0406 | 1206959.4551
49 | 2679674.7854 | 1206974.6944 | 2679665.2686 | 1206980.0375 | 2679662.0472 | 1206980.7218
50 | 2679727.562 | 1206991.9543 | 2679755.2991 | 1206982.9497
51 | 2679755.2991 | 1206982.9497 | 2679775.2243 | 1206976.4811 | 2679780.9508 | 1206976.491 | 2679788.1412 | 1206980.7675 | 2679798.9001 | 1206988.6025
52 | 2679715.8175 | 1206955.1296 | 2679714.5532 | 1206936.4787 | 2679715.6656 | 1206922.3426
53 | 2679715.8175 | 1206955.1296 | 2679730.3639 | 1206953.0114
54 | 2679715.8175 | 1206955.1296 | 2679705.0406 | 1206959.4551
55 | 2679730.3639 | 1206953.0114 | 2679734.7715 | 1206947.5122
56 | 2679756.9211 | 1206927.3831 | 2679746.0402 | 1206934.0643 | 2679736.5356 | 1206945.3112 | 2679734.7715 | 1206947.5122
57 | 2679756.9211 | 1206927.3831 | 2679770.6809 | 1206926.0883 | 2679782.8543 | 1206927.6102
58 | 2679846.3463 | 1206919.3315 | 2679841.42 | 1206924.0992 | 2679833.2432 | 1206927.6032
59 | 2679848.9554 | 1206916.8064 | 2679846.3463 | 1206919.3315
60 | 2679787.8094 | 1206928.2297 | 2679819.6835 | 1206929.8567 | 2679833.2432 | 1206927.6032
61 | 2679848.9554 | 1206916.8064 | 2679843.718 | 1206908.6534
62 | 2679789.9752 | 1206917.5518 | 2679787.8094 | 1206928.2297
63 | 2679787.8094 | 1206928.2297 | 2679782.8543 | 1206927.6102
64 | 2679789.9752 | 1206917.5518 | 2679789.2513 | 1206910.2597
65 | 2679789.9752 | 1206917.5518 | 2679799.1349 | 1206907.0787
66 | 2679643.3031 | 1206824.6345 | 2679663.5943 | 1206836.3386
67 | 2679643.3031 | 1206824.6345 | 2679638.8536 | 1206837.2054 | 2679629.1237 | 1206857.3662
68 | 2679596.912 | 1206914.0839 | 2679590.4416 | 1206949.8871 | 2679589.5251 | 1206973.5566
69 | 2679589.5251 | 1206973.5566 | 2679605.2897 | 1206974.3876
70 | 2679596.912 | 1206914.0839 | 2679603.3018 | 1206902.8328
71 | 2679614.0169 | 1206974.8476 | 2679605.2897 | 1206974.3876
72 | 2679603.3018 | 1206902.8328 | 2679607.5001 | 1206895.4405
73 | 2679614.0169 | 1206974.8476 | 2679628.4964 | 1206975.6109 | 2679632.9907 | 1206976.6024
74 | 2679659.0147 | 1206981.366 | 2679651.6692 | 1206980.7232 | 2679632.9907 | 1206976.6024
75 | 2679659.0147 | 1206981.366 | 2679662.0472 | 1206980.7218
76 | 2679659.0147 | 1206981.366 | 2679658.7728 | 1206983.5308 | 2679651.428 | 1206990.2482 | 2679649.9135 | 1206994.3195 | 2679649.887 | 1206994.4814
77 | 2679607.5001 | 1206895.4405 | 2679625.2212 | 1206864.2376
78 | 2679629.1237 | 1206857.3662 | 2679625.2212 | 1206864.2376

## bus_geodata
| x | y | coords
0 | 2679772.2749 | 1207166.6828
1 | 2679773.2021 | 1207142.5264
2 | 2679738.541 | 1207178.4522
3 | 2679718.8379 | 1207191.1118
4 | 2679747.7548 | 1207132.9693
5 | 2679709.9129 | 1207162.7414
6 | 2679719.742 | 1207153.0417
7 | 2679725.9355 | 1207144.163
8 | 2679691.4673 | 1207177.6796
9 | 2679742.3652 | 1207116.0365
10 | 2679728.6144 | 1207140.7236
11 | 2679738.4546 | 1207070.8366
12 | 2679736.4832 | 1207057.9377
13 | 2679687.3796 | 1207117.2133
14 | 2679738.6093 | 1207060.4061
15 | 2679720.0395 | 1207029.3861
16 | 2679667.8114 | 1207126.22
17 | 2679652.1604 | 1207093.0735
18 | 2679645.1361 | 1207068.2291
19 | 2679640.528 | 1207051.931
20 | 2679655.8219 | 1207041.6507
21 | 2679624.0437 | 1207056.1375
22 | 2679615.5244 | 1207135.6063
23 | 2679614.1216 | 1207136.1304
24 | 2679610.6579 | 1207120.2982
25 | 2679609.1274 | 1207137.9962
26 | 2679577.5404 | 1207147.9856
27 | 2679576.0662 | 1207121.6714
28 | 2679598.6837 | 1207060.623
29 | 2679615.8887 | 1207057.0056
30 | 2679617.9758 | 1207068.7161
31 | 2679590.9172 | 1207017.0251
32 | 2679589.9495 | 1206986.7818
33 | 2679621.425 | 1207088.0696
34 | 2679622.4156 | 1207093.6279
35 | 2679626.7199 | 1207114.9253
36 | 2679627.8902 | 1207120.1947
37 | 2679650.2049 | 1207025.9065
38 | 2679697.262 | 1207020.7109
39 | 2679711.2199 | 1207014.0724
40 | 2679649.0095 | 1207003.4959
41 | 2679764.4616 | 1207090.4195
42 | 2679717.1384 | 1207024.3488
43 | 2679794.0382 | 1207115.8879
44 | 2679713.0988 | 1207011.7627
45 | 2679689.069 | 1206988.5139
46 | 2679725.0641 | 1206997.3015
47 | 2679674.7854 | 1206974.6944
48 | 2679727.562 | 1206991.9543
49 | 2679755.2991 | 1206982.9497
50 | 2679798.9001 | 1206988.6025
51 | 2679715.8175 | 1206955.1296
52 | 2679715.6656 | 1206922.3426
53 | 2679730.3639 | 1206953.0114
54 | 2679705.0406 | 1206959.4551
55 | 2679734.7715 | 1206947.5122
56 | 2679756.9211 | 1206927.3831
57 | 2679846.3463 | 1206919.3315
58 | 2679833.2432 | 1206927.6032
59 | 2679848.9554 | 1206916.8064
60 | 2679787.8094 | 1206928.2297
61 | 2679843.718 | 1206908.6534
62 | 2679789.9752 | 1206917.5518
63 | 2679782.8543 | 1206927.6102
64 | 2679789.2513 | 1206910.2597
65 | 2679799.1349 | 1206907.0787
66 | 2679663.5943 | 1206836.3386
67 | 2679643.3031 | 1206824.6345
68 | 2679589.5251 | 1206973.5566
69 | 2679596.912 | 1206914.0839
70 | 2679605.2897 | 1206974.3876
71 | 2679603.3018 | 1206902.8328
72 | 2679614.0169 | 1206974.8476
73 | 2679632.9907 | 1206976.6024
74 | 2679659.0147 | 1206981.366
75 | 2679662.0472 | 1206980.7218
76 | 2679649.887 | 1206994.4814
77 | 2679607.5001 | 1206895.4405
78 | 2679625.2212 | 1206864.2376
79 | 2679629.1237 | 1206857.3662
80 | 2679711.2199 | 1207014.0724

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97208 | -0.19648 | 0.0021278 | 0.00053327
1 | 0.97216 | -0.19594 | 0 | 0
2 | 0.97027 | -0.20953 | 0.0024793 | 0.00062137
3 | 0.97036 | -0.20891 | 0.0027149 | 0.00068042
4 | 0.97225 | -0.1953 | 0 | 0
5 | 0.97059 | -0.20728 | 0.0024604 | 0.00061662
6 | 0.97094 | -0.20473 | 0.002444 | 0.00061253
7 | 0.97125 | -0.20248 | 0.0039903 | 0.0010001
8 | 0.97025 | -0.20969 | 0.0095741 | 0.0023995
9 | 0.973 | -0.18991 | 0.0025331 | 0.00063484
10 | 0.9714 | -0.20138 | 0.0025147 | 0.00063025
11 | 0.99589 | -0.028658 | 0.0015781 | 0.00039551
12 | 0.99591 | -0.028451 | 0 | 0
13 | 0.97574 | -0.17027 | 0.0080376 | 0.0020144
14 | 0.99577 | -0.029454 | 0.0014969 | 0.00037516
15 | 0.99744 | -0.017796 | 0.0021905 | 0.00054899
16 | 0.97697 | -0.1615 | 0.0079385 | 0.0019896
17 | 0.97964 | -0.14247 | 0.0026928 | 0.00067488
18 | 0.98151 | -0.12919 | 0.0038942 | 0.00097597
19 | 0.98284 | -0.11983 | 0 | 0
20 | 0.98514 | -0.10358 | 0 | 0
21 | 0.98203 | -0.12553 | 0.0064003 | 0.0016041
22 | 0.97858 | -0.15015 | 0.0020472 | 0.00051309
23 | 0.9786 | -0.15004 | 0.0040577 | 0.001017
24 | 0.97845 | -0.15109 | 0.0052401 | 0.0013133
25 | 0.97869 | -0.14941 | 0.0018825 | 0.00047181
26 | 0.97933 | -0.14481 | 0 | 0
27 | 0.97984 | -0.14118 | 0 | 0
28 | 0.98139 | -0.13014 | 0 | 0
29 | 0.98173 | -0.12773 | 0 | 0
30 | 0.98151 | -0.12928 | 0.0026979 | 0.00067615
31 | 0.98892 | -0.077279 | 0.0022188 | 0.00055607
32 | 0.98902 | -0.076593 | 0 | 0
33 | 0.98123 | -0.1313 | 0.0036262 | 0.00090881
34 | 0.98117 | -0.13167 | 0.0012202 | 0.00030581
35 | 0.98101 | -0.13281 | 0.0021828 | 0.00054706
36 | 0.98099 | -0.13297 | 0.0028751 | 0.00072057
37 | 0.98723 | -0.088884 | 0.0021424 | 0.00053693
38 | 1 | 0 | -0.22903 | -0.057603
39 | 0.99832 | -0.0116 | 0 | 0
40 | 0.99013 | -0.068552 | 0.0030041 | 0.00075289
41 | 0.99412 | -0.041078 | 0.0036769 | 0.00092152
42 | 0.99772 | -0.015792 | 0.00089487 | 0.00022428
43 | 0.99266 | -0.051372 | 0.025424 | 0.0063718
44 | 0.99805 | -0.013486 | 0 | 0
45 | 0.9953 | -0.03256 | 0.0037908 | 0.00095007
46 | 0.99751 | -0.017249 | 0.0016773 | 0.00042036
47 | 0.9937 | -0.043694 | 0 | 0
48 | 0.99736 | -0.018309 | 0 | 0
49 | 0.99662 | -0.023556 | 0.015867 | 0.0039766
50 | 0.99647 | -0.02455 | 0.0020441 | 0.0005123
51 | 0.99185 | -0.056711 | 0 | 0
52 | 0.99148 | -0.059322 | 0.0078224 | 0.0019605
53 | 0.99143 | -0.059651 | 0 | 0
54 | 0.99231 | -0.053463 | 0.00084819 | 0.00021258
55 | 0.99123 | -0.061065 | 0.0041055 | 0.0010289
56 | 0.99055 | -0.065888 | 0 | 0
57 | 0.98932 | -0.074626 | 0.001649 | 0.00041327
58 | 0.98939 | -0.074125 | 0.0043325 | 0.0010858
59 | 0.98931 | -0.074681 | 0 | 0
60 | 0.98988 | -0.070654 | 0 | 0
61 | 0.98929 | -0.074826 | 0.0014728 | 0.00036912
62 | 0.98981 | -0.071158 | 0 | 0
63 | 0.98996 | -0.070043 | 0.0036464 | 0.00091386
64 | 0.98979 | -0.071269 | 0.0014914 | 0.00037378
65 | 0.98975 | -0.071589 | 0.0030452 | 0.00076321
66 | 0.98528 | -0.10305 | 0.0064236 | 0.0016099
67 | 0.9855 | -0.1015 | 0 | 0
68 | 0.98906 | -0.076293 | 0 | 0
69 | 0.98722 | -0.089295 | 0 | 0
70 | 0.98959 | -0.072526 | 0.0074555 | 0.0018685
71 | 0.98683 | -0.092101 | 0.0035507 | 0.00088989
72 | 0.98998 | -0.069779 | 0.0030888 | 0.00077413
73 | 0.99092 | -0.063182 | 0.0061867 | 0.0015505
74 | 0.99245 | -0.052388 | 0 | 0
75 | 0.99275 | -0.05031 | 0.0057666 | 0.0014453
76 | 0.99133 | -0.060169 | 0.0013454 | 0.00033718
77 | 0.98661 | -0.093636 | 0.0040658 | 0.001019
78 | 0.98591 | -0.098625 | 0.0071178 | 0.0017839
79 | 0.98583 | -0.099147 | 0 | 0
80 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0021278 | -0.00053327 | 0.0021279 | 0.00053303 | 1.6002e-07 | -2.3817e-07 | 0.0032571 | 0.003257 | 0.0032571 | 0.97208 | -0.19648 | 0.97216 | -0.19594 | 1.2063
1 | -0.0021279 | -0.00053303 | 0.0021281 | 0.00053275 | 1.8843e-07 | -2.8053e-07 | 0.003257 | 0.0032568 | 0.003257 | 0.97216 | -0.19594 | 0.97225 | -0.1953 | 1.2063
2 | -0.0024793 | -0.00062137 | 0.0024795 | 0.00062116 | 2.1251e-07 | -2.0925e-07 | 0.0038023 | 0.0038022 | 0.0038023 | 0.97027 | -0.20953 | 0.97036 | -0.20891 | 1.4082
3 | -0.0051944 | -0.0013016 | 0.0051956 | 0.0013017 | 1.1775e-06 | 8.5395e-08 | 0.0079654 | 0.0079653 | 0.0079654 | 0.97036 | -0.20891 | 0.97059 | -0.20728 | 2.9502
4 | -0.028348 | -0.0071082 | 0.028369 | 0.0071162 | 2.1173e-05 | 7.9196e-06 | 0.043388 | 0.043388 | 0.043388 | 0.97225 | -0.1953 | 0.973 | -0.18991 | 16.0696
5 | 0.02622 | 0.0065755 | -0.026198 | -0.0065673 | 2.2062e-05 | 8.2133e-06 | 0.040131 | 0.040131 | 0.040131 | 0.97225 | -0.1953 | 0.9714 | -0.20138 | 14.8634
6 | 0.0095773 | 0.0024004 | -0.0095741 | -0.0023995 | 3.1932e-06 | 9.349e-07 | 0.014683 | 0.014683 | 0.014683 | 0.97059 | -0.20728 | 0.97025 | -0.20969 | 5.4382
7 | -0.017233 | -0.0043187 | 0.017239 | 0.0043209 | 6.0693e-06 | 2.1621e-06 | 0.02642 | 0.02642 | 0.02642 | 0.97059 | -0.20728 | 0.97094 | -0.20473 | 9.7853
8 | -0.019683 | -0.0049334 | 0.01969 | 0.0049356 | 6.147e-06 | 2.2303e-06 | 0.030166 | 0.030166 | 0.030166 | 0.97094 | -0.20473 | 0.97125 | -0.20248 | 11.1726
9 | -0.02368 | -0.0059357 | 0.023683 | 0.005937 | 3.6158e-06 | 1.3362e-06 | 0.036279 | 0.036279 | 0.036279 | 0.97125 | -0.20248 | 0.9714 | -0.20138 | 13.4367
10 | -0.030902 | -0.007751 | 0.030987 | 0.0077827 | 8.4384e-05 | 3.1701e-05 | 0.047262 | 0.047261 | 0.047262 | 0.973 | -0.18991 | 0.97574 | -0.17027 | 17.5043
11 | -0.0015781 | -0.00039551 | 0.0015781 | 0.00039535 | 4.5269e-08 | -1.5238e-07 | 0.0023579 | 0.0023579 | 0.0023579 | 0.99589 | -0.028658 | 0.99591 | -0.028451 | 0.8733
12 | 0.030685 | 0.007701 | -0.030681 | -0.0076994 | 4.2737e-06 | 1.6014e-06 | 0.045851 | 0.045851 | 0.045851 | 0.99591 | -0.028451 | 0.99577 | -0.029454 | 16.9818
13 | -0.032263 | -0.0080964 | 0.032311 | 0.0081143 | 4.7782e-05 | 1.7948e-05 | 0.048209 | 0.048209 | 0.048209 | 0.99591 | -0.028451 | 0.99744 | -0.017796 | 17.8551
14 | -0.039024 | -0.0097971 | 0.039072 | 0.0098152 | 4.7618e-05 | 1.8045e-05 | 0.059519 | 0.059519 | 0.059519 | 0.97574 | -0.17027 | 0.97697 | -0.1615 | 22.044
15 | 0.029184 | 0.0073243 | -0.029137 | -0.0073067 | 4.7019e-05 | 1.757e-05 | 0.043614 | 0.043614 | 0.043614 | 0.99577 | -0.029454 | 0.99412 | -0.041078 | 16.1534
16 | -0.034501 | -0.0086633 | 0.034511 | 0.008667 | 9.6116e-06 | 3.6209e-06 | 0.051476 | 0.051476 | 0.051476 | 0.99744 | -0.017796 | 0.99772 | -0.015792 | 19.0653
17 | -0.047011 | -0.011805 | 0.047135 | 0.011852 | 0.00012467 | 4.7462e-05 | 0.07161 | 0.07161 | 0.07161 | 0.97697 | -0.1615 | 0.97964 | -0.14247 | 26.5222
18 | -0.049828 | -0.012527 | 0.04992 | 0.012562 | 9.2322e-05 | 3.5183e-05 | 0.0757 | 0.0757 | 0.0757 | 0.97964 | -0.14247 | 0.98151 | -0.12919 | 28.037
19 | -0.053815 | -0.013538 | 0.053885 | 0.013565 | 7.0379e-05 | 2.6854e-05 | 0.081604 | 0.081604 | 0.081604 | 0.98151 | -0.12919 | 0.98284 | -0.11983 | 30.2236
20 | -0.086197 | -0.021671 | 0.086392 | 0.021746 | 0.00019554 | 7.4974e-05 | 0.13053 | 0.13053 | 0.13053 | 0.98284 | -0.11983 | 0.98514 | -0.10358 | 48.3431
21 | 0.032312 | 0.0081056 | -0.032286 | -0.008096 | 2.5543e-05 | 9.6078e-06 | 0.048923 | 0.048923 | 0.048923 | 0.98284 | -0.11983 | 0.98203 | -0.12553 | 18.1195
22 | -0.086392 | -0.021746 | 0.08657 | 0.021814 | 0.00017771 | 6.8138e-05 | 0.13053 | 0.13053 | 0.13053 | 0.98514 | -0.10358 | 0.98723 | -0.088884 | 48.343
23 | 0.025886 | 0.0064919 | -0.025878 | -0.006489 | 7.8737e-06 | 2.9246e-06 | 0.039225 | 0.039225 | 0.039225 | 0.98203 | -0.12553 | 0.98173 | -0.12773 | 14.5277
24 | -0.007288 | -0.0018264 | 0.0072881 | 0.0018264 | 1.1476e-07 | 2.5323e-08 | 0.011082 | 0.011082 | 0.011082 | 0.97858 | -0.15015 | 0.9786 | -0.15004 | 4.1044
25 | 0.0052408 | 0.0013133 | -0.0052401 | -0.0013133 | 6.7813e-07 | 4.5853e-08 | 0.007969 | 0.007969 | 0.007969 | 0.97858 | -0.15015 | 0.97845 | -0.15109 | 2.9515
26 | -0.011346 | -0.0028434 | 0.011347 | 0.0028437 | 9.9014e-07 | 3.1383e-07 | 0.017252 | 0.017252 | 0.017252 | 0.9786 | -0.15004 | 0.97869 | -0.14941 | 6.3896
27 | -0.013229 | -0.0033155 | 0.013238 | 0.0033184 | 8.4294e-06 | 2.8222e-06 | 0.020114 | 0.020114 | 0.020114 | 0.97869 | -0.14941 | 0.97933 | -0.14481 | 7.4497
28 | -0.013238 | -0.0033184 | 0.013244 | 0.0033206 | 6.6549e-06 | 2.2277e-06 | 0.020114 | 0.020114 | 0.020114 | 0.97933 | -0.14481 | 0.97984 | -0.14118 | 7.4496
29 | -0.013244 | -0.0033206 | 0.013265 | 0.0033274 | 2.0295e-05 | 6.7914e-06 | 0.020114 | 0.020114 | 0.020114 | 0.97984 | -0.14118 | 0.98139 | -0.13014 | 7.4496
30 | -0.013265 | -0.0033274 | 0.013269 | 0.0033289 | 4.426e-06 | 1.4807e-06 | 0.020114 | 0.020113 | 0.020114 | 0.98139 | -0.13014 | 0.98173 | -0.12773 | 7.4495
31 | 0.012609 | 0.0031602 | -0.012606 | -0.0031593 | 2.711e-06 | 8.9234e-07 | 0.019111 | 0.019111 | 0.019111 | 0.98173 | -0.12773 | 0.98151 | -0.12928 | 7.0783
32 | 0.0099083 | 0.0024831 | -0.0099055 | -0.0024823 | 2.7679e-06 | 8.162e-07 | 0.015021 | 0.015021 | 0.015021 | 0.98151 | -0.12928 | 0.98123 | -0.1313 | 5.5635
33 | -0.0022188 | -0.00055607 | 0.002219 | 0.00055577 | 2.1044e-07 | -3.0733e-07 | 0.0033385 | 0.0033384 | 0.0033385 | 0.98892 | -0.077279 | 0.98902 | -0.076593 | 1.2365
34 | -0.002219 | -0.00055577 | 0.0022191 | 0.00055563 | 9.204e-08 | -1.3445e-07 | 0.0033384 | 0.0033383 | 0.0033384 | 0.98902 | -0.076593 | 0.98906 | -0.076293 | 1.2364
35 | 0.0062793 | 0.0015735 | -0.006279 | -0.0015734 | 3.1945e-07 | 5.1555e-08 | 0.0095223 | 0.0095224 | 0.0095224 | 0.98123 | -0.1313 | 0.98117 | -0.13167 | 3.5268
36 | 0.0050588 | 0.0012676 | -0.005058 | -0.0012676 | 7.9819e-07 | 3.2556e-08 | 0.0076719 | 0.007672 | 0.007672 | 0.98117 | -0.13167 | 0.98101 | -0.13281 | 2.8415
37 | 0.0028752 | 0.00072052 | -0.0028751 | -0.00072057 | 6.4061e-08 | -4.3513e-08 | 0.0043611 | 0.0043611 | 0.0043611 | 0.98101 | -0.13281 | 0.98099 | -0.13297 | 1.6152
38 | -0.088712 | -0.022351 | 0.088965 | 0.022448 | 0.0002531 | 9.7054e-05 | 0.13376 | 0.13376 | 0.13376 | 0.98723 | -0.088884 | 0.99013 | -0.068552 | 49.539
39 | 0.22823 | 0.057602 | -0.22786 | -0.05746 | 0.0003711 | 0.00014212 | 0.33975 | 0.33975 | 0.33975 | 1 | 0 | 0.99832 | -0.0116 | 41.9446
40 | 0.19243 | 0.048561 | -0.19238 | -0.048542 | 5.0932e-05 | 1.9472e-05 | 0.28694 | 0.28694 | 0.28694 | 0.99832 | -0.0116 | 0.99805 | -0.013486 | 35.4247
41 | 0.035427 | 0.008899 | -0.035406 | -0.0088912 | 2.0638e-05 | 7.7829e-06 | 0.052811 | 0.052811 | 0.052811 | 0.99832 | -0.0116 | 0.99772 | -0.015792 | 19.5596
42 | -0.091969 | -0.023201 | 0.092078 | 0.023242 | 0.00010827 | 4.1524e-05 | 0.13827 | 0.13827 | 0.13827 | 0.99013 | -0.068552 | 0.99133 | -0.060169 | 51.211
43 | 0.02546 | 0.0063852 | -0.025424 | -0.0063718 | 3.6281e-05 | 1.3436e-05 | 0.03811 | 0.038111 | 0.038111 | 0.99412 | -0.041078 | 0.99266 | -0.051372 | 14.1151
44 | 0.17277 | 0.043624 | -0.1723 | -0.043448 | 0.00046184 | 0.00017632 | 0.2577 | 0.2577 | 0.2577 | 0.99805 | -0.013486 | 0.9953 | -0.03256 | 31.8144
45 | 0.019614 | 0.004918 | -0.019604 | -0.0049143 | 1.022e-05 | 3.6807e-06 | 0.029244 | 0.029244 | 0.029244 | 0.99805 | -0.013486 | 0.99751 | -0.017249 | 10.8312
46 | 0.16851 | 0.042497 | -0.16825 | -0.042397 | 0.00026258 | 0.00010022 | 0.25203 | 0.25203 | 0.25203 | 0.9953 | -0.03256 | 0.9937 | -0.043694 | 31.1147
47 | 0.017927 | 0.004494 | -0.017924 | -0.004493 | 2.6337e-06 | 9.3594e-07 | 0.026742 | 0.026742 | 0.026742 | 0.99751 | -0.017249 | 0.99736 | -0.018309 | 9.9046
48 | 0.028504 | 0.0071524 | -0.028465 | -0.007138 | 3.8591e-05 | 1.4404e-05 | 0.042686 | 0.042687 | 0.042687 | 0.9937 | -0.043694 | 0.99231 | -0.053463 | 15.8098
49 | 0.13975 | 0.035245 | -0.13962 | -0.035196 | 0.00012951 | 4.9259e-05 | 0.20934 | 0.20934 | 0.20934 | 0.9937 | -0.043694 | 0.99275 | -0.05031 | 25.8449
50 | 0.017924 | 0.004493 | -0.017911 | -0.0044884 | 1.3014e-05 | 4.625e-06 | 0.026742 | 0.026743 | 0.026743 | 0.99736 | -0.018309 | 0.99662 | -0.023556 | 9.9046
51 | 0.0020444 | 0.00051178 | -0.0020441 | -0.0005123 | 2.8109e-07 | -5.2184e-07 | 0.0030522 | 0.0030524 | 0.0030524 | 0.99662 | -0.023556 | 0.99647 | -0.02455 | 1.1305
52 | 0.0078252 | 0.0019611 | -0.0078224 | -0.0019605 | 2.8272e-06 | 6.6325e-07 | 0.01174 | 0.01174 | 0.01174 | 0.99185 | -0.056711 | 0.99148 | -0.059322 | 4.3481
53 | 0.01978 | 0.0049597 | -0.019771 | -0.0049568 | 8.0545e-06 | 2.9088e-06 | 0.029675 | 0.029675 | 0.029675 | 0.99185 | -0.056711 | 0.99143 | -0.059651 | 10.9908
54 | -0.027605 | -0.0069208 | 0.027617 | 0.0069255 | 1.2428e-05 | 4.6302e-06 | 0.041415 | 0.041415 | 0.041415 | 0.99185 | -0.056711 | 0.99231 | -0.053463 | 15.3388
55 | 0.019771 | 0.0049568 | -0.019768 | -0.0049554 | 3.8726e-06 | 1.3986e-06 | 0.029675 | 0.029675 | 0.029675 | 0.99143 | -0.059651 | 0.99123 | -0.061065 | 10.9908
56 | 0.015662 | 0.0039264 | -0.015652 | -0.0039228 | 1.0457e-05 | 3.6315e-06 | 0.023512 | 0.023512 | 0.023512 | 0.99123 | -0.061065 | 0.99055 | -0.065888 | 8.7082
57 | 0.015652 | 0.0039228 | -0.015643 | -0.0039197 | 8.9995e-06 | 3.1257e-06 | 0.023512 | 0.023512 | 0.023512 | 0.99055 | -0.065888 | 0.98996 | -0.070043 | 8.7082
58 | -0.0031218 | -0.00078224 | 0.003122 | 0.00078212 | 2.167e-07 | -1.1893e-07 | 0.0046954 | 0.0046954 | 0.0046954 | 0.98932 | -0.074626 | 0.98939 | -0.074125 | 1.739
59 | 0.0014728 | 0.00036896 | -0.0014728 | -0.00036901 | 1.1118e-08 | -4.2345e-08 | 0.0022152 | 0.0022152 | 0.0022152 | 0.98932 | -0.074626 | 0.98931 | -0.074681 | 0.82046
60 | -0.0074545 | -0.0018679 | 0.0074581 | 0.0018687 | 3.5813e-06 | 7.9072e-07 | 0.011211 | 0.011211 | 0.011211 | 0.98939 | -0.074125 | 0.98988 | -0.070654 | 4.1523
61 | 0.0014728 | 0.00036901 | -0.0014728 | -0.00036912 | 2.9651e-08 | -1.1293e-07 | 0.0022152 | 0.0022153 | 0.0022153 | 0.98931 | -0.074681 | 0.98929 | -0.074826 | 0.82048
62 | 0.0045372 | 0.0011368 | -0.0045368 | -0.0011368 | 3.1627e-07 | -1.8416e-08 | 0.0068203 | 0.0068203 | 0.0068203 | 0.98988 | -0.070654 | 0.98981 | -0.071158 | 2.526
63 | -0.011995 | -0.0030055 | 0.011996 | 0.0030058 | 1.0131e-06 | 3.2547e-07 | 0.018031 | 0.018031 | 0.018031 | 0.98988 | -0.070654 | 0.98996 | -0.070043 | 6.6783
64 | 0.0014914 | 0.0003737 | -0.0014914 | -0.00037378 | 2.299e-08 | -8.5357e-08 | 0.0022421 | 0.0022421 | 0.0022421 | 0.98981 | -0.071158 | 0.98979 | -0.071269 | 0.83042
65 | 0.0030454 | 0.0007631 | -0.0030452 | -0.00076321 | 1.8178e-07 | -1.0871e-07 | 0.0045782 | 0.0045783 | 0.0045783 | 0.98981 | -0.071158 | 0.98975 | -0.071589 | 1.6957
66 | -0.0064236 | -0.0016099 | 0.006425 | 0.0016101 | 1.3756e-06 | 2.3068e-07 | 0.0097012 | 0.0097011 | 0.0097012 | 0.98528 | -0.10305 | 0.9855 | -0.1015 | 3.593
67 | -0.006425 | -0.0016101 | 0.0064271 | 0.0016105 | 2.0971e-06 | 3.5141e-07 | 0.0097011 | 0.0097009 | 0.0097011 | 0.9855 | -0.1015 | 0.98583 | -0.099147 | 3.593
68 | 0.021221 | 0.0053247 | -0.021183 | -0.0053108 | 3.8221e-05 | 1.3931e-05 | 0.031929 | 0.03193 | 0.03193 | 0.98906 | -0.076293 | 0.98722 | -0.089295 | 11.8258
69 | -0.02344 | -0.0058804 | 0.023453 | 0.0058849 | 1.2252e-05 | 4.5098e-06 | 0.035268 | 0.035268 | 0.035268 | 0.98906 | -0.076293 | 0.98959 | -0.072526 | 13.0621
70 | 0.021183 | 0.0053108 | -0.021175 | -0.0053078 | 8.2314e-06 | 3.0005e-06 | 0.03193 | 0.03193 | 0.03193 | 0.98722 | -0.089295 | 0.98683 | -0.092101 | 11.8258
71 | -0.030908 | -0.0077534 | 0.03092 | 0.0077578 | 1.178e-05 | 4.4185e-06 | 0.046478 | 0.046478 | 0.046478 | 0.98959 | -0.072526 | 0.98998 | -0.069779 | 17.2141
72 | 0.017624 | 0.0044179 | -0.017621 | -0.0044166 | 3.7466e-06 | 1.3324e-06 | 0.026576 | 0.026576 | 0.026576 | 0.98683 | -0.092101 | 0.98661 | -0.093636 | 9.8428
73 | -0.034009 | -0.0085319 | 0.03404 | 0.0085437 | 3.115e-05 | 1.1735e-05 | 0.051121 | 0.051121 | 0.051121 | 0.98998 | -0.069779 | 0.99092 | -0.063182 | 18.9336
74 | -0.040227 | -0.010094 | 0.040287 | 0.010117 | 6.0351e-05 | 2.287e-05 | 0.060411 | 0.060411 | 0.060411 | 0.99092 | -0.063182 | 0.99245 | -0.052388 | 22.3745
75 | -0.13381 | -0.033735 | 0.13385 | 0.03375 | 3.8961e-05 | 1.4905e-05 | 0.2007 | 0.2007 | 0.2007 | 0.99245 | -0.052388 | 0.99275 | -0.05031 | 37.1666
76 | 0.093525 | 0.023618 | -0.093423 | -0.023579 | 0.00010218 | 3.8869e-05 | 0.14029 | 0.14029 | 0.14029 | 0.99245 | -0.052388 | 0.99133 | -0.060169 | 25.9795
77 | 0.013555 | 0.0033976 | -0.013545 | -0.0033945 | 9.3584e-06 | 3.1415e-06 | 0.020444 | 0.020444 | 0.020444 | 0.98661 | -0.093636 | 0.98591 | -0.098625 | 7.5717
78 | 0.0064275 | 0.0016106 | -0.0064271 | -0.0016105 | 4.6404e-07 | 7.7714e-08 | 0.0097009 | 0.0097009 | 0.0097009 | 0.98591 | -0.098625 | 0.98583 | -0.099147 | 3.5929

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23128 | 0.058168

## res_load
| p_mw | q_mvar
0 | 0.0021278 | 0.00053327
1 | 0.0024793 | 0.00062137
2 | 0.0027149 | 0.00068042
3 | 0.0024604 | 0.00061662
4 | 0.002444 | 0.00061253
5 | 0.0039903 | 0.0010001
6 | 0.0095741 | 0.0023995
7 | 0.0025331 | 0.00063484
8 | 0.0025147 | 0.00063025
9 | 0.0015781 | 0.00039551
10 | 0.0080376 | 0.0020144
11 | 0.0014969 | 0.00037516
12 | 0.0021905 | 0.00054899
13 | 0.0079385 | 0.0019896
14 | 0.0026928 | 0.00067488
15 | 0.0038942 | 0.00097597
16 | 0.0064003 | 0.0016041
17 | 0.0020472 | 0.00051309
18 | 0.0040577 | 0.001017
19 | 0.0052401 | 0.0013133
20 | 0.0018825 | 0.00047181
21 | 0.0026979 | 0.00067615
22 | 0.0022188 | 0.00055607
23 | 0.0036262 | 0.00090881
24 | 0.0012202 | 0.00030581
25 | 0.0021828 | 0.00054706
26 | 0.0028751 | 0.00072057
27 | 0.0021424 | 0.00053693
28 | 0.0022549 | 0.00056513
29 | 0.0030041 | 0.00075289
30 | 0.0036769 | 0.00092152
31 | 0.00089487 | 0.00022428
32 | 0.025424 | 0.0063718
33 | 0.0037908 | 0.00095007
34 | 0.0016773 | 0.00042036
35 | 0.015867 | 0.0039766
36 | 0.0020441 | 0.0005123
37 | 0.0078224 | 0.0019605
38 | 0.00084819 | 0.00021258
39 | 0.0041055 | 0.0010289
40 | 0.001649 | 0.00041327
41 | 0.0043325 | 0.0010858
42 | 0.0014728 | 0.00036912
43 | 0.0036464 | 0.00091386
44 | 0.0014914 | 0.00037378
45 | 0.0030452 | 0.00076321
46 | 0.0064236 | 0.0016099
47 | 0.0074555 | 0.0018685
48 | 0.0035507 | 0.00088989
49 | 0.0030888 | 0.00077413
50 | 0.0061867 | 0.0015505
51 | 0.0057666 | 0.0014453
52 | 0.0013454 | 0.00033718
53 | 0.0040658 | 0.001019
54 | 0.0071178 | 0.0017839

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1