## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1083-14_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1083-14_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1083-14_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1083-14_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1083-14_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1083-14_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1083-14_0_2_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1083-14_0_2_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1083-14_0_2_node_27 | 0.4 | n |  | TRUE
9 | bus_LV_1083-14_0_2_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_1083-14_0_2_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1083-14_0_2_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1083-14_0_2_node_25 | 0.4 | n |  | TRUE
13 | bus_LV_1083-14_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1083-14_0_2_node_23 | 0.4 | n |  | TRUE
15 | bus_LV_1083-14_0_2_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_1083-14_0_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1083-14_0_2_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1083-14_0_2_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1083-14_0_2_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1083-14_0_2_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1083-14_0_2_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1083-14_0_2_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1083-14_0_2_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1083-14_0_2_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1083-14_0_2_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1083-14_0_2_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1083-14_0_2_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_1083-14_0_2_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_1083-14_0_2_node_30 | 0.4 | n |  | TRUE
30 | bus_LV_1083-14_0_2_node_31 | 0.4 | n |  | TRUE
31 | bus_MV_2_1_node_89 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1083-14_0_2_load_0 | 0 | 0.0066432 | 0.0016649 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1083-14_0_2_load_1 | 1 | 0.010411 | 0.0026091 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1083-14_0_2_load_4 | 4 | 0.01611 | 0.0040376 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1083-14_0_2_load_6 | 7 | 0.0056204 | 0.0014086 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1083-14_0_2_load_27 | 8 | 0.0015515 | 0.00038883 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1083-14_0_2_load_7 | 10 | 0.00062811 | 0.00015742 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1083-14_0_2_load_23 | 14 | 0.0092537 | 0.0023192 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1083-14_0_2_load_21 | 15 | 0.0016387 | 0.0004107 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1083-14_0_2_load_18 | 17 | 0.006997 | 0.0017536 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1083-14_0_2_load_20 | 18 | 0.0069446 | 0.0017405 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1083-14_0_2_load_10 | 19 | 0.0079924 | 0.0020031 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1083-14_0_2_load_19 | 21 | 0.008508 | 0.0021323 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1083-14_0_2_load_26 | 22 | 0.0005709 | 0.00014308 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1083-14_0_2_load_24 | 23 | 0.0088932 | 0.0022288 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1083-14_0_2_load_16 | 24 | 0.0010283 | 0.00025773 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1083-14_0_2_load_17 | 25 | 0.0030619 | 0.00076738 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1083-14_0_2_load_22 | 26 | 0.0018596 | 0.00046607 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1083-14_0_2_load_28 | 27 | 0.0023228 | 0.00058214 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1083-14_0_2_load_31 | 30 | 0.0017884 | 0.00044821 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1083-14_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0088178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1083-14_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.014692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1083-14_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.016425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1083-14_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0066811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1083-14_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.045869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1083-14_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.002174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1083-14_0_2_line_6 | NAYY 4x150 SE | 3 | 7 | 0.016057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1083-14_0_2_line_7 | NAYY 4x150 SE | 5 | 8 | 0.012803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1083-14_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.015505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1083-14_0_2_line_9 | NAYY 4x150 SE | 7 | 10 | 0.025286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1083-14_0_2_line_10 | NAYY 4x150 SE | 9 | 18 | 0.0085678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1083-14_0_2_line_11 | NAYY 4x150 SE | 9 | 16 | 0.01559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1083-14_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.029591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1083-14_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.020041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1083-14_0_2_line_14 | NAYY 4x150 SE | 12 | 22 | 0.03842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1083-14_0_2_line_15 | NAYY 4x150 SE | 12 | 23 | 0.015907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1083-14_0_2_line_16 | NAYY 4x150 SE | 13 | 20 | 0.025084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1083-14_0_2_line_17 | NAYY 4x150 SE | 13 | 19 | 0.027455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1083-14_0_2_line_18 | NAYY 4x150 SE | 14 | 15 | 0.0095701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1083-14_0_2_line_19 | NAYY 4x150 SE | 15 | 26 | 0.0069237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1083-14_0_2_line_20 | NAYY 4x150 SE | 16 | 17 | 0.012816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1083-14_0_2_line_21 | NAYY 4x150 SE | 17 | 24 | 0.03131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1083-14_0_2_line_22 | NAYY 4x150 SE | 18 | 21 | 0.028489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1083-14_0_2_line_23 | NAYY 4x150 SE | 20 | 21 | 0.034327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1083-14_0_2_line_24 | NAYY 4x150 SE | 22 | 27 | 0.0026568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1083-14_0_2_line_25 | NAYY 4x150 SE | 23 | 26 | 0.012517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1083-14_0_2_line_26 | NAYY 4x150 SE | 24 | 25 | 0.011406 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1083-14_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.029504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1083-14_0_2_line_28 | NAYY 4x150 SE | 28 | 29 | 0.056022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1083-14_0_2_line_29 | NAYY 4x150 SE | 29 | 30 | 0.004542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1083-14_0_2_trafo_1 | 0.25 MVA 20/0.4 kV | 31 | 1 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2649623.7278 | 1218364.0633 | 2649626.0226 | 1218355.5493
1 | 2649619.9044 | 1218378.249 | 2649623.7278 | 1218364.0633
2 | 2649630.2971 | 1218339.6899 | 2649626.0226 | 1218355.5493
3 | 2649619.9044 | 1218378.249 | 2649626.5514 | 1218377.5748
4 | 2649603.6288 | 1218410.5553 | 2649605.7508 | 1218399.9888 | 2649604.3019 | 1218380.754 | 2649619.9044 | 1218378.249
5 | 2649632.3945 | 1218340.2855 | 2649630.2971 | 1218339.6899
6 | 2649630.2971 | 1218339.6899 | 2649614.6462 | 1218336.1005
7 | 2649603.6288 | 1218410.5553 | 2649602.9795 | 1218413.7963 | 2649599.2864 | 1218422.5486
8 | 2649632.3945 | 1218340.2855 | 2649633.4409 | 1218335.8471 | 2649634.9279 | 1218329.5335 | 2649635.9507 | 1218325.1949
9 | 2649614.6462 | 1218336.1005 | 2649608.6167 | 1218334.7176 | 2649593.3409 | 1218329.8765 | 2649590.5348 | 1218328.6192
10 | 2649635.9507 | 1218325.1949 | 2649644.2312 | 1218327.395
11 | 2649620.8426 | 1218321.1779 | 2649635.9507 | 1218325.1949
12 | 2649683.8436 | 1218375.0795 | 2649689.057 | 1218388.8201 | 2649693.7965 | 1218402.9459
13 | 2649692.5697 | 1218357.1191 | 2649689.9737 | 1218364.4353 | 2649687.7382 | 1218368.5747 | 2649683.8436 | 1218375.0795
14 | 2649693.7965 | 1218402.9459 | 2649706.0053 | 1218439.3745
15 | 2649693.7965 | 1218402.9459 | 2649687.0279 | 1218404.6016 | 2649678.144 | 1218405.5929
16 | 2649692.5697 | 1218357.1191 | 2649701.3337 | 1218359.1934 | 2649702.3811 | 1218354.6439 | 2649703.9403 | 1218347.875 | 2649704.9405 | 1218343.5252
17 | 2649692.5697 | 1218357.1191 | 2649666.1297 | 1218349.7227
18 | 2649658.8156 | 1218406.2823 | 2649651.9707 | 1218405.588 | 2649649.3093 | 1218405.9802
19 | 2649658.8156 | 1218406.2823 | 2649665.704 | 1218406.981
20 | 2649620.8426 | 1218321.1779 | 2649624.1231 | 1218308.7891
21 | 2649632.1373 | 1218278.5226 | 2649624.1231 | 1218308.7891
22 | 2649671.7645 | 1218334.7105 | 2649644.2312 | 1218327.395
23 | 2649704.9405 | 1218343.5252 | 2649671.7645 | 1218334.7105
24 | 2649706.8496 | 1218441.8936 | 2649706.0053 | 1218439.3745
25 | 2649665.704 | 1218406.981 | 2649665.704 | 1218406.981 | 2649678.144 | 1218405.5929
26 | 2649632.1373 | 1218278.5226 | 2649635.057 | 1218267.4961
27 | 2649721.7863 | 1218466.7178 | 2649713.9002 | 1218458.6027 | 2649709.7402 | 1218450.5187 | 2649706.8496 | 1218441.8936
28 | 2649721.7863 | 1218466.7178 | 2649719.2795 | 1218473.3565 | 2649713.3036 | 1218476.4307 | 2649673.1527 | 1218489.4373
29 | 2649673.1527 | 1218489.4373 | 2649668.8997 | 1218491.0317

## bus_geodata
| x | y | coords
0 | 2649623.7278 | 1218364.0633
1 | 2649626.0226 | 1218355.5493
2 | 2649619.9044 | 1218378.249
3 | 2649630.2971 | 1218339.6899
4 | 2649626.5514 | 1218377.5748
5 | 2649603.6288 | 1218410.5553
6 | 2649632.3945 | 1218340.2855
7 | 2649614.6462 | 1218336.1005
8 | 2649599.2864 | 1218422.5486
9 | 2649635.9507 | 1218325.1949
10 | 2649590.5348 | 1218328.6192
11 | 2649683.8436 | 1218375.0795
12 | 2649693.7965 | 1218402.9459
13 | 2649692.5697 | 1218357.1191
14 | 2649649.3093 | 1218405.9802
15 | 2649658.8156 | 1218406.2823
16 | 2649620.8426 | 1218321.1779
17 | 2649624.1231 | 1218308.7891
18 | 2649644.2312 | 1218327.395
19 | 2649666.1297 | 1218349.7227
20 | 2649704.9405 | 1218343.5252
21 | 2649671.7645 | 1218334.7105
22 | 2649706.0053 | 1218439.3745
23 | 2649678.144 | 1218405.5929
24 | 2649632.1373 | 1218278.5226
25 | 2649635.057 | 1218267.4961
26 | 2649665.704 | 1218406.981
27 | 2649706.8496 | 1218441.8936
28 | 2649721.7863 | 1218466.7178
29 | 2649673.1527 | 1218489.4373
30 | 2649668.8997 | 1218491.0317
31 | 2649630.2971 | 1218339.6899

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99969 | -0.0021403 | 0.0066432 | 0.0016649
1 | 1 | 0 | -0.092702 | -0.023091
2 | 0.99932 | -0.0047336 | 0 | 0
3 | 0.99842 | -0.011026 | 0 | 0
4 | 0.99917 | -0.0058095 | 0.01611 | 0.0040376
5 | 0.99922 | -0.0054465 | 0 | 0
6 | 0.99823 | -0.012352 | 0 | 0
7 | 0.99827 | -0.012031 | 0.0056204 | 0.0014086
8 | 0.99919 | -0.0056451 | 0.0015515 | 0.00038883
9 | 0.99687 | -0.021822 | 0 | 0
10 | 0.99825 | -0.012191 | 0.00062811 | 0.00015742
11 | 0.99081 | -0.064427 | 0 | 0
12 | 0.98968 | -0.072361 | 0 | 0
13 | 0.99157 | -0.059062 | 0 | 0
14 | 0.98872 | -0.079175 | 0.0092537 | 0.0023192
15 | 0.98885 | -0.07827 | 0.0016387 | 0.0004107
16 | 0.99662 | -0.02356 | 0 | 0
17 | 0.99642 | -0.024988 | 0.006997 | 0.0017536
18 | 0.99626 | -0.026111 | 0.0069446 | 0.0017405
19 | 0.99125 | -0.061291 | 0.0079924 | 0.0020031
20 | 0.99281 | -0.050328 | 0 | 0
21 | 0.9945 | -0.03841 | 0.008508 | 0.0021323
22 | 0.98942 | -0.074199 | 0.0005709 | 0.00014308
23 | 0.98919 | -0.075872 | 0.0088932 | 0.0022288
24 | 0.99624 | -0.026277 | 0.0010283 | 0.00025773
25 | 0.99619 | -0.026628 | 0.0030619 | 0.00076738
26 | 0.98896 | -0.077501 | 0.0018596 | 0.00046607
27 | 0.98941 | -0.07431 | 0.0023228 | 0.00058214
28 | 0.98933 | -0.074851 | 0 | 0
29 | 0.98919 | -0.075874 | 0 | 0
30 | 0.98918 | -0.075957 | 0.0017884 | 0.00044821
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.024314 | -0.0060938 | 0.024321 | 0.0060964 | 7.2066e-06 | 2.6561e-06 | 0.03619 | 0.03619 | 0.03619 | 0.99969 | -0.0021403 | 1 | 0 | 13.4039
1 | 0.017671 | 0.0044288 | -0.017664 | -0.0044266 | 6.3423e-06 | 2.2468e-06 | 0.026302 | 0.026302 | 0.026302 | 0.99969 | -0.0021403 | 0.99932 | -0.0047336 | 9.7416
2 | 0.067581 | 0.016994 | -0.067477 | -0.016955 | 0.00010369 | 3.9665e-05 | 0.10058 | 0.10058 | 0.10058 | 1 | 0 | 0.99842 | -0.011026 | 37.2524
3 | 0.016113 | 0.0040384 | -0.01611 | -0.0040376 | 2.3998e-06 | 8.3547e-07 | 0.023992 | 0.023992 | 0.023992 | 0.99932 | -0.0047336 | 0.99917 | -0.0058095 | 8.886
4 | 0.0015517 | 0.00038814 | -0.0015515 | -0.00038868 | 1.5277e-07 | -5.4214e-07 | 0.0023102 | 0.0023104 | 0.0023104 | 0.99932 | -0.0047336 | 0.99922 | -0.0054465 | 0.85571
5 | 0.061228 | 0.015389 | -0.061216 | -0.015384 | 1.13e-05 | 4.3177e-06 | 0.091268 | 0.091268 | 0.091268 | 0.99842 | -0.011026 | 0.99823 | -0.012352 | 33.8029
6 | 0.0062494 | 0.0015658 | -0.0062485 | -0.0015657 | 8.6919e-07 | 1.2434e-07 | 0.0093138 | 0.0093139 | 0.0093139 | 0.99842 | -0.011026 | 0.99827 | -0.012031 | 3.4496
7 | 0.0015515 | 0.00038868 | -0.0015515 | -0.00038883 | 4.2647e-08 | -1.513e-07 | 0.0023104 | 0.0023105 | 0.0023105 | 0.99922 | -0.0054465 | 0.99919 | -0.0056451 | 0.85573
8 | 0.061216 | 0.015384 | -0.061136 | -0.015354 | 8.0592e-05 | 3.0794e-05 | 0.091268 | 0.091268 | 0.091268 | 0.99823 | -0.012352 | 0.99687 | -0.021822 | 33.8029
9 | 0.00062813 | 0.00015709 | -0.00062811 | -0.00015742 | 1.383e-08 | -3.2526e-07 | 0.00093616 | 0.00093628 | 0.00093628 | 0.99827 | -0.012031 | 0.99825 | -0.012191 | 0.34677
10 | 0.050043 | 0.012574 | -0.050013 | -0.012562 | 2.984e-05 | 1.1365e-05 | 0.07471 | 0.07471 | 0.07471 | 0.99687 | -0.021822 | 0.99626 | -0.026111 | 27.6702
11 | 0.011093 | 0.00278 | -0.01109 | -0.0027792 | 2.6672e-06 | 8.2266e-07 | 0.016558 | 0.016558 | 0.016558 | 0.99687 | -0.021822 | 0.99662 | -0.02356 | 6.1327
12 | 0.026374 | 0.0066134 | -0.026345 | -0.0066027 | 2.897e-05 | 1.0762e-05 | 0.03961 | 0.03961 | 0.03961 | 0.99081 | -0.064427 | 0.98968 | -0.072361 | 14.6704
13 | -0.026374 | -0.0066134 | 0.026393 | 0.0066207 | 1.962e-05 | 7.288e-06 | 0.03961 | 0.03961 | 0.03961 | 0.99081 | -0.064427 | 0.99157 | -0.059062 | 14.6703
14 | 0.0046837 | 0.0011724 | -0.0046825 | -0.0011724 | 1.1888e-06 | -3.6349e-08 | 0.0070416 | 0.0070418 | 0.0070418 | 0.98968 | -0.072361 | 0.98942 | -0.074199 | 2.6081
15 | 0.021661 | 0.0054303 | -0.02165 | -0.0054264 | 1.0529e-05 | 3.8452e-06 | 0.032568 | 0.032568 | 0.032568 | 0.98968 | -0.072361 | 0.98919 | -0.075872 | 12.0624
16 | -0.034388 | -0.0086244 | 0.03443 | 0.0086401 | 4.1688e-05 | 1.571e-05 | 0.051607 | 0.051607 | 0.051607 | 0.99157 | -0.059062 | 0.99281 | -0.050328 | 19.1139
17 | 0.0079949 | 0.0020037 | -0.0079924 | -0.0020031 | 2.4661e-06 | 5.9447e-07 | 0.011998 | 0.011998 | 0.011998 | 0.99157 | -0.059062 | 0.99125 | -0.061291 | 4.4436
18 | -0.0092537 | -0.0023192 | 0.0092549 | 0.0023195 | 1.1583e-06 | 3.2273e-07 | 0.013927 | 0.013927 | 0.013927 | 0.98872 | -0.079175 | 0.98885 | -0.07827 | 5.1581
19 | -0.010894 | -0.0027302 | 0.010895 | 0.0027306 | 1.161e-06 | 3.577e-07 | 0.016393 | 0.016393 | 0.016393 | 0.98885 | -0.07827 | 0.98896 | -0.077501 | 6.0714
20 | 0.01109 | 0.0027792 | -0.011088 | -0.0027785 | 2.1926e-06 | 6.7635e-07 | 0.016558 | 0.016558 | 0.016558 | 0.99662 | -0.02356 | 0.99642 | -0.024988 | 6.1327
21 | 0.0040911 | 0.0010249 | -0.0040904 | -0.001025 | 7.2922e-07 | -1.2728e-07 | 0.0061093 | 0.0061095 | 0.0061095 | 0.99642 | -0.024988 | 0.99624 | -0.026277 | 2.2628
22 | 0.043068 | 0.010822 | -0.042995 | -0.010794 | 7.3583e-05 | 2.7931e-05 | 0.064337 | 0.064337 | 0.064337 | 0.99626 | -0.026111 | 0.9945 | -0.03841 | 23.8286
23 | -0.03443 | -0.0086401 | 0.034487 | 0.0086616 | 5.7048e-05 | 2.1497e-05 | 0.051607 | 0.051607 | 0.051607 | 0.99281 | -0.050328 | 0.9945 | -0.03841 | 19.1138
24 | 0.0041116 | 0.0010293 | -0.0041116 | -0.0010294 | 6.3382e-08 | -9.7434e-09 | 0.0061832 | 0.0061832 | 0.0061832 | 0.98942 | -0.074199 | 0.98941 | -0.07431 | 2.2901
25 | 0.012757 | 0.0031976 | -0.012754 | -0.0031966 | 2.8766e-06 | 9.4572e-07 | 0.019191 | 0.019191 | 0.019191 | 0.98919 | -0.075872 | 0.98896 | -0.077501 | 7.1077
26 | 0.003062 | 0.00076729 | -0.0030619 | -0.00076738 | 1.4888e-07 | -9.1252e-08 | 0.0045735 | 0.0045735 | 0.0045735 | 0.99624 | -0.026277 | 0.99619 | -0.026628 | 1.6939
27 | 0.0017888 | 0.00044721 | -0.0017887 | -0.00044754 | 1.3321e-07 | -3.2765e-07 | 0.0026899 | 0.00269 | 0.00269 | 0.98941 | -0.07431 | 0.98933 | -0.074851 | 0.9963
28 | 0.0017887 | 0.00044754 | -0.0017884 | -0.00044816 | 2.5298e-07 | -6.2196e-07 | 0.00269 | 0.0026903 | 0.0026903 | 0.98933 | -0.074851 | 0.98919 | -0.075874 | 0.99639
29 | 0.0017884 | 0.00044816 | -0.0017884 | -0.00044821 | 2.0513e-08 | -5.0416e-08 | 0.0026903 | 0.0026903 | 0.0026903 | 0.98919 | -0.075874 | 0.98918 | -0.075957 | 0.9964

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10311 | 0.0257

## res_load
| p_mw | q_mvar
0 | 0.0066432 | 0.0016649
1 | 0.010411 | 0.0026091
2 | 0.01611 | 0.0040376
3 | 0.0056204 | 0.0014086
4 | 0.0015515 | 0.00038883
5 | 0.00062811 | 0.00015742
6 | 0.0092537 | 0.0023192
7 | 0.0016387 | 0.0004107
8 | 0.006997 | 0.0017536
9 | 0.0069446 | 0.0017405
10 | 0.0079924 | 0.0020031
11 | 0.008508 | 0.0021323
12 | 0.0005709 | 0.00014308
13 | 0.0088932 | 0.0022288
14 | 0.0010283 | 0.00025773
15 | 0.0030619 | 0.00076738
16 | 0.0018596 | 0.00046607
17 | 0.0023228 | 0.00058214
18 | 0.0017884 | 0.00044821

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1