## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1086-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1086-1_0_4_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1086-1_0_4_node_6 | 0.4 | n |  | TRUE
3 | bus_LV_1086-1_0_4_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_1086-1_0_4_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1086-1_0_4_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_1086-1_0_4_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1086-1_0_4_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1086-1_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1086-1_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1086-1_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1086-1_0_4_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1086-1_0_4_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_1086-1_0_4_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1086-1_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1086-1_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1086-1_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1086-1_0_4_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1086-1_0_4_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1086-1_0_4_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1086-1_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1086-1_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1086-1_0_4_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1086-1_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1086-1_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1086-1_0_4_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1086-1_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_MV_128_0_node_293 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1086-1_0_4_load_0 | 0 | 0.010813 | 0.00271 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1086-1_0_4_load_29 | 5 | 0.0050193 | 0.001258 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1086-1_0_4_load_11 | 8 | 0.0028656 | 0.00071818 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1086-1_0_4_load_18 | 11 | 0.047069 | 0.011797 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1086-1_0_4_load_30 | 12 | 0.0045413 | 0.0011382 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1086-1_0_4_load_15 | 14 | 0.07611 | 0.019075 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1086-1_0_4_load_19 | 17 | 0.0015434 | 0.00038682 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1086-1_0_4_load_28 | 18 | 0.0026905 | 0.0006743 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1086-1_0_4_load_25 | 19 | 0.0071626 | 0.0017951 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1086-1_0_4_load_12 | 20 | 0.00076644 | 0.00019209 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1086-1_0_4_load_21 | 22 | 0.0067459 | 0.0016907 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1086-1_0_4_load_20 | 23 | 0.0034163 | 0.0008562 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1086-1_0_4_load_24 | 24 | 0.0073933 | 0.0018529 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1086-1_0_4_load_27 | 25 | 0.0056242 | 0.0014096 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1086-1_0_4_load_26 | 26 | 0.0099791 | 0.002501 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1086-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.026776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1086-1_0_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.078689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1086-1_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.052311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1086-1_0_4_line_3 | NAYY 4x150 SE | 2 | 11 | 0.019319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1086-1_0_4_line_4 | NAYY 4x150 SE | 2 | 9 | 0.070771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1086-1_0_4_line_5 | NAYY 4x150 SE | 3 | 12 | 0.011075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1086-1_0_4_line_6 | NAYY 4x150 SE | 4 | 5 | 0.0349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1086-1_0_4_line_7 | NAYY 4x150 SE | 4 | 6 | 0.028345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1086-1_0_4_line_8 | NAYY 4x150 SE | 4 | 7 | 0.098098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1086-1_0_4_line_9 | NAYY 4x150 SE | 6 | 8 | 0.00833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1086-1_0_4_line_10 | NAYY 4x150 SE | 7 | 20 | 0.07215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1086-1_0_4_line_11 | NAYY 4x150 SE | 8 | 9 | 0.010134 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1086-1_0_4_line_12 | NAYY 4x150 SE | 9 | 10 | 0.10893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1086-1_0_4_line_13 | NAYY 4x150 SE | 10 | 18 | 0.013728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1086-1_0_4_line_14 | NAYY 4x150 SE | 10 | 19 | 0.033144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1086-1_0_4_line_15 | NAYY 4x150 SE | 10 | 13 | 0.092823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1086-1_0_4_line_16 | NAYY 4x150 SE | 13 | 14 | 0.032618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1086-1_0_4_line_17 | NAYY 4x150 SE | 14 | 21 | 0.042109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1086-1_0_4_line_18 | NAYY 4x150 SE | 15 | 16 | 0.06836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1086-1_0_4_line_19 | NAYY 4x150 SE | 15 | 17 | 0.013602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1086-1_0_4_line_20 | NAYY 4x150 SE | 16 | 22 | 0.037325 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1086-1_0_4_line_21 | NAYY 4x150 SE | 16 | 21 | 0.032206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1086-1_0_4_line_22 | NAYY 4x150 SE | 17 | 23 | 0.012024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1086-1_0_4_line_23 | NAYY 4x150 SE | 19 | 24 | 0.023112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1086-1_0_4_line_24 | NAYY 4x150 SE | 24 | 26 | 0.025282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1086-1_0_4_line_25 | NAYY 4x150 SE | 25 | 26 | 0.021204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1086-1_0_4_trafo_7 | 0.25 MVA 20/0.4 kV | 27 | 3 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2646300.2529 | 1220102.9293 | 2646309.51 | 1220113.5965 | 2646299.9157 | 1220121.8446
1 | 2646353.9 | 1220125.8044 | 2646345.1021 | 1220134.141 | 2646311.1111 | 1220094.0638 | 2646300.2529 | 1220102.9293
2 | 2646300.2529 | 1220102.9293 | 2646311.1111 | 1220094.0638 | 2646307.6526 | 1220089.9789 | 2646304.9345 | 1220086.3112 | 2646318.163 | 1220074.1288 | 2646325.6773 | 1220066.9495
3 | 2646353.9 | 1220125.8044 | 2646353.5391 | 1220125.3791 | 2646341.3379 | 1220111.1271
4 | 2646353.9 | 1220125.8044 | 2646373.2725 | 1220147.9796 | 2646377.8298 | 1220153.1959 | 2646373.296 | 1220167.3803 | 2646368.8768 | 1220180.4872 | 2646365.85 | 1220185.2888
5 | 2646318.0768 | 1220058.8745 | 2646325.6773 | 1220066.9495
6 | 2646314.1824 | 1220201.6303 | 2646317.4495 | 1220201.0442 | 2646320.293 | 1220201.2665 | 2646323.732 | 1220203.9393 | 2646327.5383 | 1220212.0737 | 2646338.5084 | 1220222.9433
7 | 2646338.5084 | 1220222.9433 | 2646342.2183 | 1220215.1786 | 2646347.9641 | 1220207.0851 | 2646354.5383 | 1220199.7984
8 | 2646309.6213 | 1220247.656 | 2646344.0159 | 1220274.7396 | 2646337.8962 | 1220263.6076 | 2646335.5825 | 1220254.7731 | 2646334.1021 | 1220245.1336 | 2646335.2062 | 1220233.8909 | 2646338.5084 | 1220222.9433
9 | 2646354.5383 | 1220199.7984 | 2646360.1171 | 1220193.6125
10 | 2646309.6213 | 1220247.656 | 2646288.6165 | 1220229.5264 | 2646258.4198 | 1220196.9716
11 | 2646365.85 | 1220185.2888 | 2646361.7171 | 1220191.8384 | 2646360.1171 | 1220193.6125
12 | 2646365.85 | 1220185.2888 | 2646368.8768 | 1220180.4872 | 2646373.296 | 1220167.3803 | 2646377.8298 | 1220153.1959 | 2646379.5719 | 1220147.7395 | 2646384.668 | 1220133.4483 | 2646389.6272 | 1220117.2661 | 2646392.5523 | 1220102.1464 | 2646393.8983 | 1220092.9847 | 2646393.0586 | 1220080.9709
13 | 2646393.0586 | 1220080.9709 | 2646405.6956 | 1220075.6085
14 | 2646393.0586 | 1220080.9709 | 2646390.6906 | 1220072.2917 | 2646383.5936 | 1220056.0711 | 2646380.2067 | 1220050.5914
15 | 2646355.2631 | 1220041.3085 | 2646382.7767 | 1220082.0693 | 2646386.8182 | 1220091.1729 | 2646392.5523 | 1220102.1464 | 2646393.8983 | 1220092.9847 | 2646393.0586 | 1220080.9709
16 | 2646355.2631 | 1220041.3085 | 2646350.8276 | 1220030.1673 | 2646345.4374 | 1220021.7759 | 2646338.2779 | 1220013.8877
17 | 2646309.0638 | 1219983.5924 | 2646312.5457 | 1219986.6213 | 2646325.2964 | 1219999.8172 | 2646337.7037 | 1220013.2551 | 2646338.2779 | 1220013.8877
18 | 2646280.1456 | 1219972.1165 | 2646274.4497 | 1219979.6324 | 2646264.9884 | 1219989.3537 | 2646247.995 | 1220004.6422 | 2646240.3711 | 1220010.2975 | 2646229.9899 | 1220018.3107
19 | 2646229.9899 | 1220018.3107 | 2646233.2837 | 1220009.4087 | 2646232.9594 | 1220005.3114
20 | 2646280.1456 | 1219972.1165 | 2646290.4906 | 1219962.9246 | 2646310.7609 | 1219951.0626
21 | 2646309.0638 | 1219983.5924 | 2646300.8293 | 1219978.959 | 2646282.9088 | 1219975.8513 | 2646280.1456 | 1219972.1165
22 | 2646232.9594 | 1220005.3114 | 2646232.7378 | 1220002.5114 | 2646229.3225 | 1219993.9522
23 | 2646380.2067 | 1220050.5914 | 2646376.4677 | 1220044.5421 | 2646366.9711 | 1220031.6642
24 | 2646351.9662 | 1220011.3168 | 2646366.9711 | 1220031.6642
25 | 2646339.3816 | 1219994.2515 | 2646351.9662 | 1220011.3168

## bus_geodata
| x | y | coords
0 | 2646299.9157 | 1220121.8446
1 | 2646300.2529 | 1220102.9293
2 | 2646353.9 | 1220125.8044
3 | 2646325.6773 | 1220066.9495
4 | 2646338.5084 | 1220222.9433
5 | 2646314.1824 | 1220201.6303
6 | 2646354.5383 | 1220199.7984
7 | 2646309.6213 | 1220247.656
8 | 2646360.1171 | 1220193.6125
9 | 2646365.85 | 1220185.2888
10 | 2646393.0586 | 1220080.9709
11 | 2646341.3379 | 1220111.1271
12 | 2646318.0768 | 1220058.8745
13 | 2646355.2631 | 1220041.3085
14 | 2646338.2779 | 1220013.8877
15 | 2646229.9899 | 1220018.3107
16 | 2646280.1456 | 1219972.1165
17 | 2646232.9594 | 1220005.3114
18 | 2646405.6956 | 1220075.6085
19 | 2646380.2067 | 1220050.5914
20 | 2646258.4198 | 1220196.9716
21 | 2646309.0638 | 1219983.5924
22 | 2646310.7609 | 1219951.0626
23 | 2646229.3225 | 1219993.9522
24 | 2646366.9711 | 1220031.6642
25 | 2646339.3816 | 1219994.2515
26 | 2646351.9662 | 1220011.3168
27 | 2646318.163 | 1220074.1288

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99483 | -0.035683 | 0.010813 | 0.00271
1 | 0.99524 | -0.032764 | 0 | 0
2 | 0.98849 | -0.07974 | 0 | 0
3 | 1 | 0 | -0.19658 | -0.049585
4 | 0.98359 | -0.11417 | 0 | 0
5 | 0.98334 | -0.11598 | 0.0050193 | 0.001258
6 | 0.98383 | -0.11248 | 0 | 0
7 | 0.98348 | -0.11496 | 0 | 0
8 | 0.9839 | -0.11198 | 0.0028656 | 0.00071818
9 | 0.98403 | -0.11107 | 0 | 0
10 | 0.97761 | -0.15656 | 0 | 0
11 | 0.98718 | -0.08904 | 0.047069 | 0.011797
12 | 0.99993 | -0.00050206 | 0.0045413 | 0.0011382
13 | 0.97362 | -0.18506 | 0 | 0
14 | 0.97222 | -0.19513 | 0.07611 | 0.019075
15 | 0.97045 | -0.20793 | 0 | 0
16 | 0.97095 | -0.20434 | 0 | 0
17 | 0.97035 | -0.20865 | 0.0015434 | 0.00038682
18 | 0.97755 | -0.15694 | 0.0026905 | 0.0006743
19 | 0.97615 | -0.16701 | 0.0071626 | 0.0017951
20 | 0.9834 | -0.11553 | 0.00076644 | 0.00019209
21 | 0.9715 | -0.20034 | 0 | 0
22 | 0.97058 | -0.20701 | 0.0067459 | 0.0016907
23 | 0.97029 | -0.20908 | 0.0034163 | 0.0008562
24 | 0.97537 | -0.17259 | 0.0073933 | 0.0018529
25 | 0.97462 | -0.17798 | 0.0056242 | 0.0014096
26 | 0.97479 | -0.17673 | 0.0099791 | 0.002501
27 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.010813 | -0.00271 | 0.010817 | 0.0027113 | 4.3706e-06 | 1.3332e-06 | 0.016174 | 0.016173 | 0.016174 | 0.99483 | -0.035683 | 0.99524 | -0.032764 | 5.9902
1 | 0.17954 | 0.045398 | -0.17836 | -0.044947 | 0.0011807 | 0.00045105 | 0.26858 | 0.26858 | 0.26858 | 0.99524 | -0.032764 | 0.98849 | -0.07974 | 33.1581
2 | -0.19036 | -0.04811 | 0.19124 | 0.048447 | 0.00088226 | 0.00033728 | 0.28475 | 0.28475 | 0.28475 | 0.99524 | -0.032764 | 1 | 0 | 35.1547
3 | 0.04713 | 0.01182 | -0.047069 | -0.011797 | 6.0683e-05 | 2.3092e-05 | 0.070949 | 0.070949 | 0.070949 | 0.98849 | -0.07974 | 0.98718 | -0.08904 | 26.2773
4 | 0.13123 | 0.033128 | -0.13066 | -0.032909 | 0.00057496 | 0.00021843 | 0.19763 | 0.19763 | 0.19763 | 0.98849 | -0.07974 | 0.98403 | -0.11107 | 24.3992
5 | 0.0045417 | 0.0011381 | -0.0045413 | -0.0011382 | 3.1562e-07 | -2.3892e-08 | 0.006758 | 0.0067581 | 0.0067581 | 1 | 0 | 0.99993 | -0.00050206 | 2.503
6 | 0.0050206 | 0.001258 | -0.0050193 | -0.001258 | 1.2563e-06 | 4.0348e-08 | 0.0075952 | 0.0075953 | 0.0075953 | 0.98359 | -0.11417 | 0.98334 | -0.11598 | 2.8131
7 | -0.0057871 | -0.001448 | 0.0057885 | 0.0014481 | 1.3555e-06 | 1.6147e-07 | 0.0087541 | 0.008754 | 0.0087541 | 0.98359 | -0.11417 | 0.98383 | -0.11248 | 3.2423
8 | 0.00076658 | 0.00018998 | -0.0007665 | -0.0001912 | 8.2251e-08 | -1.2133e-06 | 0.001159 | 0.0011594 | 0.0011594 | 0.98359 | -0.11417 | 0.98348 | -0.11496 | 0.4294
9 | -0.0057885 | -0.0014481 | 0.0057889 | 0.0014482 | 3.9833e-07 | 4.7418e-08 | 0.008754 | 0.008754 | 0.008754 | 0.98383 | -0.11248 | 0.9839 | -0.11198 | 3.2422
10 | 0.0007665 | 0.0001912 | -0.00076644 | -0.00019209 | 6.0535e-08 | -8.9219e-07 | 0.0011594 | 0.0011597 | 0.0011597 | 0.98348 | -0.11496 | 0.9834 | -0.11553 | 0.42953
11 | -0.0086545 | -0.0021664 | 0.0086556 | 0.0021667 | 1.0831e-06 | 2.8787e-07 | 0.013088 | 0.013088 | 0.013088 | 0.9839 | -0.11198 | 0.98403 | -0.11107 | 4.8473
12 | 0.122 | 0.030742 | -0.12123 | -0.03045 | 0.00077164 | 0.00029266 | 0.18455 | 0.18455 | 0.18455 | 0.98403 | -0.11107 | 0.97761 | -0.15656 | 22.7836
13 | 0.0026906 | 0.00067418 | -0.0026905 | -0.0006743 | 1.4367e-07 | -1.1685e-07 | 0.0040953 | 0.0040954 | 0.0040954 | 0.97761 | -0.15656 | 0.97755 | -0.15694 | 1.5168
14 | 0.030231 | 0.0075848 | -0.030187 | -0.0075684 | 4.3795e-05 | 1.6429e-05 | 0.046017 | 0.046017 | 0.046017 | 0.97761 | -0.15656 | 0.97615 | -0.16701 | 17.0434
15 | 0.088308 | 0.022191 | -0.087959 | -0.02206 | 0.00034893 | 0.00013073 | 0.13443 | 0.13444 | 0.13444 | 0.97761 | -0.15656 | 0.97362 | -0.18506 | 16.597
16 | 0.087959 | 0.02206 | -0.087836 | -0.022014 | 0.00012262 | 4.5945e-05 | 0.13444 | 0.13444 | 0.13444 | 0.97362 | -0.18506 | 0.97222 | -0.19513 | 16.5971
17 | 0.011726 | 0.0029391 | -0.011718 | -0.0029363 | 8.4638e-06 | 2.7335e-06 | 0.017947 | 0.017948 | 0.017948 | 0.97222 | -0.19513 | 0.9715 | -0.20034 | 6.6473
18 | -0.0049604 | -0.001243 | 0.0049629 | 0.0012431 | 2.4676e-06 | 1.0402e-07 | 0.0076059 | 0.0076056 | 0.0076059 | 0.97045 | -0.20793 | 0.97095 | -0.20434 | 2.817
19 | 0.0049604 | 0.001243 | -0.0049599 | -0.001243 | 4.9101e-07 | 2.081e-08 | 0.0076059 | 0.0076059 | 0.0076059 | 0.97045 | -0.20793 | 0.97035 | -0.20865 | 2.817
20 | 0.0067484 | 0.0016912 | -0.0067459 | -0.0016907 | 2.4912e-06 | 4.967e-07 | 0.010342 | 0.010342 | 0.010342 | 0.97095 | -0.20434 | 0.97058 | -0.20701 | 3.8305
21 | -0.011711 | -0.0029343 | 0.011718 | 0.0029363 | 6.4735e-06 | 2.0912e-06 | 0.017948 | 0.017948 | 0.017948 | 0.97095 | -0.20434 | 0.9715 | -0.20034 | 6.6473
22 | 0.0034165 | 0.00085613 | -0.0034163 | -0.0008562 | 2.0595e-07 | -6.9313e-08 | 0.0052391 | 0.0052392 | 0.0052392 | 0.97035 | -0.20865 | 0.97029 | -0.20908 | 1.9404
23 | 0.023024 | 0.0057733 | -0.023007 | -0.0057667 | 1.7767e-05 | 6.5448e-06 | 0.035099 | 0.035099 | 0.035099 | 0.97615 | -0.16701 | 0.97537 | -0.17259 | 12.9996
24 | 0.015613 | 0.0039138 | -0.015604 | -0.0039107 | 8.9508e-06 | 3.1273e-06 | 0.02382 | 0.02382 | 0.02382 | 0.97537 | -0.17259 | 0.97479 | -0.17673 | 8.8222
25 | -0.0056242 | -0.0014096 | 0.0056252 | 0.0014097 | 9.7557e-07 | 1.1094e-07 | 0.0085868 | 0.0085867 | 0.0085868 | 0.97462 | -0.17798 | 0.97479 | -0.17673 | 3.1803

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19658 | 0.049585

## res_load
| p_mw | q_mvar
0 | 0.010813 | 0.00271
1 | 0.0050193 | 0.001258
2 | 0.0028656 | 0.00071818
3 | 0.047069 | 0.011797
4 | 0.0045413 | 0.0011382
5 | 0.07611 | 0.019075
6 | 0.0015434 | 0.00038682
7 | 0.0026905 | 0.0006743
8 | 0.0071626 | 0.0017951
9 | 0.00076644 | 0.00019209
10 | 0.0067459 | 0.0016907
11 | 0.0034163 | 0.0008562
12 | 0.0073933 | 0.0018529
13 | 0.0056242 | 0.0014096
14 | 0.0099791 | 0.002501

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1