## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1086-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1086-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1086-7_0_4_node_28 | 0.4 | n |  | TRUE
3 | bus_LV_1086-7_0_4_node_58 | 0.4 | n |  | TRUE
4 | bus_LV_1086-7_0_4_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_1086-7_0_4_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_1086-7_0_4_node_57 | 0.4 | n |  | TRUE
7 | bus_LV_1086-7_0_4_node_2 | 0.4 | n |  | TRUE
8 | bus_LV_1086-7_0_4_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_1086-7_0_4_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_1086-7_0_4_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1086-7_0_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1086-7_0_4_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1086-7_0_4_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1086-7_0_4_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1086-7_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1086-7_0_4_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1086-7_0_4_node_7 | 0.4 | n |  | TRUE
18 | bus_LV_1086-7_0_4_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1086-7_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_1086-7_0_4_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_1086-7_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1086-7_0_4_node_59 | 0.4 | n |  | TRUE
23 | bus_LV_1086-7_0_4_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_1086-7_0_4_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1086-7_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1086-7_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1086-7_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1086-7_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1086-7_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_1086-7_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1086-7_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_1086-7_0_4_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_1086-7_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1086-7_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_1086-7_0_4_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_1086-7_0_4_node_50 | 0.4 | n |  | TRUE
37 | bus_LV_1086-7_0_4_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1086-7_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1086-7_0_4_node_37 | 0.4 | n |  | TRUE
40 | bus_LV_1086-7_0_4_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_1086-7_0_4_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_1086-7_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_1086-7_0_4_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_1086-7_0_4_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_1086-7_0_4_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_1086-7_0_4_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_1086-7_0_4_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_1086-7_0_4_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1086-7_0_4_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_1086-7_0_4_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_1086-7_0_4_node_56 | 0.4 | n |  | TRUE
52 | bus_LV_1086-7_0_4_node_55 | 0.4 | n |  | TRUE
53 | bus_LV_1086-7_0_4_node_49 | 0.4 | n |  | TRUE
54 | bus_LV_1086-7_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_1086-7_0_4_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_1086-7_0_4_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_1086-7_0_4_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_1086-7_0_4_node_53 | 0.4 | n |  | TRUE
59 | bus_MV_128_0_node_269 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1086-7_0_4_load_0 | 0 | 0.0022853 | 0.00057276 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1086-7_0_4_load_58 | 3 | 0.0014599 | 0.0003659 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1086-7_0_4_load_29 | 4 | 0.0039752 | 0.00099627 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1086-7_0_4_load_27 | 5 | 0.0034619 | 0.00086764 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1086-7_0_4_load_57 | 6 | 0.0043814 | 0.0010981 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1086-7_0_4_load_2 | 7 | 0.057395 | 0.014385 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1086-7_0_4_load_5 | 10 | 0.0022992 | 0.00057624 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1086-7_0_4_load_15 | 12 | 0.001923 | 0.00048194 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1086-7_0_4_load_14 | 13 | 0.0020461 | 0.00051279 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1086-7_0_4_load_6 | 14 | 0.056845 | 0.014247 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1086-7_0_4_load_9 | 15 | 0.003898 | 0.00097693 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1086-7_0_4_load_11 | 16 | 0.0023818 | 0.00059694 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1086-7_0_4_load_7 | 17 | 0.0034945 | 0.00087581 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1086-7_0_4_load_8 | 19 | 0.001862 | 0.00046666 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1086-7_0_4_load_12 | 20 | 0.0028758 | 0.00072074 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1086-7_0_4_load_13 | 21 | 0.0021148 | 0.00053002 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1086-7_0_4_load_59 | 22 | 0.0021185 | 0.00053095 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1086-7_0_4_load_17 | 24 | 0.0021065 | 0.00052794 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1086-7_0_4_load_18 | 25 | 0.0019989 | 0.00050097 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1086-7_0_4_load_19 | 26 | 0.0027465 | 0.00068833 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1086-7_0_4_load_21 | 28 | 0.0028327 | 0.00070995 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1086-7_0_4_load_22 | 29 | 0.0020166 | 0.00050541 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1086-7_0_4_load_30 | 31 | 0.00373 | 0.00093483 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1086-7_0_4_load_24 | 32 | 0.0038944 | 0.00097602 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1086-7_0_4_load_31 | 33 | 0.0019884 | 0.00049835 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1086-7_0_4_load_51 | 35 | 0.0024904 | 0.00062415 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1086-7_0_4_load_50 | 36 | 0.0019265 | 0.00048283 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1086-7_0_4_load_33 | 37 | 0.0021034 | 0.00052717 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1086-7_0_4_load_34 | 38 | 0.0056771 | 0.0014228 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1086-7_0_4_load_37 | 39 | 0.0021034 | 0.00052717 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1086-7_0_4_load_45 | 40 | 0.0030793 | 0.00077174 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1086-7_0_4_load_35 | 41 | 0.0026306 | 0.0006593 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1086-7_0_4_load_36 | 43 | 0.0058941 | 0.0014772 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1086-7_0_4_load_38 | 44 | 0.0034099 | 0.00085459 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1086-7_0_4_load_39 | 45 | 0.0047541 | 0.0011915 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1086-7_0_4_load_40 | 46 | 0.0065364 | 0.0016382 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1086-7_0_4_load_43 | 48 | 0.0010729 | 0.0002689 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1086-7_0_4_load_44 | 49 | 0.002066 | 0.0005178 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1086-7_0_4_load_54 | 50 | 0.0035363 | 0.00088629 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1086-7_0_4_load_56 | 51 | 0.0016393 | 0.00041085 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1086-7_0_4_load_55 | 52 | 0.0018529 | 0.00046438 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1086-7_0_4_load_49 | 53 | 0.001643 | 0.00041179 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1086-7_0_4_load_46 | 54 | 0.0042686 | 0.0010698 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1086-7_0_4_load_47 | 55 | 0.0018192 | 0.00045593 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1086-7_0_4_load_48 | 56 | 0.0022724 | 0.00056952 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1086-7_0_4_load_52 | 57 | 0.0012678 | 0.00031774 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1086-7_0_4_load_53 | 58 | 0.002082 | 0.00052179 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1086-7_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.019425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1086-7_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.18847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1086-7_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.10024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1086-7_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.044809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1086-7_0_4_line_4 | NAYY 4x150 SE | 2 | 5 | 0.027764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1086-7_0_4_line_5 | NAYY 4x150 SE | 3 | 6 | 0.15375 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1086-7_0_4_line_6 | NAYY 4x150 SE | 4 | 35 | 0.022652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1086-7_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.052911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1086-7_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.024461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1086-7_0_4_line_9 | NAYY 4x150 SE | 8 | 10 | 0.025524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1086-7_0_4_line_10 | NAYY 4x150 SE | 9 | 11 | 0.077159 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1086-7_0_4_line_11 | NAYY 4x150 SE | 10 | 14 | 0.004313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1086-7_0_4_line_12 | NAYY 4x150 SE | 11 | 18 | 0.029473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1086-7_0_4_line_13 | NAYY 4x150 SE | 11 | 12 | 0.013604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1086-7_0_4_line_14 | NAYY 4x150 SE | 12 | 13 | 0.0075231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1086-7_0_4_line_15 | NAYY 4x150 SE | 13 | 21 | 0.016732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1086-7_0_4_line_16 | NAYY 4x150 SE | 15 | 16 | 0.0041115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1086-7_0_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.013915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1086-7_0_4_line_18 | NAYY 4x150 SE | 16 | 20 | 0.015064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1086-7_0_4_line_19 | NAYY 4x150 SE | 17 | 19 | 0.010759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1086-7_0_4_line_20 | NAYY 4x150 SE | 18 | 22 | 0.042708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1086-7_0_4_line_21 | NAYY 4x150 SE | 18 | 23 | 0.029151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1086-7_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.0052338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1086-7_0_4_line_23 | NAYY 4x150 SE | 23 | 32 | 0.058906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1086-7_0_4_line_24 | NAYY 4x150 SE | 24 | 25 | 0.0094156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1086-7_0_4_line_25 | NAYY 4x150 SE | 24 | 26 | 0.017194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1086-7_0_4_line_26 | NAYY 4x150 SE | 25 | 27 | 0.0416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1086-7_0_4_line_27 | NAYY 4x150 SE | 26 | 28 | 0.015311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1086-7_0_4_line_28 | NAYY 4x150 SE | 27 | 29 | 0.023641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1086-7_0_4_line_29 | NAYY 4x150 SE | 27 | 30 | 0.06836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1086-7_0_4_line_30 | NAYY 4x150 SE | 28 | 31 | 0.022287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1086-7_0_4_line_31 | NAYY 4x150 SE | 29 | 32 | 0.015435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_1086-7_0_4_line_32 | NAYY 4x150 SE | 30 | 33 | 0.02811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1086-7_0_4_line_33 | NAYY 4x150 SE | 33 | 34 | 0.021965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1086-7_0_4_line_34 | NAYY 4x150 SE | 34 | 37 | 0.012246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1086-7_0_4_line_35 | NAYY 4x150 SE | 34 | 38 | 0.015517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1086-7_0_4_line_36 | NAYY 4x150 SE | 35 | 36 | 0.027067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1086-7_0_4_line_37 | NAYY 4x150 SE | 36 | 57 | 0.004805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1086-7_0_4_line_38 | NAYY 4x150 SE | 37 | 39 | 0.0069097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1086-7_0_4_line_39 | NAYY 4x150 SE | 38 | 40 | 0.016106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1086-7_0_4_line_40 | NAYY 4x150 SE | 39 | 41 | 0.026221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1086-7_0_4_line_41 | NAYY 4x150 SE | 40 | 42 | 0.018767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1086-7_0_4_line_42 | NAYY 4x150 SE | 41 | 43 | 0.0039825 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1086-7_0_4_line_43 | NAYY 4x150 SE | 42 | 50 | 0.01468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1086-7_0_4_line_44 | NAYY 4x150 SE | 42 | 46 | 0.0086096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1086-7_0_4_line_45 | NAYY 4x150 SE | 43 | 44 | 0.009823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1086-7_0_4_line_46 | NAYY 4x150 SE | 45 | 46 | 0.021905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1086-7_0_4_line_47 | NAYY 4x150 SE | 45 | 47 | 0.019183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1086-7_0_4_line_48 | NAYY 4x150 SE | 47 | 48 | 0.040097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1086-7_0_4_line_49 | NAYY 4x150 SE | 47 | 49 | 0.0089611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1086-7_0_4_line_50 | NAYY 4x150 SE | 49 | 51 | 0.016083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1086-7_0_4_line_51 | NAYY 4x150 SE | 50 | 52 | 0.02584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1086-7_0_4_line_52 | NAYY 4x150 SE | 51 | 53 | 0.026546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1086-7_0_4_line_53 | NAYY 4x150 SE | 52 | 58 | 0.0032853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1086-7_0_4_line_54 | NAYY 4x150 SE | 53 | 56 | 0.029927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1086-7_0_4_line_55 | NAYY 4x150 SE | 54 | 55 | 0.019177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1086-7_0_4_line_56 | NAYY 4x150 SE | 54 | 56 | 0.0069852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1086-7_0_4_line_57 | NAYY 4x150 SE | 57 | 58 | 0.023231 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1086-7_0_4_trafo_25 | 0.25 MVA 20/0.4 kV | 59 | 23 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2646163.8568 | 1219658.9374 | 2646182.5506 | 1219664.2187
1 | 2646228.276 | 1219847.061 | 2646182.5506 | 1219664.2187
2 | 2646163.8568 | 1219658.9374 | 2646171.1344 | 1219558.967
3 | 2646228.276 | 1219847.061 | 2646244.4579 | 1219845.4633 | 2646265.8344 | 1219845.229 | 2646273.0043 | 1219845.3593
4 | 2646228.276 | 1219847.061 | 2646214.888 | 1219852.3715 | 2646202.3568 | 1219857.0062
5 | 2646171.1344 | 1219558.967 | 2646320.8387 | 1219593.9837
6 | 2646295.2308 | 1219847.7402 | 2646290.4 | 1219845.6755 | 2646273.0043 | 1219845.3593
7 | 2646050.9762 | 1220106.823 | 2646044.7114 | 1220054.2842
8 | 2646041.8201 | 1220029.9949 | 2646043.3875 | 1220043.1816 | 2646044.7114 | 1220054.2842
9 | 2646050.9762 | 1220106.823 | 2646075.6354 | 1220100.2362
10 | 2646112.5095 | 1219999.0671 | 2646041.8201 | 1220029.9949
11 | 2646079.8023 | 1220099.1232 | 2646075.6354 | 1220100.2362
12 | 2646112.5095 | 1219999.0671 | 2646127.6982 | 1219991.4244 | 2646139.1718 | 1219986.3657
13 | 2646112.5095 | 1219999.0671 | 2646119.2623 | 1220010.8764
14 | 2646119.2623 | 1220010.8764 | 2646122.9967 | 1220017.4072
15 | 2646131.3023 | 1220031.9321 | 2646122.9967 | 1220017.4072
16 | 2646143.4191 | 1220053.1222 | 2646141.3781 | 1220049.553
17 | 2646143.4191 | 1220053.1222 | 2646150.3266 | 1220065.2022
18 | 2646133.9003 | 1220036.4756 | 2646141.3781 | 1220049.553
19 | 2646155.6673 | 1220074.542 | 2646150.3266 | 1220065.2022
20 | 2646139.1718 | 1219986.3657 | 2646160.9897 | 1220023.1123
21 | 2646166.6929 | 1219978.4073 | 2646162.8812 | 1219977.7774 | 2646155.6781 | 1219979.078 | 2646139.1718 | 1219986.3657
22 | 2646131.3023 | 1220031.9321 | 2646133.9003 | 1220036.4756
23 | 2646166.6929 | 1219978.4073 | 2646169.6077 | 1219980.2198 | 2646173.1803 | 1219984.2722 | 2646190.5073 | 1220023.808 | 2646194.5307 | 1220029.4203
24 | 2646223.4024 | 1219979.1154 | 2646219.913 | 1219970.3703
25 | 2646213.6174 | 1219954.3706 | 2646215.0982 | 1219958.3036 | 2646219.913 | 1219970.3703
26 | 2646229.9899 | 1220018.3107 | 2646233.2837 | 1220009.4087 | 2646232.7378 | 1220002.5114 | 2646223.4024 | 1219979.1154
27 | 2646213.6174 | 1219954.3706 | 2646208.2225 | 1219940.042
28 | 2646229.9899 | 1220018.3107 | 2646226.099 | 1220021.0489 | 2646209.0714 | 1220029.2115
29 | 2646280.1456 | 1219972.1165 | 2646274.4497 | 1219979.6324 | 2646264.9884 | 1219989.3537 | 2646247.995 | 1220004.6422 | 2646240.3711 | 1220010.2975 | 2646229.9899 | 1220018.3107
30 | 2646202.1804 | 1219918.6685 | 2646204.3926 | 1219929.8701 | 2646208.2225 | 1219940.042
31 | 2646194.5307 | 1220029.4203 | 2646199.0676 | 1220031.4345 | 2646204.8051 | 1220031.2566 | 2646209.0714 | 1220029.2115
32 | 2646280.1456 | 1219972.1165 | 2646290.4906 | 1219962.9246 | 2646302.8075 | 1219955.7169
33 | 2646321.7648 | 1219944.6232 | 2646302.8075 | 1219955.7169
34 | 2646321.7648 | 1219944.6232 | 2646312.7999 | 1219936.2811
35 | 2646321.7648 | 1219944.6232 | 2646334.8625 | 1219936.3031
36 | 2646316.1511 | 1219864.2842 | 2646311.8868 | 1219859.5619 | 2646302.349 | 1219850.7825 | 2646295.2308 | 1219847.7402
37 | 2646316.1511 | 1219864.2842 | 2646319.3713 | 1219867.8504
38 | 2646312.7999 | 1219936.2811 | 2646307.7415 | 1219931.5741
39 | 2646334.8625 | 1219936.3031 | 2646348.4577 | 1219927.667
40 | 2646290.9241 | 1219911.5991 | 2646291.7725 | 1219913.1713 | 2646301.8246 | 1219926.0682 | 2646307.7415 | 1219931.5741
41 | 2646364.2988 | 1219917.6042 | 2646348.4577 | 1219927.667
42 | 2646290.9241 | 1219911.5991 | 2646289.0326 | 1219908.0944
43 | 2646364.2988 | 1219917.6042 | 2646354.4607 | 1219906.7092
44 | 2646364.2988 | 1219917.6042 | 2646371.311 | 1219912.6087
45 | 2646284.3674 | 1219899.4499 | 2646289.0326 | 1219908.0944
46 | 2646389.1521 | 1219899.8988 | 2646371.311 | 1219912.6087
47 | 2646404.7759 | 1219888.7684 | 2646389.1521 | 1219899.8988
48 | 2646404.7759 | 1219888.7684 | 2646428.4953 | 1219921.0974
49 | 2646404.7759 | 1219888.7684 | 2646399.0481 | 1219881.8768
50 | 2646388.7681 | 1219869.508 | 2646399.0481 | 1219881.8768
51 | 2646337.1427 | 1219887.5308 | 2646354.4607 | 1219906.7092
52 | 2646388.7681 | 1219869.508 | 2646383.3291 | 1219862.9638 | 2646371.4955 | 1219849.3514
53 | 2646334.9409 | 1219885.0925 | 2646337.1427 | 1219887.5308
54 | 2646351.4062 | 1219827.1869 | 2646358.4666 | 1219834.3643 | 2646371.4955 | 1219849.3514
55 | 2646346.5077 | 1219822.2072 | 2646333.0596 | 1219808.5364
56 | 2646346.5077 | 1219822.2072 | 2646351.4062 | 1219827.1869
57 | 2646334.9409 | 1219885.0925 | 2646319.3713 | 1219867.8504

## bus_geodata
| x | y | coords
0 | 2646182.5506 | 1219664.2187
1 | 2646163.8568 | 1219658.9374
2 | 2646228.276 | 1219847.061
3 | 2646171.1344 | 1219558.967
4 | 2646273.0043 | 1219845.3593
5 | 2646202.3568 | 1219857.0062
6 | 2646320.8387 | 1219593.9837
7 | 2646044.7114 | 1220054.2842
8 | 2646050.9762 | 1220106.823
9 | 2646041.8201 | 1220029.9949
10 | 2646075.6354 | 1220100.2362
11 | 2646112.5095 | 1219999.0671
12 | 2646119.2623 | 1220010.8764
13 | 2646122.9967 | 1220017.4072
14 | 2646079.8023 | 1220099.1232
15 | 2646143.4191 | 1220053.1222
16 | 2646141.3781 | 1220049.553
17 | 2646150.3266 | 1220065.2022
18 | 2646139.1718 | 1219986.3657
19 | 2646155.6673 | 1220074.542
20 | 2646133.9003 | 1220036.4756
21 | 2646131.3023 | 1220031.9321
22 | 2646160.9897 | 1220023.1123
23 | 2646166.6929 | 1219978.4073
24 | 2646219.913 | 1219970.3703
25 | 2646223.4024 | 1219979.1154
26 | 2646213.6174 | 1219954.3706
27 | 2646229.9899 | 1220018.3107
28 | 2646208.2225 | 1219940.042
29 | 2646209.0714 | 1220029.2115
30 | 2646280.1456 | 1219972.1165
31 | 2646202.1804 | 1219918.6685
32 | 2646194.5307 | 1220029.4203
33 | 2646302.8075 | 1219955.7169
34 | 2646321.7648 | 1219944.6232
35 | 2646295.2308 | 1219847.7402
36 | 2646316.1511 | 1219864.2842
37 | 2646312.7999 | 1219936.2811
38 | 2646334.8625 | 1219936.3031
39 | 2646307.7415 | 1219931.5741
40 | 2646348.4577 | 1219927.667
41 | 2646290.9241 | 1219911.5991
42 | 2646364.2988 | 1219917.6042
43 | 2646289.0326 | 1219908.0944
44 | 2646284.3674 | 1219899.4499
45 | 2646389.1521 | 1219899.8988
46 | 2646371.311 | 1219912.6087
47 | 2646404.7759 | 1219888.7684
48 | 2646428.4953 | 1219921.0974
49 | 2646399.0481 | 1219881.8768
50 | 2646354.4607 | 1219906.7092
51 | 2646388.7681 | 1219869.508
52 | 2646337.1427 | 1219887.5308
53 | 2646371.4955 | 1219849.3514
54 | 2646346.5077 | 1219822.2072
55 | 2646333.0596 | 1219808.5364
56 | 2646351.4062 | 1219827.1869
57 | 2646319.3713 | 1219867.8504
58 | 2646334.9409 | 1219885.0925
59 | 2646139.1718 | 1219986.3657

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97361 | -0.18603 | 0.0022853 | 0.00057276
1 | 0.97344 | -0.18723 | 0 | 0
2 | 0.97585 | -0.16987 | 0 | 0
3 | 0.97258 | -0.19342 | 0.0014599 | 0.0003659
4 | 0.97661 | -0.16441 | 0.0039752 | 0.00099627
5 | 0.97571 | -0.17088 | 0.0034619 | 0.00086764
6 | 0.9716 | -0.20055 | 0.0043814 | 0.0010981
7 | 0.98553 | -0.101 | 0.057395 | 0.014385
8 | 0.98097 | -0.13331 | 0 | 0
9 | 0.9876 | -0.086388 | 0 | 0
10 | 0.97878 | -0.149 | 0.0022992 | 0.00057624
11 | 0.99413 | -0.040678 | 0 | 0
12 | 0.99373 | -0.043509 | 0.001923 | 0.00048194
13 | 0.99353 | -0.04493 | 0.0020461 | 0.00051279
14 | 0.97842 | -0.15156 | 0.056845 | 0.014247
15 | 0.99271 | -0.050674 | 0.003898 | 0.00097693
16 | 0.99277 | -0.050289 | 0.0023818 | 0.00059694
17 | 0.9926 | -0.051429 | 0.0034945 | 0.00087581
18 | 0.99706 | -0.020324 | 0 | 0
19 | 0.99258 | -0.051632 | 0.001862 | 0.00046666
20 | 0.99302 | -0.048514 | 0.0028758 | 0.00072074
21 | 0.99313 | -0.047745 | 0.0021148 | 0.00053002
22 | 0.99693 | -0.021233 | 0.0021185 | 0.00053095
23 | 1 | 0 | -0.24508 | -0.061734
24 | 0.992 | -0.055542 | 0.0021065 | 0.00052794
25 | 0.99216 | -0.054452 | 0.0019989 | 0.00050097
26 | 0.99177 | -0.057167 | 0.0027465 | 0.00068833
27 | 0.99296 | -0.048795 | 0 | 0
28 | 0.99163 | -0.058187 | 0.0028327 | 0.00070995
29 | 0.99459 | -0.037421 | 0.0020166 | 0.00050541
30 | 0.9889 | -0.077206 | 0 | 0
31 | 0.99151 | -0.059031 | 0.00373 | 0.00093483
32 | 0.99568 | -0.029858 | 0.0038944 | 0.00097602
33 | 0.98723 | -0.088956 | 0.0019884 | 0.00049835
34 | 0.98468 | -0.10695 | 0 | 0
35 | 0.97713 | -0.16071 | 0.0024904 | 0.00062415
36 | 0.97784 | -0.15559 | 0.0019265 | 0.00048283
37 | 0.98439 | -0.10898 | 0.0021034 | 0.00052717
38 | 0.98324 | -0.11712 | 0.0056771 | 0.0014228
39 | 0.98425 | -0.10998 | 0.0021034 | 0.00052717
40 | 0.98188 | -0.12677 | 0.0030793 | 0.00077174
41 | 0.9838 | -0.11321 | 0.0026306 | 0.0006593
42 | 0.98038 | -0.13745 | 0 | 0
43 | 0.98375 | -0.11359 | 0.0058941 | 0.0014772
44 | 0.9837 | -0.11394 | 0.0034099 | 0.00085459
45 | 0.97943 | -0.14424 | 0.0047541 | 0.0011915
46 | 0.98006 | -0.13978 | 0.0065364 | 0.0016382
47 | 0.97902 | -0.14719 | 0 | 0
48 | 0.97896 | -0.14764 | 0.0010729 | 0.0002689
49 | 0.97884 | -0.14847 | 0.002066 | 0.0005178
50 | 0.97977 | -0.14184 | 0.0035363 | 0.00088629
51 | 0.97857 | -0.15042 | 0.0016393 | 0.00041085
52 | 0.97882 | -0.14863 | 0.0018529 | 0.00046438
53 | 0.97818 | -0.15319 | 0.001643 | 0.00041179
54 | 0.97775 | -0.15625 | 0.0042686 | 0.0010698
55 | 0.9777 | -0.15661 | 0.0018192 | 0.00045593
56 | 0.97782 | -0.15581 | 0.0022724 | 0.00056952
57 | 0.97798 | -0.15459 | 0.0012678 | 0.00031774
58 | 0.97871 | -0.14943 | 0.002082 | 0.00052179
59 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0058517 | 0.0014646 | -0.0058507 | -0.0014644 | 9.6939e-07 | 1.3131e-07 | 0.0089427 | 0.0089428 | 0.0089428 | 0.97361 | -0.18603 | 0.97344 | -0.18723 | 3.3121
1 | -0.008137 | -0.0020373 | 0.0081552 | 0.002042 | 1.8186e-05 | 4.6453e-06 | 0.012435 | 0.012435 | 0.012435 | 0.97361 | -0.18603 | 0.97585 | -0.16987 | 4.6057
2 | 0.0058507 | 0.0014644 | -0.0058457 | -0.0014637 | 5.0023e-06 | 6.7897e-07 | 0.0089428 | 0.0089432 | 0.0089432 | 0.97344 | -0.18723 | 0.97258 | -0.19342 | 3.3123
3 | -0.011618 | -0.0029094 | 0.011626 | 0.0029123 | 8.7739e-06 | 2.8143e-06 | 0.017714 | 0.017714 | 0.017714 | 0.97585 | -0.16987 | 0.97661 | -0.16441 | 6.5608
4 | 0.0034624 | 0.00086748 | -0.0034619 | -0.00086764 | 4.829e-07 | -1.6108e-07 | 0.0052795 | 0.0052796 | 0.0052796 | 0.97585 | -0.16987 | 0.97571 | -0.17088 | 1.9554
5 | 0.0043858 | 0.0010978 | -0.0043814 | -0.0010981 | 4.3194e-06 | -2.4472e-07 | 0.0067096 | 0.0067103 | 0.0067103 | 0.97258 | -0.19342 | 0.9716 | -0.20055 | 2.4853
6 | -0.015602 | -0.0039085 | 0.01561 | 0.0039113 | 7.9869e-06 | 2.7883e-06 | 0.023771 | 0.023771 | 0.023771 | 0.97661 | -0.16441 | 0.97713 | -0.16071 | 8.804
7 | 0.05956 | 0.014982 | -0.059293 | -0.01488 | 0.00026712 | 0.00010207 | 0.089947 | 0.089947 | 0.089947 | 0.98553 | -0.101 | 0.98097 | -0.13331 | 33.3136
8 | -0.11696 | -0.029366 | 0.11719 | 0.029457 | 0.00023803 | 9.0925e-05 | 0.17661 | 0.1766 | 0.17661 | 0.98553 | -0.101 | 0.9876 | -0.086388 | 32.7046
9 | 0.059293 | 0.01488 | -0.059164 | -0.014831 | 0.00012885 | 4.9238e-05 | 0.089947 | 0.089947 | 0.089947 | 0.98097 | -0.13331 | 0.97878 | -0.149 | 33.3137
10 | -0.11719 | -0.029457 | 0.11794 | 0.029744 | 0.00075084 | 0.00028679 | 0.1766 | 0.1766 | 0.1766 | 0.9876 | -0.086388 | 0.99413 | -0.040678 | 32.7046
11 | 0.056865 | 0.014254 | -0.056845 | -0.014247 | 2.0114e-05 | 7.6821e-06 | 0.086451 | 0.086451 | 0.086451 | 0.97878 | -0.149 | 0.97842 | -0.15156 | 32.0191
12 | -0.13856 | -0.034914 | 0.13896 | 0.035065 | 0.00039581 | 0.00015147 | 0.20747 | 0.20747 | 0.20747 | 0.99413 | -0.040678 | 0.99706 | -0.020324 | 38.4201
13 | 0.02062 | 0.0051699 | -0.020612 | -0.0051669 | 8.0865e-06 | 2.9339e-06 | 0.030864 | 0.030864 | 0.030864 | 0.99413 | -0.040678 | 0.99373 | -0.043509 | 11.4313
14 | 0.018689 | 0.004685 | -0.018685 | -0.0046837 | 3.6765e-06 | 1.3166e-06 | 0.027985 | 0.027985 | 0.027985 | 0.99373 | -0.043509 | 0.99353 | -0.04493 | 10.3648
15 | 0.016639 | 0.0041709 | -0.016632 | -0.0041686 | 6.4841e-06 | 2.2773e-06 | 0.024921 | 0.024921 | 0.024921 | 0.99353 | -0.04493 | 0.99313 | -0.047745 | 9.2299
16 | -0.0092551 | -0.0023193 | 0.0092556 | 0.0023195 | 4.9376e-07 | 1.3675e-07 | 0.013873 | 0.013873 | 0.013873 | 0.99271 | -0.050674 | 0.99277 | -0.050289 | 5.1381
17 | 0.0053571 | 0.0013424 | -0.0053566 | -0.0013424 | 5.599e-07 | 3.5457e-08 | 0.00803 | 0.00803 | 0.00803 | 0.99271 | -0.050674 | 0.9926 | -0.051429 | 2.9741
18 | -0.011637 | -0.0029164 | 0.01164 | 0.0029173 | 2.86e-06 | 9.0517e-07 | 0.017443 | 0.017443 | 0.017443 | 0.99277 | -0.050289 | 0.99302 | -0.048514 | 6.4603
19 | 0.001862 | 0.00046654 | -0.001862 | -0.00046666 | 5.2311e-08 | -1.1895e-07 | 0.0027913 | 0.0027914 | 0.0027914 | 0.9926 | -0.051429 | 0.99258 | -0.051632 | 1.0339
20 | 0.0021188 | 0.00053049 | -0.0021185 | -0.00053095 | 2.6645e-07 | -4.5446e-07 | 0.0031619 | 0.0031621 | 0.0031621 | 0.99706 | -0.020324 | 0.99693 | -0.021233 | 1.1711
21 | -0.14108 | -0.035596 | 0.14148 | 0.03575 | 0.0004035 | 0.00015443 | 0.21063 | 0.21063 | 0.21063 | 0.99706 | -0.020324 | 1 | 0 | 39.0056
22 | -0.014516 | -0.003638 | 0.014518 | 0.0036386 | 1.5453e-06 | 5.2662e-07 | 0.021752 | 0.021752 | 0.021752 | 0.99302 | -0.048514 | 0.99313 | -0.047745 | 8.0563
23 | 0.10279 | 0.025984 | -0.10236 | -0.02582 | 0.00043044 | 0.00016401 | 0.15304 | 0.15304 | 0.15304 | 1 | 0 | 0.99568 | -0.029858 | 28.3403
24 | -0.011419 | -0.0028617 | 0.011421 | 0.0028622 | 1.7238e-06 | 5.4142e-07 | 0.017129 | 0.017129 | 0.017129 | 0.992 | -0.055542 | 0.99216 | -0.054452 | 6.344
25 | 0.0093127 | 0.0023337 | -0.0093106 | -0.0023331 | 2.0937e-06 | 5.8332e-07 | 0.013969 | 0.013969 | 0.013969 | 0.992 | -0.055542 | 0.99177 | -0.057167 | 5.1737
26 | -0.01342 | -0.0033632 | 0.01343 | 0.0033667 | 1.0515e-05 | 3.5067e-06 | 0.020127 | 0.020126 | 0.020127 | 0.99216 | -0.054452 | 0.99296 | -0.048795 | 7.4543
27 | 0.0065641 | 0.0016448 | -0.0065632 | -0.0016447 | 9.2664e-07 | 1.5886e-07 | 0.0098484 | 0.0098485 | 0.0098485 | 0.99177 | -0.057167 | 0.99163 | -0.058187 | 3.6476
28 | -0.096195 | -0.02424 | 0.096348 | 0.024299 | 0.00015337 | 5.8377e-05 | 0.1442 | 0.1442 | 0.1442 | 0.99296 | -0.048795 | 0.99459 | -0.037421 | 26.7039
29 | 0.082765 | 0.020874 | -0.082436 | -0.020749 | 0.00032834 | 0.00012452 | 0.12407 | 0.12408 | 0.12408 | 0.99296 | -0.048795 | 0.9889 | -0.077206 | 22.9769
30 | 0.0037305 | 0.00093471 | -0.00373 | -0.00093483 | 4.3578e-07 | -1.1987e-07 | 0.0055977 | 0.0055979 | 0.0055979 | 0.99163 | -0.058187 | 0.99151 | -0.059031 | 2.0733
31 | -0.098365 | -0.024804 | 0.098469 | 0.024844 | 0.00010437 | 3.9743e-05 | 0.14722 | 0.14722 | 0.14722 | 0.99459 | -0.037421 | 0.99568 | -0.029858 | 27.2626
32 | 0.082436 | 0.020749 | -0.082301 | -0.020698 | 0.00013501 | 5.1208e-05 | 0.12408 | 0.12408 | 0.12408 | 0.9889 | -0.077206 | 0.98723 | -0.088956 | 22.9769
33 | 0.080313 | 0.020199 | -0.080112 | -0.020122 | 0.00020093 | 7.7001e-05 | 0.12108 | 0.12108 | 0.12108 | 0.98723 | -0.088956 | 0.98468 | -0.10695 | 44.8439
34 | 0.016154 | 0.0040495 | -0.016149 | -0.0040479 | 4.5537e-06 | 1.5957e-06 | 0.024412 | 0.024412 | 0.024412 | 0.98468 | -0.10695 | 0.98439 | -0.10898 | 9.0414
35 | 0.063958 | 0.016073 | -0.063868 | -0.016038 | 9.0478e-05 | 3.4602e-05 | 0.096667 | 0.096667 | 0.096667 | 0.98468 | -0.10695 | 0.98324 | -0.11712 | 35.8026
36 | -0.0181 | -0.0045355 | 0.018113 | 0.0045401 | 1.2832e-05 | 4.5959e-06 | 0.027563 | 0.027563 | 0.027563 | 0.97713 | -0.16071 | 0.97784 | -0.15559 | 10.2086
37 | -0.020039 | -0.0050229 | 0.020042 | 0.0050239 | 2.7882e-06 | 1.0121e-06 | 0.030495 | 0.030495 | 0.030495 | 0.97784 | -0.15559 | 0.97798 | -0.15459 | 11.2943
38 | 0.014046 | 0.0035207 | -0.014044 | -0.00352 | 1.9437e-06 | 6.5974e-07 | 0.021232 | 0.021232 | 0.021232 | 0.98439 | -0.10898 | 0.98425 | -0.10998 | 7.8637
39 | 0.05819 | 0.014616 | -0.058112 | -0.014586 | 7.7963e-05 | 2.9782e-05 | 0.088075 | 0.088075 | 0.088075 | 0.98324 | -0.11712 | 0.98188 | -0.12677 | 32.6205
40 | 0.011941 | 0.0029929 | -0.011935 | -0.0029912 | 5.3319e-06 | 1.7176e-06 | 0.018052 | 0.018052 | 0.018052 | 0.98425 | -0.10998 | 0.9838 | -0.11321 | 6.686
41 | 0.055033 | 0.013814 | -0.054952 | -0.013783 | 8.1472e-05 | 3.1098e-05 | 0.083409 | 0.083409 | 0.083409 | 0.98188 | -0.12677 | 0.98038 | -0.13745 | 30.8922
42 | 0.0093046 | 0.0023319 | -0.0093041 | -0.0023317 | 4.9219e-07 | 1.3874e-07 | 0.014073 | 0.014073 | 0.014073 | 0.9838 | -0.11321 | 0.98375 | -0.11359 | 5.2124
43 | 0.02884 | 0.007236 | -0.028823 | -0.0072294 | 1.7554e-05 | 6.5665e-06 | 0.043776 | 0.043776 | 0.043776 | 0.98038 | -0.13745 | 0.97977 | -0.14184 | 16.2134
44 | 0.026112 | 0.006547 | -0.026103 | -0.0065439 | 8.4388e-06 | 3.1372e-06 | 0.039633 | 0.039633 | 0.039633 | 0.98038 | -0.13745 | 0.98006 | -0.13978 | 14.6789
45 | 0.00341 | 0.00085453 | -0.0034099 | -0.00085459 | 1.6308e-07 | -6.1988e-08 | 0.005158 | 0.005158 | 0.005158 | 0.98375 | -0.11359 | 0.9837 | -0.11394 | 1.9104
46 | -0.019555 | -0.0049013 | 0.019567 | 0.0049057 | 1.2064e-05 | 4.3643e-06 | 0.029709 | 0.029709 | 0.029709 | 0.97943 | -0.14424 | 0.98006 | -0.13978 | 11.0033
47 | 0.014801 | 0.0037098 | -0.014795 | -0.0037077 | 6.0525e-06 | 2.0866e-06 | 0.022486 | 0.022486 | 0.022486 | 0.97943 | -0.14424 | 0.97902 | -0.14719 | 8.3282
48 | 0.001073 | 0.00026842 | -0.0010729 | -0.0002689 | 6.6537e-08 | -4.7858e-07 | 0.0016306 | 0.0016308 | 0.0016308 | 0.97902 | -0.14719 | 0.97896 | -0.14764 | 0.60401
49 | 0.013722 | 0.0034393 | -0.013719 | -0.0034385 | 2.4322e-06 | 8.2278e-07 | 0.020856 | 0.020856 | 0.020856 | 0.97902 | -0.14719 | 0.97884 | -0.14847 | 7.7243
50 | 0.011653 | 0.0029207 | -0.01165 | -0.0029197 | 3.1494e-06 | 1.0092e-06 | 0.017715 | 0.017715 | 0.017715 | 0.97884 | -0.14847 | 0.97857 | -0.15042 | 6.5611
51 | 0.025286 | 0.0063431 | -0.025263 | -0.0063343 | 2.3783e-05 | 8.8223e-06 | 0.038405 | 0.038406 | 0.038406 | 0.97977 | -0.14184 | 0.97882 | -0.14863 | 14.2243
52 | 0.010011 | 0.0025088 | -0.010007 | -0.0025077 | 3.8383e-06 | 1.1429e-06 | 0.015222 | 0.015222 | 0.015222 | 0.97857 | -0.15042 | 0.97818 | -0.15319 | 5.6379
53 | 0.02341 | 0.00587 | -0.023407 | -0.005869 | 2.5965e-06 | 9.5737e-07 | 0.035589 | 0.035589 | 0.035589 | 0.97882 | -0.14863 | 0.97871 | -0.14943 | 13.181
54 | 0.0083637 | 0.0020959 | -0.0083607 | -0.0020951 | 3.0228e-06 | 7.871e-07 | 0.012723 | 0.012723 | 0.012723 | 0.97818 | -0.15319 | 0.97782 | -0.15581 | 4.7122
55 | 0.0018193 | 0.00045572 | -0.0018192 | -0.00045593 | 9.1726e-08 | -2.0522e-07 | 0.0027686 | 0.0027687 | 0.0027687 | 0.97775 | -0.15625 | 0.9777 | -0.15661 | 1.0254
56 | -0.0060879 | -0.0015255 | 0.0060883 | 0.0015256 | 3.7415e-07 | 5.6288e-08 | 0.0092649 | 0.0092649 | 0.0092649 | 0.97775 | -0.15625 | 0.97782 | -0.15581 | 3.4314
57 | -0.02131 | -0.0053416 | 0.021325 | 0.0053472 | 1.524e-05 | 5.5698e-06 | 0.032424 | 0.032423 | 0.032424 | 0.97798 | -0.15459 | 0.97871 | -0.14943 | 12.0087

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24508 | 0.061734

## res_load
| p_mw | q_mvar
0 | 0.0022853 | 0.00057276
1 | 0.0014599 | 0.0003659
2 | 0.0039752 | 0.00099627
3 | 0.0034619 | 0.00086764
4 | 0.0043814 | 0.0010981
5 | 0.057395 | 0.014385
6 | 0.0022992 | 0.00057624
7 | 0.001923 | 0.00048194
8 | 0.0020461 | 0.00051279
9 | 0.056845 | 0.014247
10 | 0.003898 | 0.00097693
11 | 0.0023818 | 0.00059694
12 | 0.0034945 | 0.00087581
13 | 0.001862 | 0.00046666
14 | 0.0028758 | 0.00072074
15 | 0.0021148 | 0.00053002
16 | 0.0021185 | 0.00053095
17 | 0.0021065 | 0.00052794
18 | 0.0019989 | 0.00050097
19 | 0.0027465 | 0.00068833
20 | 0.0028327 | 0.00070995
21 | 0.0020166 | 0.00050541
22 | 0.00373 | 0.00093483
23 | 0.0038944 | 0.00097602
24 | 0.0019884 | 0.00049835
25 | 0.0024904 | 0.00062415
26 | 0.0019265 | 0.00048283
27 | 0.0021034 | 0.00052717
28 | 0.0056771 | 0.0014228
29 | 0.0021034 | 0.00052717
30 | 0.0030793 | 0.00077174
31 | 0.0026306 | 0.0006593
32 | 0.0058941 | 0.0014772
33 | 0.0034099 | 0.00085459
34 | 0.0047541 | 0.0011915
35 | 0.0065364 | 0.0016382
36 | 0.0010729 | 0.0002689
37 | 0.002066 | 0.0005178
38 | 0.0035363 | 0.00088629
39 | 0.0016393 | 0.00041085
40 | 0.0018529 | 0.00046438
41 | 0.001643 | 0.00041179
42 | 0.0042686 | 0.0010698
43 | 0.0018192 | 0.00045593
44 | 0.0022724 | 0.00056952
45 | 0.0012678 | 0.00031774
46 | 0.002082 | 0.00052179

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1