## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1098-13_1_2_node_8 | 0.4 | n |  | TRUE
1 | bus_LV_1098-13_1_2_node_9 | 0.4 | n |  | TRUE
2 | bus_LV_1098-13_1_2_node_11 | 0.4 | n |  | TRUE
3 | bus_LV_1098-13_1_2_node_70 | 0.4 | n |  | TRUE
4 | bus_LV_1098-13_1_2_node_71 | 0.4 | n |  | TRUE
5 | bus_LV_1098-13_1_2_node_64 | 0.4 | n |  | TRUE
6 | bus_LV_1098-13_1_2_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_1098-13_1_2_node_62 | 0.4 | n |  | TRUE
8 | bus_LV_1098-13_1_2_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1098-13_1_2_node_66 | 0.4 | n |  | TRUE
10 | bus_LV_1098-13_1_2_node_81 | 0.4 | n |  | TRUE
11 | bus_LV_1098-13_1_2_node_14 | 0.4 | n |  | TRUE
12 | bus_LV_1098-13_1_2_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_1098-13_1_2_node_63 | 0.4 | n |  | TRUE
14 | bus_LV_1098-13_1_2_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1098-13_1_2_node_80 | 0.4 | n |  | TRUE
16 | bus_LV_1098-13_1_2_node_77 | 0.4 | n |  | TRUE
17 | bus_LV_1098-13_1_2_node_72 | 0.4 | n |  | TRUE
18 | bus_LV_1098-13_1_2_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1098-13_1_2_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1098-13_1_2_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1098-13_1_2_node_59 | 0.4 | n |  | TRUE
22 | bus_LV_1098-13_1_2_node_69 | 0.4 | n |  | TRUE
23 | bus_LV_1098-13_1_2_node_65 | 0.4 | n |  | TRUE
24 | bus_LV_1098-13_1_2_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_1098-13_1_2_node_68 | 0.4 | n |  | TRUE
26 | bus_LV_1098-13_1_2_node_100 | 0.4 | n |  | TRUE
27 | bus_LV_1098-13_1_2_node_74 | 0.4 | n |  | TRUE
28 | bus_LV_1098-13_1_2_node_75 | 0.4 | n |  | TRUE
29 | bus_LV_1098-13_1_2_node_76 | 0.4 | n |  | TRUE
30 | bus_LV_1098-13_1_2_node_78 | 0.4 | n |  | TRUE
31 | bus_LV_1098-13_1_2_node_79 | 0.4 | n |  | TRUE
32 | bus_LV_1098-13_1_2_node_99 | 0.4 | n |  | TRUE
33 | bus_LV_1098-13_1_2_node_82 | 0.4 | n |  | TRUE
34 | bus_LV_1098-13_1_2_node_83 | 0.4 | n |  | TRUE
35 | bus_LV_1098-13_1_2_node_84 | 0.4 | n |  | TRUE
36 | bus_LV_1098-13_1_2_node_85 | 0.4 | n |  | TRUE
37 | bus_MV_2_1_node_135 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1098-13_1_2_load_8 | 0 | 0.0040512 | 0.0010153 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1098-13_1_2_load_9 | 1 | 0.0023148 | 0.00058014 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1098-13_1_2_load_70 | 3 | 0.00327 | 0.00081954 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1098-13_1_2_load_71 | 4 | 0.0039673 | 0.00099431 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1098-13_1_2_load_64 | 5 | 0.0023148 | 0.00058014 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1098-13_1_2_load_62 | 7 | 0.010905 | 0.0027329 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1098-13_1_2_load_81 | 10 | 0.0018106 | 0.00045378 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1098-13_1_2_load_63 | 13 | 0.0033802 | 0.00084717 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1098-13_1_2_load_80 | 15 | 0.0014527 | 0.00036408 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1098-13_1_2_load_77 | 16 | 0.0035188 | 0.00088189 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1098-13_1_2_load_72 | 17 | 0.0074897 | 0.0018771 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1098-13_1_2_load_20 | 18 | 0.0048452 | 0.0012143 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1098-13_1_2_load_21 | 19 | 0.0085779 | 0.0021498 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1098-13_1_2_load_23 | 20 | 0.0075528 | 0.0018929 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1098-13_1_2_load_59 | 21 | 0.0035762 | 0.00089629 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1098-13_1_2_load_69 | 22 | 0.0024508 | 0.00061423 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1098-13_1_2_load_65 | 23 | 0.0021109 | 0.00052905 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1098-13_1_2_load_67 | 24 | 0.0015376 | 0.00038536 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1098-13_1_2_load_68 | 25 | 0.0015712 | 0.00039378 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1098-13_1_2_load_100 | 26 | 0.0074731 | 0.0018729 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1098-13_1_2_load_74 | 27 | 0.001439 | 0.00036064 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1098-13_1_2_load_75 | 28 | 0.0034989 | 0.0008769 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1098-13_1_2_load_76 | 29 | 0.0034935 | 0.00087554 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1098-13_1_2_load_78 | 30 | 0.0021582 | 0.00054089 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1098-13_1_2_load_79 | 31 | 0.0011199 | 0.00028067 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1098-13_1_2_load_99 | 32 | 0.0026258 | 0.00065808 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1098-13_1_2_load_82 | 33 | 0.0068565 | 0.0017184 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1098-13_1_2_load_83 | 34 | 0.0064496 | 0.0016164 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1098-13_1_2_load_84 | 35 | 0.0068594 | 0.0017191 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1098-13_1_2_load_85 | 36 | 0.0074512 | 0.0018674 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1098-13_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.042772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1098-13_1_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.015731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1098-13_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.058068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1098-13_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.037497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1098-13_1_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.02586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1098-13_1_2_line_5 | NAYY 4x150 SE | 3 | 20 | 0.02832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1098-13_1_2_line_6 | NAYY 4x150 SE | 4 | 26 | 0.024166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1098-13_1_2_line_7 | NAYY 4x150 SE | 5 | 6 | 0.020896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1098-13_1_2_line_8 | NAYY 4x150 SE | 6 | 7 | 0.030905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1098-13_1_2_line_9 | NAYY 4x150 SE | 7 | 13 | 0.035138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1098-13_1_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.088196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1098-13_1_2_line_11 | NAYY 4x150 SE | 8 | 10 | 0.095519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1098-13_1_2_line_12 | NAYY 4x150 SE | 9 | 24 | 0.021064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1098-13_1_2_line_13 | NAYY 4x150 SE | 9 | 23 | 0.017786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1098-13_1_2_line_14 | NAYY 4x150 SE | 10 | 31 | 0.033834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1098-13_1_2_line_15 | NAYY 4x150 SE | 11 | 12 | 0.018678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1098-13_1_2_line_16 | NAYY 4x150 SE | 11 | 13 | 0.01015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1098-13_1_2_line_17 | NAYY 4x150 SE | 12 | 17 | 0.017698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1098-13_1_2_line_18 | NAYY 4x150 SE | 12 | 14 | 0.012721 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1098-13_1_2_line_19 | NAYY 4x150 SE | 14 | 15 | 0.011594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1098-13_1_2_line_20 | NAYY 4x150 SE | 14 | 16 | 0.014281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1098-13_1_2_line_21 | NAYY 4x150 SE | 15 | 32 | 0.028312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1098-13_1_2_line_22 | NAYY 4x150 SE | 15 | 27 | 0.023505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1098-13_1_2_line_23 | NAYY 4x150 SE | 16 | 30 | 0.061851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1098-13_1_2_line_24 | NAYY 4x150 SE | 18 | 19 | 0.26795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1098-13_1_2_line_25 | NAYY 4x150 SE | 19 | 20 | 0.010143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1098-13_1_2_line_26 | NAYY 4x150 SE | 21 | 22 | 0.10006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1098-13_1_2_line_27 | NAYY 4x150 SE | 22 | 25 | 0.053671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1098-13_1_2_line_28 | NAYY 4x150 SE | 24 | 25 | 0.0068288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1098-13_1_2_line_29 | NAYY 4x150 SE | 26 | 36 | 0.003196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1098-13_1_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.00059828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1098-13_1_2_line_31 | NAYY 4x150 SE | 28 | 29 | 0.00059829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1098-13_1_2_line_32 | NAYY 4x150 SE | 30 | 31 | 0.023367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1098-13_1_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.037922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1098-13_1_2_line_34 | NAYY 4x150 SE | 33 | 35 | 0.0011625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1098-13_1_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.033818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1098-13_1_2_trafo_71 | 0.25 MVA 20/0.4 kV | 37 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2652612.0224 | 1214490.023 | 2652574.9402 | 1214511.3384
1 | 2652561.3015 | 1214519.1781 | 2652574.9402 | 1214511.3384
2 | 2652561.3015 | 1214519.1781 | 2652531.733 | 1214469.2024
3 | 2652561.3015 | 1214519.1781 | 2652527.8871 | 1214536.1932
4 | 2652561.3015 | 1214519.1781 | 2652564.7477 | 1214526.2794 | 2652573.1432 | 1214542.1639
5 | 2652517.3122 | 1214444.829 | 2652531.733 | 1214469.2024
6 | 2652527.8871 | 1214536.1932 | 2652519.129 | 1214540.653 | 2652506.4418 | 1214547.3314
7 | 2652582.9073 | 1214560.6379 | 2652573.1432 | 1214542.1639
8 | 2652582.9073 | 1214560.6379 | 2652577.1474 | 1214558.408 | 2652561.6565 | 1214559.8946 | 2652555.4389 | 1214563.0639 | 2652553.5266 | 1214564.1256
9 | 2652553.5266 | 1214564.1256 | 2652546.4103 | 1214568.0763 | 2652528.0947 | 1214577.265 | 2652524.4397 | 1214582.6487
10 | 2652663.2853 | 1214559.3016 | 2652711.3442 | 1214529.2191 | 2652713.5821 | 1214526.9264 | 2652715.224 | 1214524.1837 | 2652716.1776 | 1214521.1347 | 2652716.3996 | 1214518.3572 | 2652716.0519 | 1214515.5858 | 2652715.1411 | 1214512.954 | 2652708.64 | 1214500.9338
11 | 2652708.64 | 1214500.9338 | 2652693.7819 | 1214511.5645 | 2652679.7139 | 1214520.4567 | 2652664.194 | 1214527.7907 | 2652648.6579 | 1214533.5237 | 2652625.1593 | 1214546.5788
12 | 2652663.2853 | 1214559.3016 | 2652653.7208 | 1214564.7872 | 2652644.7005 | 1214569.1907
13 | 2652663.2853 | 1214559.3016 | 2652668.8958 | 1214565.5438 | 2652676.3624 | 1214568.8561 | 2652677.5641 | 1214568.6205
14 | 2652595.5835 | 1214563.0102 | 2652625.1593 | 1214546.5788
15 | 2652518.7383 | 1214591.0464 | 2652501.6515 | 1214598.7006
16 | 2652518.7383 | 1214591.0464 | 2652524.4397 | 1214582.6487
17 | 2652501.6515 | 1214598.7006 | 2652486.6373 | 1214608.0702
18 | 2652501.6515 | 1214598.7006 | 2652505.0303 | 1214604.8229 | 2652507.7961 | 1214609.8392
19 | 2652507.7961 | 1214609.8392 | 2652497.4576 | 1214615.0862
20 | 2652507.7961 | 1214609.8392 | 2652520.4085 | 1214603.1409
21 | 2652497.4576 | 1214615.0862 | 2652472.2108 | 1214627.8997
22 | 2652497.4576 | 1214615.0862 | 2652495.1517 | 1214638.4778
23 | 2652520.4085 | 1214603.1409 | 2652575.0337 | 1214574.1302
24 | 2652357.1342 | 1214235.5756 | 2652366.976 | 1214231.3077 | 2652377.5665 | 1214241.34 | 2652402.9356 | 1214265.3438 | 2652454.5063 | 1214377.4865 | 2652465.5567 | 1214390.447 | 2652479.1761 | 1214398.0047 | 2652496.1893 | 1214409.1277 | 2652512.1473 | 1214436.0994
25 | 2652512.1473 | 1214436.0994 | 2652517.3122 | 1214444.829
26 | 2652589.5688 | 1214594.0945 | 2652624.9714 | 1214687.6821
27 | 2652589.5688 | 1214594.0945 | 2652637.1005 | 1214572.9009 | 2652638.5639 | 1214572.1865
28 | 2652638.5639 | 1214572.1865 | 2652644.7005 | 1214569.1907
29 | 2652503.6137 | 1214548.8201 | 2652506.4418 | 1214547.3314
30 | 2652495.1517 | 1214638.4778 | 2652494.5898 | 1214638.6832
31 | 2652494.5898 | 1214638.6832 | 2652494.0279 | 1214638.8887
32 | 2652575.0337 | 1214574.1302 | 2652587.1588 | 1214567.6907 | 2652595.5835 | 1214563.0102
33 | 2652473.4989 | 1214566.5355 | 2652441.8165 | 1214587.3761
34 | 2652473.4989 | 1214566.5355 | 2652474.4702 | 1214565.8966
35 | 2652503.6137 | 1214548.8201 | 2652487.6782 | 1214557.2083 | 2652474.4702 | 1214565.8966

## bus_geodata
| x | y | coords
0 | 2652612.0224 | 1214490.023
1 | 2652574.9402 | 1214511.3384
2 | 2652561.3015 | 1214519.1781
3 | 2652531.733 | 1214469.2024
4 | 2652527.8871 | 1214536.1932
5 | 2652573.1432 | 1214542.1639
6 | 2652582.9073 | 1214560.6379
7 | 2652553.5266 | 1214564.1256
8 | 2652708.64 | 1214500.9338
9 | 2652663.2853 | 1214559.3016
10 | 2652625.1593 | 1214546.5788
11 | 2652518.7383 | 1214591.0464
12 | 2652501.6515 | 1214598.7006
13 | 2652524.4397 | 1214582.6487
14 | 2652507.7961 | 1214609.8392
15 | 2652497.4576 | 1214615.0862
16 | 2652520.4085 | 1214603.1409
17 | 2652486.6373 | 1214608.0702
18 | 2652357.1342 | 1214235.5756
19 | 2652512.1473 | 1214436.0994
20 | 2652517.3122 | 1214444.829
21 | 2652624.9714 | 1214687.6821
22 | 2652589.5688 | 1214594.0945
23 | 2652677.5641 | 1214568.6205
24 | 2652644.7005 | 1214569.1907
25 | 2652638.5639 | 1214572.1865
26 | 2652506.4418 | 1214547.3314
27 | 2652495.1517 | 1214638.4778
28 | 2652494.5898 | 1214638.6832
29 | 2652494.0279 | 1214638.8887
30 | 2652575.0337 | 1214574.1302
31 | 2652595.5835 | 1214563.0102
32 | 2652472.2108 | 1214627.8997
33 | 2652473.4989 | 1214566.5355
34 | 2652441.8165 | 1214587.3761
35 | 2652474.4702 | 1214565.8966
36 | 2652503.6137 | 1214548.8201
37 | 2652561.3015 | 1214519.1781

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99489 | -0.035537 | 0.0040512 | 0.0010153
1 | 0.99514 | -0.03379 | 0.0023148 | 0.00058014
2 | 0.99529 | -0.03278 | 0 | 0
3 | 0.99326 | -0.047012 | 0.00327 | 0.00081954
4 | 1 | 0 | -0.12411 | -0.031043
5 | 0.99317 | -0.047538 | 0.0023148 | 0.00058014
6 | 0.99153 | -0.059017 | 0 | 0
7 | 0.98911 | -0.076064 | 0.010905 | 0.0027329
8 | 0.98007 | -0.14025 | 0 | 0
9 | 0.97862 | -0.15059 | 0 | 0
10 | 0.98163 | -0.12907 | 0.0018106 | 0.00045378
11 | 0.98632 | -0.095772 | 0 | 0
12 | 0.98524 | -0.10343 | 0 | 0
13 | 0.98691 | -0.091618 | 0.0033802 | 0.00084717
14 | 0.98464 | -0.10767 | 0 | 0
15 | 0.98443 | -0.10916 | 0.0014527 | 0.00036408
16 | 0.98423 | -0.1106 | 0.0035188 | 0.00088189
17 | 0.98505 | -0.10479 | 0.0074897 | 0.0018771
18 | 0.99035 | -0.067639 | 0.0048452 | 0.0012143
19 | 0.99221 | -0.054418 | 0.0085779 | 0.0021498
20 | 0.99241 | -0.053035 | 0.0075528 | 0.0018929
21 | 0.97727 | -0.16027 | 0.0035762 | 0.00089629
22 | 0.97779 | -0.15652 | 0.0024508 | 0.00061423
23 | 0.97857 | -0.15098 | 0.0021109 | 0.00052905
24 | 0.97834 | -0.1526 | 0.0015376 | 0.00038536
25 | 0.97827 | -0.15314 | 0.0015712 | 0.00039378
26 | 0.99879 | -0.0084753 | 0.0074731 | 0.0018729
27 | 0.98414 | -0.11121 | 0.001439 | 0.00036064
28 | 0.98414 | -0.11125 | 0.0034989 | 0.0008769
29 | 0.98414 | -0.11127 | 0.0034935 | 0.00087554
30 | 0.98276 | -0.12105 | 0.0021582 | 0.00054089
31 | 0.98228 | -0.12449 | 0.0011199 | 0.00028067
32 | 0.98432 | -0.10993 | 0.0026258 | 0.00065808
33 | 0.99767 | -0.016347 | 0.0068565 | 0.0017184
34 | 0.99732 | -0.018801 | 0.0064496 | 0.0016164
35 | 0.99769 | -0.016192 | 0.0068594 | 0.0017191
36 | 0.99866 | -0.0093587 | 0.0074512 | 0.0018674
37 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0040512 | -0.0010153 | 0.0040522 | 0.0010151 | 9.7984e-07 | -1.787e-07 | 0.0060592 | 0.006059 | 0.0060592 | 0.99489 | -0.035537 | 0.99514 | -0.03379 | 2.2441
1 | -0.0063669 | -0.0015953 | 0.0063678 | 0.0015954 | 8.8969e-07 | 1.3778e-07 | 0.0095202 | 0.0095201 | 0.0095202 | 0.99514 | -0.03379 | 0.99529 | -0.03278 | 3.526
2 | 0.024323 | 0.0061014 | -0.024275 | -0.0060838 | 4.792e-05 | 1.7678e-05 | 0.036366 | 0.036366 | 0.036366 | 0.99529 | -0.03278 | 0.99326 | -0.047012 | 13.469
3 | -0.087752 | -0.02207 | 0.088155 | 0.022224 | 0.0004029 | 0.00015447 | 0.13122 | 0.13122 | 0.13122 | 0.99529 | -0.03278 | 1 | 0 | 48.6006
4 | 0.057061 | 0.014373 | -0.056944 | -0.014328 | 0.00011751 | 4.4861e-05 | 0.085335 | 0.085336 | 0.085336 | 0.99529 | -0.03278 | 0.99317 | -0.047538 | 31.6058
5 | 0.021005 | 0.0052642 | -0.020987 | -0.0052579 | 1.7499e-05 | 6.364e-06 | 0.031467 | 0.031468 | 0.031468 | 0.99326 | -0.047012 | 0.99241 | -0.053035 | 11.6547
6 | 0.035156 | 0.0088185 | -0.035115 | -0.0088029 | 4.1271e-05 | 1.5557e-05 | 0.052315 | 0.052315 | 0.052315 | 1 | 0 | 0.99879 | -0.0084753 | 19.3761
7 | 0.054629 | 0.013748 | -0.054541 | -0.013714 | 8.739e-05 | 3.3342e-05 | 0.081867 | 0.081868 | 0.081868 | 0.99317 | -0.047538 | 0.99153 | -0.059017 | 30.3213
8 | 0.054541 | 0.013714 | -0.054412 | -0.013665 | 0.00012925 | 4.9314e-05 | 0.081868 | 0.081868 | 0.081868 | 0.99153 | -0.059017 | 0.98911 | -0.076064 | 30.3214
9 | 0.043508 | 0.010932 | -0.043414 | -0.010897 | 9.3962e-05 | 3.5689e-05 | 0.065463 | 0.065463 | 0.065463 | 0.98911 | -0.076064 | 0.98691 | -0.091618 | 24.2456
10 | 0.011271 | 0.0028243 | -0.011255 | -0.0028192 | 1.6116e-05 | 5.0886e-06 | 0.017112 | 0.017112 | 0.017112 | 0.98007 | -0.14025 | 0.97862 | -0.15059 | 6.338
11 | -0.011271 | -0.0028243 | 0.011288 | 0.0028298 | 1.7453e-05 | 5.5071e-06 | 0.017112 | 0.017112 | 0.017112 | 0.98007 | -0.14025 | 0.98163 | -0.12907 | 6.3378
12 | 0.0091436 | 0.0022904 | -0.0091411 | -0.0022897 | 2.5405e-06 | 7.1254e-07 | 0.013903 | 0.013903 | 0.013903 | 0.97862 | -0.15059 | 0.97834 | -0.1526 | 5.1492
13 | 0.0021111 | 0.00052887 | -0.0021109 | -0.00052905 | 1.1435e-07 | -1.7948e-07 | 0.0032098 | 0.0032099 | 0.0032099 | 0.97862 | -0.15059 | 0.97857 | -0.15098 | 1.1889
14 | -0.013099 | -0.0032836 | 0.013107 | 0.0032864 | 8.3239e-06 | 2.7735e-06 | 0.019856 | 0.019856 | 0.019856 | 0.98163 | -0.12907 | 0.98228 | -0.12449 | 7.3542
15 | 0.04001 | 0.010041 | -0.039968 | -0.010024 | 4.2473e-05 | 1.6097e-05 | 0.060367 | 0.060367 | 0.060367 | 0.98632 | -0.095772 | 0.98524 | -0.10343 | 22.358
16 | -0.04001 | -0.010041 | 0.040033 | 0.010049 | 2.3081e-05 | 8.7477e-06 | 0.060367 | 0.060367 | 0.060367 | 0.98632 | -0.095772 | 0.98691 | -0.091618 | 22.358
17 | 0.0074911 | 0.0018774 | -0.0074897 | -0.0018771 | 1.4136e-06 | 3.1836e-07 | 0.011314 | 0.011314 | 0.011314 | 0.98524 | -0.10343 | 0.98505 | -0.10479 | 4.1904
18 | 0.032477 | 0.0081471 | -0.032458 | -0.0081399 | 1.91e-05 | 7.1843e-06 | 0.049053 | 0.049053 | 0.049053 | 0.98524 | -0.10343 | 0.98464 | -0.10767 | 18.1677
19 | 0.012515 | 0.0031365 | -0.012512 | -0.0031356 | 2.5878e-06 | 8.4788e-07 | 0.018913 | 0.018913 | 0.018913 | 0.98464 | -0.10767 | 0.98443 | -0.10916 | 7.0048
20 | 0.019943 | 0.0050035 | -0.019935 | -0.0050005 | 8.095e-06 | 2.9319e-06 | 0.03014 | 0.03014 | 0.03014 | 0.98464 | -0.10767 | 0.98423 | -0.1106 | 11.1629
21 | 0.002626 | 0.00065783 | -0.0026258 | -0.00065808 | 2.7835e-07 | -2.5286e-07 | 0.0039693 | 0.0039694 | 0.0039694 | 0.98443 | -0.10916 | 0.98432 | -0.10993 | 1.4702
22 | 0.0084337 | 0.0021137 | -0.0084313 | -0.0021131 | 2.3836e-06 | 6.1801e-07 | 0.012748 | 0.012748 | 0.012748 | 0.98443 | -0.10916 | 0.98414 | -0.11121 | 4.7215
23 | 0.016416 | 0.0041186 | -0.016392 | -0.0041103 | 2.3776e-05 | 8.3597e-06 | 0.02482 | 0.02482 | 0.02482 | 0.98423 | -0.1106 | 0.98276 | -0.12105 | 9.1927
24 | -0.0048452 | -0.0012143 | 0.0048541 | 0.0012143 | 8.8599e-06 | -4.6568e-08 | 0.0072801 | 0.0072788 | 0.0072801 | 0.99035 | -0.067639 | 0.99221 | -0.054418 | 2.6963
25 | -0.013432 | -0.0033641 | 0.013435 | 0.003365 | 2.568e-06 | 8.5667e-07 | 0.020143 | 0.020143 | 0.020143 | 0.99221 | -0.054418 | 0.99241 | -0.053035 | 7.4604
26 | -0.0035762 | -0.00089629 | 0.0035781 | 0.00089574 | 1.8512e-06 | -5.4241e-07 | 0.0054452 | 0.0054448 | 0.0054452 | 0.97727 | -0.16027 | 0.97779 | -0.15652 | 2.0168
27 | -0.0060289 | -0.00151 | 0.0060317 | 0.0015104 | 2.8188e-06 | 4.1065e-07 | 0.0091744 | 0.0091742 | 0.0091744 | 0.97779 | -0.15652 | 0.97827 | -0.15314 | 3.3979
28 | 0.0076035 | 0.0019043 | -0.0076029 | -0.0019042 | 5.6984e-07 | 1.3343e-07 | 0.011564 | 0.011564 | 0.011564 | 0.97834 | -0.1526 | 0.97827 | -0.15314 | 4.283
29 | 0.027642 | 0.00693 | -0.027638 | -0.0069287 | 3.3823e-06 | 1.2591e-06 | 0.041182 | 0.041182 | 0.041182 | 0.99879 | -0.0084753 | 0.99866 | -0.0093587 | 15.2526
30 | 0.0069924 | 0.0017524 | -0.0069923 | -0.0017524 | 4.1729e-08 | 8.4476e-09 | 0.010572 | 0.010572 | 0.010572 | 0.98414 | -0.11121 | 0.98414 | -0.11125 | 3.9157
31 | 0.0034935 | 0.00087554 | -0.0034935 | -0.00087554 | 1.0416e-08 | -3.5959e-09 | 0.0052821 | 0.0052821 | 0.0052821 | 0.98414 | -0.11125 | 0.98414 | -0.11127 | 1.9563
32 | 0.014234 | 0.0035694 | -0.014227 | -0.0035671 | 6.7729e-06 | 2.3091e-06 | 0.021553 | 0.021553 | 0.021553 | 0.98276 | -0.12105 | 0.98228 | -0.12449 | 7.9825
33 | 0.0064518 | 0.0016168 | -0.0064496 | -0.0016164 | 2.1912e-06 | 3.4775e-07 | 0.0096227 | 0.0096229 | 0.0096229 | 0.99767 | -0.016347 | 0.99732 | -0.018801 | 3.564
34 | -0.013308 | -0.0033352 | 0.013309 | 0.0033353 | 2.8581e-07 | 9.4747e-08 | 0.019849 | 0.019849 | 0.019849 | 0.99767 | -0.016347 | 0.99769 | -0.016192 | 7.3516
35 | -0.020168 | -0.0050544 | 0.020187 | 0.0050613 | 1.9093e-05 | 6.9015e-06 | 0.03008 | 0.03008 | 0.03008 | 0.99769 | -0.016192 | 0.99866 | -0.0093587 | 11.1407

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.12808 | 0.032037

## res_load
| p_mw | q_mvar
0 | 0.0040512 | 0.0010153
1 | 0.0023148 | 0.00058014
2 | 0.00327 | 0.00081954
3 | 0.0039673 | 0.00099431
4 | 0.0023148 | 0.00058014
5 | 0.010905 | 0.0027329
6 | 0.0018106 | 0.00045378
7 | 0.0033802 | 0.00084717
8 | 0.0014527 | 0.00036408
9 | 0.0035188 | 0.00088189
10 | 0.0074897 | 0.0018771
11 | 0.0048452 | 0.0012143
12 | 0.0085779 | 0.0021498
13 | 0.0075528 | 0.0018929
14 | 0.0035762 | 0.00089629
15 | 0.0024508 | 0.00061423
16 | 0.0021109 | 0.00052905
17 | 0.0015376 | 0.00038536
18 | 0.0015712 | 0.00039378
19 | 0.0074731 | 0.0018729
20 | 0.001439 | 0.00036064
21 | 0.0034989 | 0.0008769
22 | 0.0034935 | 0.00087554
23 | 0.0021582 | 0.00054089
24 | 0.0011199 | 0.00028067
25 | 0.0026258 | 0.00065808
26 | 0.0068565 | 0.0017184
27 | 0.0064496 | 0.0016164
28 | 0.0068594 | 0.0017191
29 | 0.0074512 | 0.0018674

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1