## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1098-19_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1098-19_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1098-19_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1098-19_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1098-19_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1098-19_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1098-19_0_2_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1098-19_0_2_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1098-19_0_2_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1098-19_0_2_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1098-19_0_2_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1098-19_0_2_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1098-19_0_2_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1098-19_0_2_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1098-19_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1098-19_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1098-19_0_2_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1098-19_0_2_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1098-19_0_2_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1098-19_0_2_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1098-19_0_2_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1098-19_0_2_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1098-19_0_2_node_30 | 0.4 | n |  | TRUE
23 | bus_LV_1098-19_0_2_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_1098-19_0_2_node_31 | 0.4 | n |  | TRUE
25 | bus_LV_1098-19_0_2_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_1098-19_0_2_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1098-19_0_2_node_21 | 0.4 | n |  | TRUE
28 | bus_LV_1098-19_0_2_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_1098-19_0_2_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1098-19_0_2_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1098-19_0_2_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1098-19_0_2_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_1098-19_0_2_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_1098-19_0_2_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_1098-19_0_2_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_1098-19_0_2_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1098-19_0_2_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_1098-19_0_2_node_37 | 0.4 | n |  | TRUE
39 | bus_LV_1098-19_0_2_node_38 | 0.4 | n |  | TRUE
40 | bus_MV_2_1_node_159 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1098-19_0_2_load_0 | 0 | 0.0014779 | 0.0003704 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1098-19_0_2_load_1 | 1 | 0.0006933 | 0.00017376 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1098-19_0_2_load_3 | 3 | 0.0010748 | 0.00026936 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1098-19_0_2_load_4 | 4 | 0.0048282 | 0.0012101 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1098-19_0_2_load_5 | 5 | 0.0068672 | 0.0017211 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1098-19_0_2_load_7 | 7 | 0.0070704 | 0.001772 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1098-19_0_2_load_8 | 8 | 0.0031575 | 0.00079134 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1098-19_0_2_load_17 | 9 | 0.0044822 | 0.0011233 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1098-19_0_2_load_14 | 10 | 0.0022758 | 0.00057038 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1098-19_0_2_load_15 | 12 | 0.0014016 | 0.00035128 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1098-19_0_2_load_9 | 13 | 0.0040005 | 0.0010026 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1098-19_0_2_load_10 | 14 | 0.0039129 | 0.00098066 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1098-19_0_2_load_12 | 15 | 0.0029106 | 0.00072948 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1098-19_0_2_load_22 | 17 | 0.0016143 | 0.00040459 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1098-19_0_2_load_19 | 18 | 0.0015014 | 0.00037627 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1098-19_0_2_load_23 | 19 | 0.0019904 | 0.00049884 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1098-19_0_2_load_16 | 20 | 0.0028186 | 0.0007064 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1098-19_0_2_load_27 | 21 | 0.0038863 | 0.000974 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1098-19_0_2_load_30 | 22 | 0.00064245 | 0.00016101 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1098-19_0_2_load_25 | 23 | 0.0061428 | 0.0015395 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1098-19_0_2_load_31 | 24 | 0.00064296 | 0.00016114 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1098-19_0_2_load_20 | 26 | 0.001995 | 0.00050001 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1098-19_0_2_load_21 | 27 | 0.0027292 | 0.00068401 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1098-19_0_2_load_40 | 28 | 0.00076051 | 0.0001906 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1098-19_0_2_load_24 | 29 | 0.0035527 | 0.00089039 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1098-19_0_2_load_26 | 30 | 0.0036018 | 0.00090271 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1098-19_0_2_load_28 | 31 | 0.0042346 | 0.0010613 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1098-19_0_2_load_29 | 32 | 0.0032821 | 0.00082258 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1098-19_0_2_load_32 | 33 | 0.0023197 | 0.00058138 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1098-19_0_2_load_33 | 34 | 0.0024227 | 0.00060719 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1098-19_0_2_load_34 | 35 | 0.0043433 | 0.0010885 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1098-19_0_2_load_36 | 37 | 0.0018656 | 0.00046756 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1098-19_0_2_load_37 | 38 | 0.0051347 | 0.0012869 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1098-19_0_2_load_38 | 39 | 0.0043842 | 0.0010988 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 12 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1098-19_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0018431 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1098-19_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.057849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1098-19_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0042012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1098-19_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.011464 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1098-19_0_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.019213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1098-19_0_2_line_5 | NAYY 4x150 SE | 5 | 6 | 0.022284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1098-19_0_2_line_6 | NAYY 4x150 SE | 6 | 7 | 0.030077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1098-19_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.01926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1098-19_0_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.023515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1098-19_0_2_line_9 | NAYY 4x150 SE | 8 | 10 | 0.039354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1098-19_0_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.013683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1098-19_0_2_line_11 | NAYY 4x150 SE | 10 | 12 | 0.02586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1098-19_0_2_line_12 | NAYY 4x150 SE | 11 | 26 | 0.018812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1098-19_0_2_line_13 | NAYY 4x150 SE | 11 | 18 | 0.012062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1098-19_0_2_line_14 | NAYY 4x150 SE | 12 | 20 | 0.028868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1098-19_0_2_line_15 | NAYY 4x150 SE | 13 | 14 | 0.02418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1098-19_0_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.020476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1098-19_0_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.060974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1098-19_0_2_line_18 | NAYY 4x150 SE | 16 | 17 | 0.066489 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1098-19_0_2_line_19 | NAYY 4x150 SE | 16 | 18 | 0.032781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1098-19_0_2_line_20 | NAYY 4x150 SE | 17 | 19 | 0.02501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1098-19_0_2_line_21 | NAYY 4x150 SE | 19 | 29 | 0.0060118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1098-19_0_2_line_22 | NAYY 4x150 SE | 20 | 21 | 0.024774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1098-19_0_2_line_23 | NAYY 4x150 SE | 20 | 22 | 0.032181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1098-19_0_2_line_24 | NAYY 4x150 SE | 21 | 23 | 0.010666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1098-19_0_2_line_25 | NAYY 4x150 SE | 22 | 24 | 0.0074875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1098-19_0_2_line_26 | NAYY 4x150 SE | 23 | 30 | 0.011019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1098-19_0_2_line_27 | NAYY 4x150 SE | 24 | 25 | 0.20488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1098-19_0_2_line_28 | NAYY 4x150 SE | 25 | 39 | 0.074765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1098-19_0_2_line_29 | NAYY 4x150 SE | 26 | 27 | 0.013487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1098-19_0_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.018438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1098-19_0_2_line_31 | NAYY 4x150 SE | 30 | 31 | 0.0135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1098-19_0_2_line_32 | NAYY 4x150 SE | 31 | 32 | 0.023139 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1098-19_0_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.002902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1098-19_0_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.03573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1098-19_0_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.022219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1098-19_0_2_line_36 | NAYY 4x150 SE | 36 | 37 | 0.056738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1098-19_0_2_line_37 | NAYY 4x150 SE | 37 | 38 | 0.0077885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1098-19_0_2_line_38 | NAYY 4x150 SE | 38 | 39 | 0.018066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1098-19_0_2_trafo_15 | 0.25 MVA 20/0.4 kV | 40 | 12 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2652913.9028 | 1215062.3138 | 2652915.7226 | 1215062.6061
1 | 2652856.7445 | 1215053.3985 | 2652909.4121 | 1215061.5926 | 2652913.9028 | 1215062.3138
2 | 2652919.8706 | 1215063.2723 | 2652915.7226 | 1215062.6061
3 | 2652856.7445 | 1215053.3985 | 2652863.4547 | 1215044.1038
4 | 2652863.4547 | 1215044.1038 | 2652874.7009 | 1215028.5259
5 | 2652887.7444 | 1215010.4586 | 2652874.7009 | 1215028.5259
6 | 2652887.7444 | 1215010.4586 | 2652905.1718 | 1214985.9447
7 | 2652887.7444 | 1215010.4586 | 2652904.0736 | 1215020.671
8 | 2652918.7971 | 1214966.7791 | 2652905.1718 | 1214985.9447
9 | 2652940.687 | 1215026.6907 | 2652930.8019 | 1215030.219 | 2652914.2524 | 1215027.0369 | 2652904.0736 | 1215020.671
10 | 2652926.7255 | 1214955.6268 | 2652918.7971 | 1214966.7791
11 | 2652940.687 | 1215026.6907 | 2652956.6047 | 1215021.0091 | 2652963.5892 | 1215015.3991
12 | 2652926.7255 | 1214955.6268 | 2652943.4884 | 1214949.3385 | 2652944.3901 | 1214949.4511
13 | 2652926.7255 | 1214955.6268 | 2652916.5053 | 1214949.2201
14 | 2652963.5892 | 1215015.3991 | 2652983.1914 | 1214999.6546 | 2652986.2506 | 1214997.5273
15 | 2652807.717 | 1214995.8229 | 2652808.978 | 1214995.1404 | 2652829.8197 | 1214986.0297
16 | 2652829.8197 | 1214986.0297 | 2652835.6758 | 1214983.4698 | 2652848.1534 | 1214976.9364
17 | 2652888.7307 | 1214931.8089 | 2652862.7634 | 1214964.6874 | 2652848.6002 | 1214976.7024 | 2652848.1534 | 1214976.9364
18 | 2652888.7307 | 1214931.8089 | 2652907.3746 | 1214904.4021 | 2652922.447 | 1214887.5257 | 2652930.1273 | 1214880.0544
19 | 2652888.7307 | 1214931.8089 | 2652916.5053 | 1214949.2201
20 | 2652930.1273 | 1214880.0544 | 2652948.0543 | 1214862.6153
21 | 2652952.3635 | 1214858.4234 | 2652948.0543 | 1214862.6153
22 | 2653006.5899 | 1214983.3837 | 2652986.2506 | 1214997.5273
23 | 2652986.2506 | 1214997.5273 | 2653003.3242 | 1215024.8061
24 | 2653015.3469 | 1214977.2942 | 2653006.5899 | 1214983.3837
25 | 2653003.3242 | 1215024.8061 | 2653009.4479 | 1215020.4977
26 | 2653015.3469 | 1214977.2942 | 2653024.3934 | 1214971.0034 | 2653024.3934 | 1214971.0034
27 | 2653009.4479 | 1215020.4977 | 2653189.6435 | 1215117.9853
28 | 2653189.6435 | 1215117.9853 | 2653169.7865 | 1215157.8768 | 2653156.9691 | 1215185.2269
29 | 2652944.3901 | 1214949.4511 | 2652957.7732 | 1214951.1227
30 | 2652976.069 | 1214953.4079 | 2652957.7732 | 1214951.1227
31 | 2653027.5554 | 1214957.8792 | 2653024.3934 | 1214971.0034
32 | 2653014.863 | 1214938.5325 | 2653027.5554 | 1214957.8792 | 2653027.5554 | 1214957.8792
33 | 2653154.8425 | 1215299.8886 | 2653157.0732 | 1215298.0322
34 | 2653179.439 | 1215271.6578 | 2653175.6913 | 1215282.5379 | 2653157.0732 | 1215298.0322
35 | 2653186.6753 | 1215250.6499 | 2653179.439 | 1215271.6578
36 | 2653186.6753 | 1215250.6499 | 2653175.1925 | 1215245.6668 | 2653163.228 | 1215236.7881 | 2653155.701 | 1215225.8922 | 2653152.4828 | 1215213.7896 | 2653152.2741 | 1215210.2408
37 | 2653151.8168 | 1215202.4657 | 2653152.2741 | 1215210.2408
38 | 2653151.8168 | 1215202.4657 | 2653151.8168 | 1215202.4657 | 2653154.8848 | 1215189.6743 | 2653156.9691 | 1215185.2269

## bus_geodata
| x | y | coords
0 | 2652913.9028 | 1215062.3138
1 | 2652915.7226 | 1215062.6061
2 | 2652856.7445 | 1215053.3985
3 | 2652919.8706 | 1215063.2723
4 | 2652863.4547 | 1215044.1038
5 | 2652874.7009 | 1215028.5259
6 | 2652887.7444 | 1215010.4586
7 | 2652905.1718 | 1214985.9447
8 | 2652904.0736 | 1215020.671
9 | 2652918.7971 | 1214966.7791
10 | 2652940.687 | 1215026.6907
11 | 2652926.7255 | 1214955.6268
12 | 2652963.5892 | 1215015.3991
13 | 2652807.717 | 1214995.8229
14 | 2652829.8197 | 1214986.0297
15 | 2652848.1534 | 1214976.9364
16 | 2652888.7307 | 1214931.8089
17 | 2652930.1273 | 1214880.0544
18 | 2652916.5053 | 1214949.2201
19 | 2652948.0543 | 1214862.6153
20 | 2652986.2506 | 1214997.5273
21 | 2653006.5899 | 1214983.3837
22 | 2653003.3242 | 1215024.8061
23 | 2653015.3469 | 1214977.2942
24 | 2653009.4479 | 1215020.4977
25 | 2653189.6435 | 1215117.9853
26 | 2652944.3901 | 1214949.4511
27 | 2652957.7732 | 1214951.1227
28 | 2652976.069 | 1214953.4079
29 | 2652952.3635 | 1214858.4234
30 | 2653024.3934 | 1214971.0034
31 | 2653027.5554 | 1214957.8792
32 | 2653014.863 | 1214938.5325
33 | 2653154.8425 | 1215299.8886
34 | 2653157.0732 | 1215298.0322
35 | 2653179.439 | 1215271.6578
36 | 2653186.6753 | 1215250.6499
37 | 2653152.2741 | 1215210.2408
38 | 2653151.8168 | 1215202.4657
39 | 2653156.9691 | 1215185.2269
40 | 2652887.7444 | 1215010.4586

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99234 | -0.053605 | 0.0014779 | 0.0003704
1 | 0.99234 | -0.053638 | 0.0006933 | 0.00017376
2 | 0.99261 | -0.0517 | 0 | 0
3 | 0.99233 | -0.053684 | 0.0010748 | 0.00026936
4 | 0.99266 | -0.051322 | 0.0048282 | 0.0012101
5 | 0.99289 | -0.04975 | 0.0068672 | 0.0017211
6 | 0.99336 | -0.046379 | 0 | 0
7 | 0.99178 | -0.057516 | 0.0070704 | 0.001772
8 | 0.99479 | -0.036359 | 0.0031575 | 0.00079134
9 | 0.99078 | -0.064557 | 0.0044822 | 0.0011233
10 | 0.99788 | -0.014729 | 0.0022758 | 0.00057038
11 | 0.99029 | -0.068036 | 0 | 0
12 | 1 | 0 | -0.10424 | -0.026019
13 | 0.98778 | -0.085837 | 0.0040005 | 0.0010026
14 | 0.98792 | -0.084848 | 0.0039129 | 0.00098066
15 | 0.98815 | -0.08319 | 0.0029106 | 0.00072948
16 | 0.9891 | -0.076447 | 0 | 0
17 | 0.98842 | -0.081309 | 0.0016143 | 0.00040459
18 | 0.98995 | -0.070432 | 0.0015014 | 0.00037627
19 | 0.98822 | -0.082726 | 0.0019904 | 0.00049884
20 | 0.99811 | -0.013214 | 0.0028186 | 0.0007064
21 | 0.99736 | -0.018468 | 0.0038863 | 0.000974
22 | 0.9971 | -0.020249 | 0.00064245 | 0.00016101
23 | 0.99709 | -0.020316 | 0.0061428 | 0.0015395
24 | 0.99687 | -0.021839 | 0.00064296 | 0.00016114
25 | 0.99082 | -0.06428 | 0 | 0
26 | 0.99014 | -0.069087 | 0.001995 | 0.00050001
27 | 0.99008 | -0.069567 | 0.0027292 | 0.00068401
28 | 0.99006 | -0.06971 | 0.00076051 | 0.0001906
29 | 0.98819 | -0.082944 | 0.0035527 | 0.00089039
30 | 0.99692 | -0.021547 | 0.0036018 | 0.00090271
31 | 0.99677 | -0.022567 | 0.0042346 | 0.0010613
32 | 0.99666 | -0.02333 | 0.0032821 | 0.00082258
33 | 0.98677 | -0.092884 | 0.0023197 | 0.00058138
34 | 0.98678 | -0.092815 | 0.0024227 | 0.00060719
35 | 0.98703 | -0.091078 | 0.0043433 | 0.0010885
36 | 0.98732 | -0.08901 | 0 | 0
37 | 0.98806 | -0.083731 | 0.0018656 | 0.00046756
38 | 0.98819 | -0.082858 | 0.0051347 | 0.0012869
39 | 0.98861 | -0.079887 | 0.0043842 | 0.0010988
40 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0017681 | 0.00044305 | -0.0017681 | -0.00044307 | 8.084e-09 | -2.0702e-08 | 0.0026512 | 0.0026512 | 0.0026512 | 0.99234 | -0.053605 | 0.99234 | -0.053638 | 0.98193
1 | -0.003246 | -0.00081345 | 0.0032468 | 0.00081303 | 8.5515e-07 | -4.1866e-07 | 0.0048673 | 0.0048671 | 0.0048673 | 0.99234 | -0.053605 | 0.99261 | -0.0517 | 1.8027
2 | 0.0010748 | 0.00026931 | -0.0010748 | -0.00026936 | 6.8089e-09 | -5.1656e-08 | 0.0016116 | 0.0016116 | 0.0016116 | 0.99234 | -0.053638 | 0.99233 | -0.053684 | 0.5969
3 | -0.0032468 | -0.00081303 | 0.003247 | 0.00081294 | 1.6945e-07 | -8.3016e-08 | 0.0048671 | 0.004867 | 0.0048671 | 0.99261 | -0.0517 | 0.99266 | -0.051322 | 1.8026
4 | -0.0080752 | -0.002023 | 0.008077 | 0.0020234 | 1.7566e-06 | 4.272e-07 | 0.012105 | 0.012105 | 0.012105 | 0.99266 | -0.051322 | 0.99289 | -0.04975 | 4.4832
5 | -0.014944 | -0.0037445 | 0.014951 | 0.0037469 | 6.9746e-06 | 2.3942e-06 | 0.022396 | 0.022396 | 0.022396 | 0.99289 | -0.04975 | 0.99336 | -0.046379 | 8.2949
6 | 0.036659 | 0.0092014 | -0.036602 | -0.00918 | 5.6605e-05 | 2.1382e-05 | 0.054918 | 0.054918 | 0.054918 | 0.99336 | -0.046379 | 0.99178 | -0.057516 | 20.34
7 | -0.05161 | -0.012948 | 0.051682 | 0.012976 | 7.1838e-05 | 2.738e-05 | 0.077314 | 0.077314 | 0.077314 | 0.99336 | -0.046379 | 0.99479 | -0.036359 | 28.6349
8 | 0.029532 | 0.007408 | -0.029503 | -0.0073972 | 2.881e-05 | 1.0778e-05 | 0.04431 | 0.04431 | 0.04431 | 0.99178 | -0.057516 | 0.99078 | -0.064557 | 16.4112
9 | -0.054839 | -0.013767 | 0.055004 | 0.01383 | 0.00016527 | 6.3053e-05 | 0.082037 | 0.082037 | 0.082037 | 0.99479 | -0.036359 | 0.99788 | -0.014729 | 30.3841
10 | 0.025021 | 0.0062739 | -0.025009 | -0.0062694 | 1.2058e-05 | 4.4614e-06 | 0.037579 | 0.037579 | 0.037579 | 0.99078 | -0.064557 | 0.99029 | -0.068036 | 13.918
11 | -0.05728 | -0.0144 | 0.057398 | 0.014445 | 0.00011777 | 4.4958e-05 | 0.08543 | 0.08543 | 0.08543 | 0.99788 | -0.014729 | 1 | 0 | 31.6409
12 | 0.0054858 | 0.0013744 | -0.005485 | -0.0013743 | 7.976e-07 | 6.4769e-08 | 0.0082428 | 0.0082429 | 0.0082429 | 0.99029 | -0.068036 | 0.99014 | -0.069087 | 3.0529
13 | 0.019523 | 0.0048951 | -0.019516 | -0.0048927 | 6.4776e-06 | 2.3362e-06 | 0.029336 | 0.029336 | 0.029336 | 0.99029 | -0.068036 | 0.98995 | -0.070432 | 10.8651
14 | 0.04604 | 0.011574 | -0.045956 | -0.011542 | 8.4578e-05 | 3.2152e-05 | 0.068521 | 0.068521 | 0.068521 | 1 | 0 | 0.99811 | -0.013214 | 25.3782
15 | -0.0040005 | -0.0010026 | 0.0040011 | 0.0010025 | 5.4798e-07 | -9.8799e-08 | 0.0060265 | 0.0060264 | 0.0060265 | 0.98778 | -0.085837 | 0.98792 | -0.084848 | 2.232
16 | -0.007914 | -0.0019832 | 0.0079158 | 0.0019836 | 1.8154e-06 | 4.36e-07 | 0.01192 | 0.01192 | 0.01192 | 0.98792 | -0.084848 | 0.98815 | -0.08319 | 4.4148
17 | -0.010826 | -0.0027131 | 0.010837 | 0.0027162 | 1.0112e-05 | 3.1075e-06 | 0.016303 | 0.016303 | 0.016303 | 0.98815 | -0.08319 | 0.9891 | -0.076447 | 6.0381
18 | 0.0071635 | 0.0017949 | -0.0071586 | -0.0017939 | 4.8185e-06 | 1.0005e-06 | 0.010777 | 0.010777 | 0.010777 | 0.9891 | -0.076447 | 0.98842 | -0.081309 | 3.9915
19 | -0.018 | -0.0045111 | 0.018015 | 0.0045164 | 1.5e-05 | 5.3479e-06 | 0.027079 | 0.027079 | 0.027079 | 0.9891 | -0.076447 | 0.98995 | -0.070432 | 10.0294
20 | 0.0055443 | 0.0013893 | -0.0055432 | -0.0013892 | 1.0872e-06 | 9.7679e-08 | 0.0083466 | 0.0083467 | 0.0083467 | 0.98842 | -0.081309 | 0.98822 | -0.082726 | 3.0914
21 | 0.0035528 | 0.00089036 | -0.0035527 | -0.00089039 | 1.0736e-07 | -3.5728e-08 | 0.0053497 | 0.0053497 | 0.0053497 | 0.98822 | -0.082726 | 0.98819 | -0.082944 | 1.9814
22 | 0.021171 | 0.0053079 | -0.021155 | -0.0053023 | 1.54e-05 | 5.5997e-06 | 0.031563 | 0.031563 | 0.031563 | 0.99811 | -0.013214 | 0.99736 | -0.018468 | 11.6901
23 | 0.021966 | 0.0055275 | -0.021945 | -0.0055196 | 2.1546e-05 | 7.8669e-06 | 0.032756 | 0.032756 | 0.032756 | 0.99811 | -0.013214 | 0.9971 | -0.020249 | 12.1319
24 | 0.017269 | 0.0043283 | -0.017265 | -0.0043268 | 4.4183e-06 | 1.5602e-06 | 0.025765 | 0.025765 | 0.025765 | 0.99736 | -0.018468 | 0.99709 | -0.020316 | 9.5426
25 | 0.021302 | 0.0053586 | -0.021298 | -0.0053569 | 4.724e-06 | 1.7193e-06 | 0.031797 | 0.031797 | 0.031797 | 0.9971 | -0.020249 | 0.99687 | -0.021839 | 11.7768
26 | 0.011122 | 0.0027872 | -0.01112 | -0.0027867 | 1.8942e-06 | 5.8483e-07 | 0.016598 | 0.016598 | 0.016598 | 0.99709 | -0.020316 | 0.99692 | -0.021547 | 6.1473
27 | 0.020655 | 0.0051958 | -0.020533 | -0.0051517 | 0.00012158 | 4.4106e-05 | 0.030838 | 0.030839 | 0.030839 | 0.99687 | -0.021839 | 0.99082 | -0.06428 | 11.4217
28 | 0.020533 | 0.0051517 | -0.020489 | -0.0051356 | 4.4369e-05 | 1.6104e-05 | 0.030839 | 0.030839 | 0.030839 | 0.99082 | -0.06428 | 0.98861 | -0.079887 | 11.4219
29 | 0.00349 | 0.00087429 | -0.0034897 | -0.00087438 | 2.315e-07 | -8.442e-08 | 0.0052447 | 0.0052448 | 0.0052448 | 0.99014 | -0.069087 | 0.99008 | -0.069567 | 1.9425
30 | 0.00076053 | 0.00019037 | -0.00076051 | -0.0001906 | 1.5031e-08 | -2.3133e-07 | 0.0011429 | 0.001143 | 0.001143 | 0.99008 | -0.069567 | 0.99006 | -0.06971 | 0.42334
31 | 0.0075182 | 0.0018839 | -0.0075171 | -0.0018837 | 1.0608e-06 | 2.32e-07 | 0.011222 | 0.011222 | 0.011222 | 0.99692 | -0.021547 | 0.99677 | -0.022567 | 4.1562
32 | 0.0032825 | 0.00082241 | -0.0032821 | -0.00082258 | 3.4669e-07 | -1.6823e-07 | 0.0049001 | 0.0049002 | 0.0049002 | 0.99677 | -0.022567 | 0.99666 | -0.02333 | 1.8149
33 | -0.0023197 | -0.00058138 | 0.0023198 | 0.00058135 | 2.2158e-08 | -2.855e-08 | 0.0034981 | 0.0034981 | 0.0034981 | 0.98677 | -0.092884 | 0.98678 | -0.092815 | 1.2956
34 | -0.0047425 | -0.0011885 | 0.0047436 | 0.0011885 | 1.1402e-06 | -1.8014e-08 | 0.0071514 | 0.0071512 | 0.0071514 | 0.98678 | -0.092815 | 0.98703 | -0.091078 | 2.6487
35 | -0.0090869 | -0.0022771 | 0.0090895 | 0.0022778 | 2.6019e-06 | 7.1667e-07 | 0.013699 | 0.013699 | 0.013699 | 0.98703 | -0.091078 | 0.98732 | -0.08901 | 5.0737
36 | -0.0090895 | -0.0022778 | 0.0090962 | 0.0022796 | 6.6439e-06 | 1.8292e-06 | 0.013699 | 0.013699 | 0.013699 | 0.98732 | -0.08901 | 0.98806 | -0.083731 | 5.0737
37 | -0.010962 | -0.0027472 | 0.010963 | 0.0027476 | 1.3245e-06 | 4.0964e-07 | 0.016508 | 0.016508 | 0.016508 | 0.98806 | -0.083731 | 0.98819 | -0.082858 | 6.1142
38 | -0.016098 | -0.0040345 | 0.016104 | 0.0040368 | 6.6239e-06 | 2.3161e-06 | 0.02424 | 0.02424 | 0.02424 | 0.98819 | -0.082858 | 0.98861 | -0.079887 | 8.9778

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10564 | 0.026371

## res_load
| p_mw | q_mvar
0 | 0.0014779 | 0.0003704
1 | 0.0006933 | 0.00017376
2 | 0.0010748 | 0.00026936
3 | 0.0048282 | 0.0012101
4 | 0.0068672 | 0.0017211
5 | 0.0070704 | 0.001772
6 | 0.0031575 | 0.00079134
7 | 0.0044822 | 0.0011233
8 | 0.0022758 | 0.00057038
9 | 0.0014016 | 0.00035128
10 | 0.0040005 | 0.0010026
11 | 0.0039129 | 0.00098066
12 | 0.0029106 | 0.00072948
13 | 0.0016143 | 0.00040459
14 | 0.0015014 | 0.00037627
15 | 0.0019904 | 0.00049884
16 | 0.0028186 | 0.0007064
17 | 0.0038863 | 0.000974
18 | 0.00064245 | 0.00016101
19 | 0.0061428 | 0.0015395
20 | 0.00064296 | 0.00016114
21 | 0.001995 | 0.00050001
22 | 0.0027292 | 0.00068401
23 | 0.00076051 | 0.0001906
24 | 0.0035527 | 0.00089039
25 | 0.0036018 | 0.00090271
26 | 0.0042346 | 0.0010613
27 | 0.0032821 | 0.00082258
28 | 0.0023197 | 0.00058138
29 | 0.0024227 | 0.00060719
30 | 0.0043433 | 0.0010885
31 | 0.0018656 | 0.00046756
32 | 0.0051347 | 0.0012869
33 | 0.0043842 | 0.0010988

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1