## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1098-26_1_3_node_11 | 0.4 | n |  | TRUE
1 | bus_LV_1098-26_1_3_node_12 | 0.4 | n |  | TRUE
2 | bus_LV_1098-26_1_3_node_13 | 0.4 | n |  | TRUE
3 | bus_LV_1098-26_1_3_node_14 | 0.4 | n |  | TRUE
4 | bus_LV_1098-26_1_3_node_15 | 0.4 | n |  | TRUE
5 | bus_LV_1098-26_1_3_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1098-26_1_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1098-26_1_3_node_113 | 0.4 | n |  | TRUE
8 | bus_LV_1098-26_1_3_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_1098-26_1_3_node_84 | 0.4 | n |  | TRUE
10 | bus_LV_1098-26_1_3_node_38 | 0.4 | n |  | TRUE
11 | bus_LV_1098-26_1_3_node_39 | 0.4 | n |  | TRUE
12 | bus_LV_1098-26_1_3_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_1098-26_1_3_node_41 | 0.4 | n |  | TRUE
14 | bus_LV_1098-26_1_3_node_46 | 0.4 | n |  | TRUE
15 | bus_LV_1098-26_1_3_node_47 | 0.4 | n |  | TRUE
16 | bus_LV_1098-26_1_3_node_42 | 0.4 | n |  | TRUE
17 | bus_LV_1098-26_1_3_node_43 | 0.4 | n |  | TRUE
18 | bus_LV_1098-26_1_3_node_44 | 0.4 | n |  | TRUE
19 | bus_LV_1098-26_1_3_node_45 | 0.4 | n |  | TRUE
20 | bus_LV_1098-26_1_3_node_160 | 0.4 | n |  | TRUE
21 | bus_LV_1098-26_1_3_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_1098-26_1_3_node_48 | 0.4 | n |  | TRUE
23 | bus_LV_1098-26_1_3_node_49 | 0.4 | n |  | TRUE
24 | bus_LV_1098-26_1_3_node_108 | 0.4 | n |  | TRUE
25 | bus_LV_1098-26_1_3_node_176 | 0.4 | n |  | TRUE
26 | bus_LV_1098-26_1_3_node_82 | 0.4 | n |  | TRUE
27 | bus_LV_1098-26_1_3_node_83 | 0.4 | n |  | TRUE
28 | bus_LV_1098-26_1_3_node_85 | 0.4 | n |  | TRUE
29 | bus_LV_1098-26_1_3_node_86 | 0.4 | n |  | TRUE
30 | bus_LV_1098-26_1_3_node_87 | 0.4 | n |  | TRUE
31 | bus_LV_1098-26_1_3_node_94 | 0.4 | n |  | TRUE
32 | bus_LV_1098-26_1_3_node_88 | 0.4 | n |  | TRUE
33 | bus_LV_1098-26_1_3_node_92 | 0.4 | n |  | TRUE
34 | bus_LV_1098-26_1_3_node_89 | 0.4 | n |  | TRUE
35 | bus_LV_1098-26_1_3_node_90 | 0.4 | n |  | TRUE
36 | bus_LV_1098-26_1_3_node_91 | 0.4 | n |  | TRUE
37 | bus_LV_1098-26_1_3_node_93 | 0.4 | n |  | TRUE
38 | bus_LV_1098-26_1_3_node_95 | 0.4 | n |  | TRUE
39 | bus_LV_1098-26_1_3_node_96 | 0.4 | n |  | TRUE
40 | bus_LV_1098-26_1_3_node_97 | 0.4 | n |  | TRUE
41 | bus_LV_1098-26_1_3_node_106 | 0.4 | n |  | TRUE
42 | bus_LV_1098-26_1_3_node_98 | 0.4 | n |  | TRUE
43 | bus_LV_1098-26_1_3_node_99 | 0.4 | n |  | TRUE
44 | bus_LV_1098-26_1_3_node_103 | 0.4 | n |  | TRUE
45 | bus_LV_1098-26_1_3_node_100 | 0.4 | n |  | TRUE
46 | bus_LV_1098-26_1_3_node_101 | 0.4 | n |  | TRUE
47 | bus_LV_1098-26_1_3_node_102 | 0.4 | n |  | TRUE
48 | bus_LV_1098-26_1_3_node_114 | 0.4 | n |  | TRUE
49 | bus_LV_1098-26_1_3_node_104 | 0.4 | n |  | TRUE
50 | bus_LV_1098-26_1_3_node_105 | 0.4 | n |  | TRUE
51 | bus_LV_1098-26_1_3_node_107 | 0.4 | n |  | TRUE
52 | bus_LV_1098-26_1_3_node_115 | 0.4 | n |  | TRUE
53 | bus_LV_1098-26_1_3_node_109 | 0.4 | n |  | TRUE
54 | bus_LV_1098-26_1_3_node_121 | 0.4 | n |  | TRUE
55 | bus_LV_1098-26_1_3_node_122 | 0.4 | n |  | TRUE
56 | bus_LV_1098-26_1_3_node_110 | 0.4 | n |  | TRUE
57 | bus_LV_1098-26_1_3_node_111 | 0.4 | n |  | TRUE
58 | bus_LV_1098-26_1_3_node_112 | 0.4 | n |  | TRUE
59 | bus_LV_1098-26_1_3_node_116 | 0.4 | n |  | TRUE
60 | bus_LV_1098-26_1_3_node_117 | 0.4 | n |  | TRUE
61 | bus_LV_1098-26_1_3_node_118 | 0.4 | n |  | TRUE
62 | bus_LV_1098-26_1_3_node_119 | 0.4 | n |  | TRUE
63 | bus_LV_1098-26_1_3_node_120 | 0.4 | n |  | TRUE
64 | bus_LV_1098-26_1_3_node_123 | 0.4 | n |  | TRUE
65 | bus_LV_1098-26_1_3_node_127 | 0.4 | n |  | TRUE
66 | bus_LV_1098-26_1_3_node_124 | 0.4 | n |  | TRUE
67 | bus_LV_1098-26_1_3_node_125 | 0.4 | n |  | TRUE
68 | bus_LV_1098-26_1_3_node_126 | 0.4 | n |  | TRUE
69 | bus_LV_1098-26_1_3_node_128 | 0.4 | n |  | TRUE
70 | bus_LV_1098-26_1_3_node_129 | 0.4 | n |  | TRUE
71 | bus_LV_1098-26_1_3_node_130 | 0.4 | n |  | TRUE
72 | bus_LV_1098-26_1_3_node_131 | 0.4 | n |  | TRUE
73 | bus_LV_1098-26_1_3_node_132 | 0.4 | n |  | TRUE
74 | bus_LV_1098-26_1_3_node_133 | 0.4 | n |  | TRUE
75 | bus_LV_1098-26_1_3_node_134 | 0.4 | n |  | TRUE
76 | bus_LV_1098-26_1_3_node_142 | 0.4 | n |  | TRUE
77 | bus_LV_1098-26_1_3_node_162 | 0.4 | n |  | TRUE
78 | bus_LV_1098-26_1_3_node_173 | 0.4 | n |  | TRUE
79 | bus_MV_0_node_102 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1098-26_1_3_load_11 | 0 | 0.0002609 | 6.5387e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1098-26_1_3_load_13 | 2 | 0.0008147 | 0.00020418 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1098-26_1_3_load_14 | 3 | 0.0016769 | 0.00042028 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1098-26_1_3_load_15 | 4 | 0.00077232 | 0.00019356 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1098-26_1_3_load_18 | 5 | 0.00019948 | 4.9996e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1098-26_1_3_load_38 | 10 | 0.00056312 | 0.00014113 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1098-26_1_3_load_39 | 11 | 0.00014789 | 3.7064e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1098-26_1_3_load_40 | 12 | 8.9818e-05 | 2.2511e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1098-26_1_3_load_47 | 15 | 0.00018251 | 4.5742e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1098-26_1_3_load_42 | 16 | 0.00057259 | 0.0001435 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1098-26_1_3_load_43 | 17 | 0.00017123 | 4.2915e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1098-26_1_3_load_44 | 18 | 5.9732e-05 | 1.497e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1098-26_1_3_load_45 | 19 | 0.00051165 | 0.00012823 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1098-26_1_3_load_160 | 20 | 0.0002537 | 6.3583e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1098-26_1_3_load_48 | 22 | 5.4618e-05 | 1.3689e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1098-26_1_3_load_49 | 23 | 0.00015402 | 3.8601e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1098-26_1_3_load_176 | 25 | 8.3688e-05 | 2.0974e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1098-26_1_3_load_82 | 26 | 0.00031411 | 7.8725e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1098-26_1_3_load_83 | 27 | 0.00078764 | 0.0001974 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1098-26_1_3_load_88 | 32 | 0.0056886 | 0.0014257 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1098-26_1_3_load_92 | 33 | 0.0001936 | 4.852e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1098-26_1_3_load_89 | 34 | 0.00061875 | 0.00015507 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1098-26_1_3_load_90 | 35 | 0.00042428 | 0.00010633 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1098-26_1_3_load_91 | 36 | 0.00072306 | 0.00018121 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1098-26_1_3_load_93 | 37 | 0.0011938 | 0.0002992 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1098-26_1_3_load_95 | 38 | 0.00072398 | 0.00018145 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1098-26_1_3_load_97 | 40 | 0.00024726 | 6.1969e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1098-26_1_3_load_99 | 43 | 0.00016408 | 4.1122e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1098-26_1_3_load_103 | 44 | 0.00019403 | 4.8629e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1098-26_1_3_load_102 | 47 | 0.00071938 | 0.00018029 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1098-26_1_3_load_114 | 48 | 0.0020235 | 0.00050713 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1098-26_1_3_load_104 | 49 | 0.0021756 | 0.00054525 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1098-26_1_3_load_105 | 50 | 0.00067006 | 0.00016793 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1098-26_1_3_load_115 | 52 | 0.00024576 | 6.1593e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1098-26_1_3_load_121 | 54 | 0.0003473 | 8.7042e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1098-26_1_3_load_110 | 56 | 0.00059673 | 0.00014955 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1098-26_1_3_load_111 | 57 | 0.0033855 | 0.00084847 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1098-26_1_3_load_116 | 59 | 0.00018533 | 4.6449e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1098-26_1_3_load_118 | 61 | 0.00059595 | 0.00014936 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1098-26_1_3_load_119 | 62 | 0.00013002 | 3.2587e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1098-26_1_3_load_120 | 63 | 0.00010624 | 2.6627e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1098-26_1_3_load_123 | 64 | 6.672e-05 | 1.6722e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1098-26_1_3_load_127 | 65 | 0.00046794 | 0.00011728 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1098-26_1_3_load_124 | 66 | 0.00036562 | 9.1633e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1098-26_1_3_load_125 | 67 | 0.00017287 | 4.3325e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1098-26_1_3_load_126 | 68 | 5.4295e-05 | 1.3608e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1098-26_1_3_load_128 | 69 | 0.00020953 | 5.2513e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1098-26_1_3_load_129 | 70 | 0.00025312 | 6.3439e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1098-26_1_3_load_130 | 71 | 0.00020069 | 5.0299e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1098-26_1_3_load_132 | 73 | 0.0006144 | 0.00015398 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1098-26_1_3_load_134 | 75 | 0.00039742 | 9.9602e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1098-26_1_3_load_142 | 76 | 0.00019579 | 4.9069e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1098-26_1_3_load_162 | 77 | 0.00030008 | 7.5208e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1098-26_1_3_load_173 | 78 | 0.00039567 | 9.9164e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1098-26_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.050977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1098-26_1_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.024652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1098-26_1_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.010239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1098-26_1_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.02256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1098-26_1_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.040931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1098-26_1_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.14309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1098-26_1_3_line_6 | NAYY 4x150 SE | 5 | 8 | 0.048196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1098-26_1_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.4789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1098-26_1_3_line_8 | NAYY 4x150 SE | 7 | 57 | 0.019727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1098-26_1_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.45187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1098-26_1_3_line_10 | NAYY 4x150 SE | 9 | 29 | 0.1575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1098-26_1_3_line_11 | NAYY 4x150 SE | 10 | 11 | 0.027227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1098-26_1_3_line_12 | NAYY 4x150 SE | 10 | 12 | 0.026577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1098-26_1_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.027888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1098-26_1_3_line_14 | NAYY 4x150 SE | 13 | 14 | 0.030901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1098-26_1_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.029568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1098-26_1_3_line_16 | NAYY 4x150 SE | 14 | 21 | 0.013887 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1098-26_1_3_line_17 | NAYY 4x150 SE | 14 | 18 | 0.016075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1098-26_1_3_line_18 | NAYY 4x150 SE | 15 | 22 | 0.038167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1098-26_1_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.024747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1098-26_1_3_line_20 | NAYY 4x150 SE | 16 | 18 | 0.0011548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1098-26_1_3_line_21 | NAYY 4x150 SE | 17 | 19 | 0.058631 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1098-26_1_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.51871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1098-26_1_3_line_23 | NAYY 4x150 SE | 20 | 75 | 0.045361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1098-26_1_3_line_24 | NAYY 4x150 SE | 21 | 25 | 0.051267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1098-26_1_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.074785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1098-26_1_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.0944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1098-26_1_3_line_27 | NAYY 4x150 SE | 24 | 53 | 0.11709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1098-26_1_3_line_28 | NAYY 4x150 SE | 26 | 27 | 0.088046 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1098-26_1_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.040529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1098-26_1_3_line_30 | NAYY 4x150 SE | 28 | 30 | 0.013369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1098-26_1_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.011681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1098-26_1_3_line_32 | NAYY 4x150 SE | 29 | 32 | 0.023773 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1098-26_1_3_line_33 | NAYY 4x150 SE | 30 | 33 | 0.0098192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1098-26_1_3_line_34 | NAYY 4x150 SE | 30 | 34 | 0.012658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1098-26_1_3_line_35 | NAYY 4x150 SE | 31 | 37 | 0.062302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1098-26_1_3_line_36 | NAYY 4x150 SE | 33 | 37 | 0.022748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1098-26_1_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.015736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1098-26_1_3_line_38 | NAYY 4x150 SE | 35 | 36 | 0.0023618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1098-26_1_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.032864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1098-26_1_3_line_40 | NAYY 4x150 SE | 38 | 40 | 0.05196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1098-26_1_3_line_41 | NAYY 4x150 SE | 38 | 41 | 0.15946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1098-26_1_3_line_42 | NAYY 4x150 SE | 39 | 42 | 0.055022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1098-26_1_3_line_43 | NAYY 4x150 SE | 39 | 43 | 0.021084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1098-26_1_3_line_44 | NAYY 4x150 SE | 41 | 51 | 0.15831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1098-26_1_3_line_45 | NAYY 4x150 SE | 41 | 50 | 0.1726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1098-26_1_3_line_46 | NAYY 4x150 SE | 42 | 44 | 0.018205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1098-26_1_3_line_47 | NAYY 4x150 SE | 45 | 46 | 0.049925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1098-26_1_3_line_48 | NAYY 4x150 SE | 45 | 47 | 0.07916 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1098-26_1_3_line_49 | NAYY 4x150 SE | 46 | 48 | 0.060702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1098-26_1_3_line_50 | NAYY 4x150 SE | 47 | 49 | 0.052337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1098-26_1_3_line_51 | NAYY 4x150 SE | 48 | 58 | 0.0029491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1098-26_1_3_line_52 | NAYY 4x150 SE | 49 | 50 | 0.0083754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1098-26_1_3_line_53 | NAYY 4x150 SE | 51 | 52 | 0.1833 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1098-26_1_3_line_54 | NAYY 4x150 SE | 52 | 59 | 0.033345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1098-26_1_3_line_55 | NAYY 4x150 SE | 53 | 54 | 0.026847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1098-26_1_3_line_56 | NAYY 4x150 SE | 53 | 55 | 0.012668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1098-26_1_3_line_57 | NAYY 4x150 SE | 54 | 63 | 0.0051953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1098-26_1_3_line_58 | NAYY 4x150 SE | 55 | 64 | 0.010865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1098-26_1_3_line_59 | NAYY 4x150 SE | 56 | 57 | 0.0078999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1098-26_1_3_line_60 | NAYY 4x150 SE | 56 | 58 | 0.021786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1098-26_1_3_line_61 | NAYY 4x150 SE | 59 | 60 | 0.022421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1098-26_1_3_line_62 | NAYY 4x150 SE | 60 | 61 | 0.032516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1098-26_1_3_line_63 | NAYY 4x150 SE | 60 | 62 | 0.032488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1098-26_1_3_line_64 | NAYY 4x150 SE | 61 | 63 | 0.033229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1098-26_1_3_line_65 | NAYY 4x150 SE | 64 | 65 | 0.013349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1098-26_1_3_line_66 | NAYY 4x150 SE | 65 | 67 | 0.011706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1098-26_1_3_line_67 | NAYY 4x150 SE | 66 | 67 | 0.02597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1098-26_1_3_line_68 | NAYY 4x150 SE | 66 | 68 | 0.0028667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1098-26_1_3_line_69 | NAYY 4x150 SE | 68 | 69 | 0.017297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1098-26_1_3_line_70 | NAYY 4x150 SE | 70 | 71 | 0.01921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1098-26_1_3_line_71 | NAYY 4x150 SE | 70 | 72 | 0.014011 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1098-26_1_3_line_72 | NAYY 4x150 SE | 71 | 73 | 0.0015766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1098-26_1_3_line_73 | NAYY 4x150 SE | 72 | 74 | 0.03795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1098-26_1_3_line_74 | NAYY 4x150 SE | 72 | 75 | 0.057362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1098-26_1_3_line_75 | NAYY 4x150 SE | 73 | 76 | 0.062719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1098-26_1_3_line_76 | NAYY 4x150 SE | 74 | 77 | 0.017839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1098-26_1_3_line_77 | NAYY 4x150 SE | 76 | 78 | 0.036259 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1098-26_1_3_trafo_102 | 0.25 MVA 20/0.4 kV | 79 | 47 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2653251.9048 | 1218119.3025 | 2653258.6124 | 1218132.2703 | 2653262.5022 | 1218155.6415 | 2653266.4059 | 1218167.7107
1 | 2653251.9048 | 1218119.3025 | 2653236.4496 | 1218127.147 | 2653229.6905 | 1218129.9575
2 | 2653251.9048 | 1218119.3025 | 2653246.349 | 1218110.7015
3 | 2653229.6905 | 1218129.9575 | 2653229.3036 | 1218130.1183 | 2653207.6401 | 1218134.6937
4 | 2653223.9078 | 1218076.4842 | 2653226.0163 | 1218079.2247 | 2653246.349 | 1218110.7015
5 | 2653081.5309 | 1218131.1348 | 2653086.1259 | 1218136.7569 | 2653109.2672 | 1218158.9988 | 2653115.5505 | 1218161.6897 | 2653122.2693 | 1218162.3611 | 2653128.459 | 1218161.0821 | 2653137.039 | 1218157.3119 | 2653156.0561 | 1218148.3426 | 2653167.8957 | 1218144.1901 | 2653186.8786 | 1218139.0785 | 2653207.6401 | 1218134.6937
6 | 2653194.5184 | 1218038.2854 | 2653223.9078 | 1218076.4842
7 | 2652821.0115 | 1217729.2992 | 2653081.5309 | 1218131.1348
8 | 2652821.0115 | 1217729.2992 | 2652801.2879 | 1217729.6581
9 | 2653186.3684 | 1217586.4936 | 2653194.5184 | 1218038.2854
10 | 2653186.3684 | 1217586.4936 | 2653344.3056 | 1217589.4952
11 | 2651836.689 | 1217672.6574 | 2651839.1244 | 1217699.7752
12 | 2651836.689 | 1217672.6574 | 2651834.3117 | 1217646.1866
13 | 2651832.5455 | 1217618.3687 | 2651832.8131 | 1217629.5 | 2651834.3117 | 1217646.1866
14 | 2651806.9393 | 1217602.103 | 2651816.1608 | 1217610.9663 | 2651826.2655 | 1217616.9132 | 2651832.5455 | 1217618.3687
15 | 2651832.5455 | 1217618.3687 | 2651839.0649 | 1217618.4921 | 2651862.0751 | 1217617.1735
16 | 2651806.9393 | 1217602.103 | 2651801.6631 | 1217591.6953 | 2651801.3634 | 1217589.4914
17 | 2651806.9393 | 1217602.103 | 2651792.3409 | 1217606.6345 | 2651791.5695 | 1217606.8023
18 | 2651900.1794 | 1217614.9899 | 2651862.0751 | 1217617.1735
19 | 2651790.4411 | 1217607.0479 | 2651775.1458 | 1217610.3763 | 2651766.102 | 1217611.3303
20 | 2651790.4411 | 1217607.0479 | 2651791.5695 | 1217606.8023
21 | 2651766.102 | 1217611.3303 | 2651750.7041 | 1217612.9546 | 2651707.6603 | 1217615.9493
22 | 2651707.6603 | 1217615.9493 | 2651489.3982 | 1217145.3997
23 | 2651489.3982 | 1217145.3997 | 2651491.0851 | 1217144.8797 | 2651497.4391 | 1217140.4764 | 2651504.6662 | 1217128.1536 | 2651506.5733 | 1217120.054 | 2651509.0719 | 1217113.7829 | 2651513.1885 | 1217108.743
24 | 2651801.3634 | 1217589.4914 | 2651812.963 | 1217587.6355 | 2651831.3993 | 1217585.2053 | 2651834.9848 | 1217570.939 | 2651839.5318 | 1217566.5647
25 | 2651900.1794 | 1217614.9899 | 2651974.8416 | 1217610.7113
26 | 2652069.0872 | 1217605.3105 | 2651974.8416 | 1217610.7113
27 | 2652069.0872 | 1217605.3105 | 2652080.5043 | 1217593.0806 | 2652088.5322 | 1217583.0113 | 2652093.297 | 1217573.714 | 2652096.2409 | 1217562.5774 | 2652100.7977 | 1217507.6061 | 2652103.1255 | 1217497.487
28 | 2653256.0471 | 1217427.5579 | 2653262.8333 | 1217434.9842 | 2653287.7713 | 1217461.1117 | 2653315.5406 | 1217488.0763 | 2653317.7591 | 1217490.3269
29 | 2653344.7407 | 1217520.535 | 2653327.6144 | 1217500.3251 | 2653317.7591 | 1217490.3269
30 | 2653344.7407 | 1217520.535 | 2653358.0317 | 1217522.2994
31 | 2653355.8644 | 1217591.3998 | 2653344.3056 | 1217589.4952
32 | 2653344.3056 | 1217589.4952 | 2653332.5835 | 1217576.9827 | 2653329.1185 | 1217571.3327
33 | 2653358.0317 | 1217522.2994 | 2653366.0462 | 1217527.9725
34 | 2653358.0317 | 1217522.2994 | 2653360.9932 | 1217509.9929
35 | 2653355.8644 | 1217591.3998 | 2653364.2409 | 1217588.4285 | 2653375.3224 | 1217578.3771 | 2653377.8191 | 1217572.5181 | 2653384.6133 | 1217541.1154
36 | 2653384.6133 | 1217541.1154 | 2653366.0462 | 1217527.9725
37 | 2653360.9932 | 1217509.9929 | 2653362.0763 | 1217505.4921 | 2653366.491 | 1217495.301
38 | 2653367.4298 | 1217493.1337 | 2653366.491 | 1217495.301
39 | 2652541.2036 | 1217449.9466 | 2652529.9051 | 1217463.2218 | 2652514.5223 | 1217461.997
40 | 2652488.2564 | 1217430.1794 | 2652488.0723 | 1217451.0794 | 2652495.5196 | 1217460.4839 | 2652514.5223 | 1217461.997
41 | 2652529.245 | 1217620.7781 | 2652514.5223 | 1217461.997
42 | 2652541.2036 | 1217449.9466 | 2652538.059 | 1217446.7169 | 2652538.1038 | 1217441.6365 | 2652541.5991 | 1217437.8094 | 2652555.8859 | 1217434.2887 | 2652581.5409 | 1217433.7034
43 | 2652541.2036 | 1217449.9466 | 2652561.2989 | 1217456.3266
44 | 2652370.5528 | 1217615.6903 | 2652529.245 | 1217620.7781
45 | 2652529.245 | 1217620.7781 | 2652701.8254 | 1217617.8677
46 | 2652581.5409 | 1217433.7034 | 2652599.7456 | 1217433.7679
47 | 2652872.1219 | 1217680.1891 | 2652845.7683 | 1217650.9599 | 2652837.6081 | 1217644.139
48 | 2652837.6081 | 1217644.139 | 2652771.4569 | 1217621.6618 | 2652762.3339 | 1217619.8847
49 | 2652872.1219 | 1217680.1891 | 2652868.929 | 1217684.1521 | 2652860.7987 | 1217688.516 | 2652835.1831 | 1217692.4802 | 2652830.0668 | 1217695.0809 | 2652823.2597 | 1217705.1601 | 2652822.335 | 1217707.5506
50 | 2652710.1996 | 1217617.7265 | 2652722.6549 | 1217617.5165 | 2652751.7247 | 1217617.8182 | 2652762.3339 | 1217619.8847
51 | 2652821.2709 | 1217710.3011 | 2652822.335 | 1217707.5506
52 | 2652710.1996 | 1217617.7265 | 2652701.8254 | 1217617.8677
53 | 2652370.5528 | 1217615.6903 | 2652367.1398 | 1217610.1792 | 2652327.7086 | 1217579.6367 | 2652273.1432 | 1217533.2411 | 2652260.9929 | 1217526.0302 | 2652251.0455 | 1217522.0851 | 2652220.9539 | 1217517.1657
54 | 2652220.9539 | 1217517.1657 | 2652213.0319 | 1217515.8706 | 2652206.5297 | 1217513.7791 | 2652201.6901 | 1217509.0672 | 2652196.4234 | 1217498.5831
55 | 2652103.1255 | 1217497.487 | 2652127.8795 | 1217507.8806
56 | 2652107.9116 | 1217485.7551 | 2652103.1255 | 1217497.487
57 | 2652132.6697 | 1217509.8918 | 2652127.8795 | 1217507.8806
58 | 2652107.9116 | 1217485.7551 | 2652103.5361 | 1217477.434 | 2652102.3161 | 1217476.6247
59 | 2652802.8367 | 1217721.9116 | 2652801.2879 | 1217729.6581
60 | 2652821.2709 | 1217710.3011 | 2652802.8367 | 1217721.9116 | 2652802.8367 | 1217721.9116
61 | 2652183.206 | 1217480.4992 | 2652195.7662 | 1217497.2748 | 2652196.4234 | 1217498.5831
62 | 2652183.206 | 1217480.4992 | 2652166.4561 | 1217490.5476 | 2652160.7247 | 1217502.1968
63 | 2652183.206 | 1217480.4992 | 2652157.7611 | 1217479.665 | 2652150.7496 | 1217480.1602
64 | 2652160.7247 | 1217502.1968 | 2652157.3985 | 1217508.9573 | 2652139.4434 | 1217512.7359 | 2652132.6697 | 1217509.8918
65 | 2652102.3161 | 1217476.6247 | 2652091.1916 | 1217469.2455
66 | 2652081.4369 | 1217462.775 | 2652091.1916 | 1217469.2455
67 | 2652059.7952 | 1217448.4194 | 2652081.4369 | 1217462.775
68 | 2652059.7952 | 1217448.4194 | 2652057.4062 | 1217446.8347
69 | 2652041.3084 | 1217440.6572 | 2652055.7249 | 1217445.7195 | 2652057.4062 | 1217446.8347
70 | 2651557.593 | 1217062.9465 | 2651576.8013 | 1217063.2155
71 | 2651543.5832 | 1217062.7503 | 2651557.593 | 1217062.9465
72 | 2651578.3777 | 1217063.2376 | 2651576.8013 | 1217063.2155
73 | 2651543.5832 | 1217062.7503 | 2651505.5471 | 1217061.3542
74 | 2651543.5832 | 1217062.7503 | 2651542.419 | 1217071.8457 | 2651533.9146 | 1217089.6385 | 2651530.0017 | 1217095.2859 | 2651514.834 | 1217106.7284 | 2651513.1885 | 1217108.743
75 | 2651578.3777 | 1217063.2376 | 2651612.1556 | 1217063.7106 | 2651628.8907 | 1217061.5431 | 2651640.5182 | 1217058.3307 | 2651640.5182 | 1217058.3307
76 | 2651505.5471 | 1217061.3542 | 2651487.7202 | 1217060.7004
77 | 2651675.1677 | 1217047.6477 | 2651640.5182 | 1217058.3307

## bus_geodata
| x | y | coords
0 | 2653266.4059 | 1218167.7107
1 | 2653251.9048 | 1218119.3025
2 | 2653229.6905 | 1218129.9575
3 | 2653246.349 | 1218110.7015
4 | 2653207.6401 | 1218134.6937
5 | 2653223.9078 | 1218076.4842
6 | 2653081.5309 | 1218131.1348
7 | 2652821.0115 | 1217729.2992
8 | 2653194.5184 | 1218038.2854
9 | 2653186.3684 | 1217586.4936
10 | 2651836.689 | 1217672.6574
11 | 2651839.1244 | 1217699.7752
12 | 2651834.3117 | 1217646.1866
13 | 2651832.5455 | 1217618.3687
14 | 2651806.9393 | 1217602.103
15 | 2651862.0751 | 1217617.1735
16 | 2651790.4411 | 1217607.0479
17 | 2651766.102 | 1217611.3303
18 | 2651791.5695 | 1217606.8023
19 | 2651707.6603 | 1217615.9493
20 | 2651489.3982 | 1217145.3997
21 | 2651801.3634 | 1217589.4914
22 | 2651900.1794 | 1217614.9899
23 | 2651974.8416 | 1217610.7113
24 | 2652069.0872 | 1217605.3105
25 | 2651839.5318 | 1217566.5647
26 | 2653256.0471 | 1217427.5579
27 | 2653317.7591 | 1217490.3269
28 | 2653344.7407 | 1217520.535
29 | 2653344.3056 | 1217589.4952
30 | 2653358.0317 | 1217522.2994
31 | 2653355.8644 | 1217591.3998
32 | 2653329.1185 | 1217571.3327
33 | 2653366.0462 | 1217527.9725
34 | 2653360.9932 | 1217509.9929
35 | 2653366.491 | 1217495.301
36 | 2653367.4298 | 1217493.1337
37 | 2653384.6133 | 1217541.1154
38 | 2652514.5223 | 1217461.997
39 | 2652541.2036 | 1217449.9466
40 | 2652488.2564 | 1217430.1794
41 | 2652529.245 | 1217620.7781
42 | 2652581.5409 | 1217433.7034
43 | 2652561.2989 | 1217456.3266
44 | 2652599.7456 | 1217433.7679
45 | 2652837.6081 | 1217644.139
46 | 2652872.1219 | 1217680.1891
47 | 2652762.3339 | 1217619.8847
48 | 2652822.335 | 1217707.5506
49 | 2652710.1996 | 1217617.7265
50 | 2652701.8254 | 1217617.8677
51 | 2652370.5528 | 1217615.6903
52 | 2652220.9539 | 1217517.1657
53 | 2652103.1255 | 1217497.487
54 | 2652127.8795 | 1217507.8806
55 | 2652107.9116 | 1217485.7551
56 | 2652802.8367 | 1217721.9116
57 | 2652801.2879 | 1217729.6581
58 | 2652821.2709 | 1217710.3011
59 | 2652196.4234 | 1217498.5831
60 | 2652183.206 | 1217480.4992
61 | 2652160.7247 | 1217502.1968
62 | 2652150.7496 | 1217480.1602
63 | 2652132.6697 | 1217509.8918
64 | 2652102.3161 | 1217476.6247
65 | 2652091.1916 | 1217469.2455
66 | 2652059.7952 | 1217448.4194
67 | 2652081.4369 | 1217462.775
68 | 2652057.4062 | 1217446.8347
69 | 2652041.3084 | 1217440.6572
70 | 2651557.593 | 1217062.9465
71 | 2651576.8013 | 1217063.2155
72 | 2651543.5832 | 1217062.7503
73 | 2651578.3777 | 1217063.2376
74 | 2651505.5471 | 1217061.3542
75 | 2651513.1885 | 1217108.743
76 | 2651640.5182 | 1217058.3307
77 | 2651487.7202 | 1217060.7004
78 | 2651675.1677 | 1217047.6477
79 | 2652762.3339 | 1217619.8847

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98115 | -0.13246 | 0.0002609 | 6.5387e-05
1 | 0.98117 | -0.13232 | 0 | 0
2 | 0.9816 | -0.12921 | 0.0008147 | 0.00020418
3 | 0.98099 | -0.13359 | 0.0016769 | 0.00042028
4 | 0.98203 | -0.12617 | 0.00077232 | 0.00019356
5 | 0.98038 | -0.13793 | 0.00019948 | 4.9996e-05
6 | 0.98489 | -0.10583 | 0 | 0
7 | 0.99448 | -0.03845 | 0 | 0
8 | 0.97968 | -0.14296 | 0 | 0
9 | 0.97308 | -0.1903 | 0 | 0
10 | 0.98829 | -0.083959 | 0.00056312 | 0.00014113
11 | 0.98829 | -0.084 | 0.00014789 | 3.7064e-05
12 | 0.98832 | -0.083764 | 8.9818e-05 | 2.2511e-05
13 | 0.98835 | -0.083534 | 0 | 0
14 | 0.98817 | -0.08483 | 0 | 0
15 | 0.98856 | -0.08205 | 0.00018251 | 4.5742e-05
16 | 0.98807 | -0.085536 | 0.00057259 | 0.0001435
17 | 0.98796 | -0.086391 | 0.00017123 | 4.2915e-05
18 | 0.98808 | -0.08549 | 5.9732e-05 | 1.497e-05
19 | 0.98769 | -0.088311 | 0.00051165 | 0.00012823
20 | 0.98573 | -0.10247 | 0.0002537 | 6.3583e-05
21 | 0.98817 | -0.084843 | 0 | 0
22 | 0.98883 | -0.080062 | 5.4618e-05 | 1.3689e-05
23 | 0.98938 | -0.076124 | 0.00015402 | 3.8601e-05
24 | 0.99008 | -0.071003 | 0 | 0
25 | 0.98816 | -0.084888 | 8.3688e-05 | 2.0974e-05
26 | 0.97004 | -0.21223 | 0.00031411 | 7.8725e-05
27 | 0.97008 | -0.21194 | 0.00078764 | 0.0001974
28 | 0.97015 | -0.21146 | 0 | 0
29 | 0.97078 | -0.2069 | 0 | 0
30 | 0.97017 | -0.2113 | 0 | 0
31 | 0.9707 | -0.20743 | 0 | 0
32 | 0.97058 | -0.20834 | 0.0056886 | 0.0014257
33 | 0.97021 | -0.211 | 0.0001936 | 4.852e-05
34 | 0.97014 | -0.21154 | 0.00061875 | 0.00015507
35 | 0.97011 | -0.21173 | 0.00042428 | 0.00010633
36 | 0.97011 | -0.21175 | 0.00072306 | 0.00018121
37 | 0.97031 | -0.21026 | 0.0011938 | 0.0002992
38 | 0.99629 | -0.026432 | 0.00072398 | 0.00018145
39 | 0.99628 | -0.026554 | 0 | 0
40 | 0.99628 | -0.026562 | 0.00024726 | 6.1969e-05
41 | 0.9966 | -0.024261 | 0 | 0
42 | 0.99626 | -0.026664 | 0 | 0
43 | 0.99627 | -0.026589 | 0.00016408 | 4.1122e-05
44 | 0.99626 | -0.026699 | 0.00019403 | 4.8629e-05
45 | 0.99887 | -0.0078541 | 0 | 0
46 | 0.99744 | -0.017781 | 0 | 0
47 | 1 | 0 | -0.033289 | -0.0081483
48 | 0.9957 | -0.029887 | 0.0020235 | 0.00050713
49 | 0.99907 | -0.0065747 | 0.0021756 | 0.00054525
50 | 0.99895 | -0.0074454 | 0.00067006 | 0.00016793
51 | 0.99474 | -0.037552 | 0 | 0
52 | 0.99259 | -0.052973 | 0.00024576 | 6.1593e-05
53 | 0.99096 | -0.06465 | 0 | 0
54 | 0.99122 | -0.062826 | 0.0003473 | 8.7042e-05
55 | 0.99094 | -0.064824 | 0 | 0
56 | 0.99507 | -0.034326 | 0.00059673 | 0.00014955
57 | 0.99487 | -0.035697 | 0.0033855 | 0.00084847
58 | 0.99563 | -0.030416 | 0 | 0
59 | 0.99221 | -0.055699 | 0.00018533 | 4.6449e-05
60 | 0.99196 | -0.05749 | 0 | 0
61 | 0.9916 | -0.060045 | 0.00059595 | 0.00014936
62 | 0.99195 | -0.057534 | 0.00013002 | 3.2587e-05
63 | 0.99127 | -0.062455 | 0.00010624 | 2.6627e-05
64 | 0.99092 | -0.064972 | 6.672e-05 | 1.6722e-05
65 | 0.99089 | -0.065145 | 0.00046794 | 0.00011728
66 | 0.99086 | -0.065408 | 0.00036562 | 9.1633e-05
67 | 0.99088 | -0.065241 | 0.00017287 | 4.3325e-05
68 | 0.99085 | -0.065416 | 5.4295e-05 | 1.3608e-05
69 | 0.99085 | -0.065453 | 0.00020953 | 5.2513e-05
70 | 0.98538 | -0.10499 | 0.00025312 | 6.3439e-05
71 | 0.98534 | -0.10527 | 0.00020069 | 5.0299e-05
72 | 0.98542 | -0.10475 | 0 | 0
73 | 0.98534 | -0.10529 | 0.0006144 | 0.00015398
74 | 0.9854 | -0.10487 | 0 | 0
75 | 0.98558 | -0.10358 | 0.00039742 | 9.9602e-05
76 | 0.98529 | -0.10568 | 0.00019579 | 4.9069e-05
77 | 0.98539 | -0.10492 | 0.00030008 | 7.5208e-05
78 | 0.98527 | -0.10582 | 0.00039567 | 9.9164e-05
79 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0002609 | -6.5387e-05 | 0.0002609 | 6.4745e-05 | 4.9774e-09 | -6.4191e-07 | 0.00039568 | 0.00039545 | 0.00039568 | 0.98115 | -0.13246 | 0.98117 | -0.13232 | 0.14655
1 | -0.012189 | -0.0030559 | 0.012194 | 0.0030576 | 5.2564e-06 | 1.7102e-06 | 0.018485 | 0.018485 | 0.018485 | 0.98117 | -0.13232 | 0.9816 | -0.12921 | 6.8464
2 | 0.011928 | 0.0029911 | -0.011926 | -0.0029905 | 2.0909e-06 | 6.7488e-07 | 0.01809 | 0.01809 | 0.01809 | 0.98117 | -0.13232 | 0.98099 | -0.13359 | 6.7
3 | -0.013009 | -0.0032618 | 0.013014 | 0.0032636 | 5.4746e-06 | 1.8203e-06 | 0.01972 | 0.01972 | 0.01972 | 0.9816 | -0.12921 | 0.98203 | -0.12617 | 7.3038
4 | 0.010249 | 0.0025702 | -0.010242 | -0.0025683 | 6.1729e-06 | 1.8578e-06 | 0.015546 | 0.015546 | 0.015546 | 0.98099 | -0.13359 | 0.98038 | -0.13793 | 5.7579
5 | -0.013786 | -0.0034572 | 0.013825 | 0.0034703 | 3.8965e-05 | 1.3171e-05 | 0.02089 | 0.02089 | 0.02089 | 0.98203 | -0.12617 | 0.98489 | -0.10583 | 7.7372
6 | 0.010043 | 0.0025183 | -0.010036 | -0.0025163 | 6.9885e-06 | 2.0806e-06 | 0.015244 | 0.015244 | 0.015244 | 0.98038 | -0.13793 | 0.97968 | -0.14296 | 5.6459
7 | -0.013825 | -0.0034703 | 0.013956 | 0.0035143 | 0.00013039 | 4.3996e-05 | 0.02089 | 0.020888 | 0.02089 | 0.98489 | -0.10583 | 0.99448 | -0.03845 | 7.7369
8 | -0.013956 | -0.0035143 | 0.013961 | 0.0035161 | 5.3705e-06 | 1.8095e-06 | 0.020888 | 0.020887 | 0.020888 | 0.99448 | -0.03845 | 0.99487 | -0.035697 | 7.7361
9 | 0.010036 | 0.0025163 | -0.0099705 | -0.0024967 | 6.5531e-05 | 1.9553e-05 | 0.015244 | 0.015246 | 0.015246 | 0.97968 | -0.14296 | 0.97308 | -0.1903 | 5.6466
10 | 0.0099705 | 0.0024967 | -0.0099476 | -0.0024899 | 2.2846e-05 | 6.8348e-06 | 0.015246 | 0.015247 | 0.015247 | 0.97308 | -0.1903 | 0.97078 | -0.2069 | 5.6469
11 | 0.00014789 | 3.6715e-05 | -0.00014789 | -3.7064e-05 | 8.4187e-10 | -3.4856e-07 | 0.00022254 | 0.00022266 | 0.00022266 | 0.98829 | -0.083959 | 0.98829 | -0.084 | 0.082468
12 | -0.00071101 | -0.00017785 | 0.00071103 | 0.00017751 | 1.8999e-08 | -3.3326e-07 | 0.0010704 | 0.0010703 | 0.0010704 | 0.98829 | -0.083959 | 0.98832 | -0.083764 | 0.39645
13 | -0.00080085 | -0.00020002 | 0.00080087 | 0.00019968 | 2.5287e-08 | -3.4766e-07 | 0.0012055 | 0.0012054 | 0.0012055 | 0.98832 | -0.083764 | 0.98835 | -0.083534 | 0.44649
14 | 0.0040179 | 0.0009952 | -0.0040172 | -0.00099533 | 7.0463e-07 | -1.2493e-07 | 0.006045 | 0.0060451 | 0.0060451 | 0.98835 | -0.083534 | 0.98817 | -0.08483 | 2.2389
15 | -0.0048188 | -0.0011949 | 0.0048197 | 0.0011949 | 9.699e-07 | -5.9706e-09 | 0.0072504 | 0.0072503 | 0.0072504 | 0.98835 | -0.083534 | 0.98856 | -0.08205 | 2.6853
16 | 8.3689e-05 | 2.014e-05 | -8.3689e-05 | -2.0318e-05 | 1.3706e-10 | -1.7785e-07 | 0.00012573 | 0.00012579 | 0.00012579 | 0.98817 | -0.08483 | 0.98817 | -0.084843 | 0.046589
17 | 0.0039335 | 0.00097519 | -0.0039332 | -0.00097526 | 3.5148e-07 | -7.073e-08 | 0.0059194 | 0.0059195 | 0.0059195 | 0.98817 | -0.08483 | 0.98808 | -0.08549 | 2.1924
18 | -0.0050023 | -0.0012406 | 0.0050036 | 0.0012406 | 1.3486e-06 | 2.9217e-08 | 0.007525 | 0.0075248 | 0.007525 | 0.98856 | -0.08205 | 0.98883 | -0.080062 | 2.787
19 | 0.0033008 | 0.00081679 | -0.0033004 | -0.00081696 | 3.8102e-07 | -1.7038e-07 | 0.0049672 | 0.0049674 | 0.0049674 | 0.98807 | -0.085536 | 0.98796 | -0.086391 | 1.8398
20 | -0.0038734 | -0.00096029 | 0.0038734 | 0.00096029 | 2.4488e-08 | -5.3724e-09 | 0.0058295 | 0.0058295 | 0.0058295 | 0.98807 | -0.085536 | 0.98808 | -0.08549 | 2.1591
21 | 0.0031292 | 0.00077404 | -0.0031284 | -0.00077448 | 8.1148e-07 | -4.3847e-07 | 0.0047095 | 0.0047097 | 0.0047097 | 0.98796 | -0.086391 | 0.98769 | -0.088311 | 1.7443
22 | 0.0026167 | 0.00064625 | -0.0026117 | -0.00065094 | 5.0247e-06 | -4.6928e-06 | 0.0039389 | 0.0039412 | 0.0039412 | 0.98769 | -0.088311 | 0.98573 | -0.10247 | 1.4597
23 | 0.002358 | 0.00058736 | -0.0023577 | -0.0005878 | 3.584e-07 | -4.4031e-07 | 0.0035583 | 0.0035585 | 0.0035585 | 0.98573 | -0.10247 | 0.98558 | -0.10358 | 1.3179
24 | 8.3689e-05 | 2.0318e-05 | -8.3688e-05 | -2.0974e-05 | 5.0712e-10 | -6.5657e-07 | 0.00012579 | 0.00012602 | 0.00012602 | 0.98817 | -0.084843 | 0.98816 | -0.084888 | 0.046675
25 | -0.0050582 | -0.0012543 | 0.0050609 | 0.0012544 | 2.7003e-06 | 7.8705e-08 | 0.007607 | 0.0076067 | 0.007607 | 0.98883 | -0.080062 | 0.98938 | -0.076124 | 2.8174
26 | -0.0052149 | -0.001293 | 0.0052186 | 0.0012932 | 3.6189e-06 | 1.7874e-07 | 0.0078383 | 0.0078379 | 0.0078383 | 0.98938 | -0.076124 | 0.99008 | -0.071003 | 2.9031
27 | -0.0052186 | -0.0012932 | 0.005223 | 0.0012934 | 4.4882e-06 | 2.1907e-07 | 0.0078379 | 0.0078374 | 0.0078379 | 0.99008 | -0.071003 | 0.99096 | -0.06465 | 2.9029
28 | -0.00031411 | -7.8725e-05 | 0.00031413 | 7.7643e-05 | 1.2745e-08 | -1.0821e-06 | 0.00048184 | 0.00048145 | 0.00048184 | 0.97004 | -0.21223 | 0.97008 | -0.21194 | 0.17846
29 | -0.0011018 | -0.00027504 | 0.0011018 | 0.00027457 | 7.2191e-08 | -4.7265e-07 | 0.0016896 | 0.0016894 | 0.0016896 | 0.97008 | -0.21194 | 0.97015 | -0.21146 | 0.62578
30 | -0.0011018 | -0.00027457 | 0.0011019 | 0.00027442 | 2.381e-08 | -1.5592e-07 | 0.0016894 | 0.0016894 | 0.0016894 | 0.97015 | -0.21146 | 0.97017 | -0.2113 | 0.62572
31 | 0.0042579 | 0.001064 | -0.0042576 | -0.001064 | 3.1037e-07 | -2.5037e-08 | 0.0065254 | 0.0065254 | 0.0065254 | 0.97078 | -0.2069 | 0.9707 | -0.20743 | 2.4168
32 | 0.0056898 | 0.0014258 | -0.0056886 | -0.0014257 | 1.1283e-06 | 1.4011e-07 | 0.0087213 | 0.0087214 | 0.0087214 | 0.97078 | -0.2069 | 0.97058 | -0.20834 | 3.2301
33 | -0.002868 | -0.00071669 | 0.0028682 | 0.00071662 | 1.1852e-07 | -7.5671e-08 | 0.0043981 | 0.0043981 | 0.0043981 | 0.97017 | -0.2113 | 0.97021 | -0.211 | 1.6289
34 | 0.0017662 | 0.00044228 | -0.0017661 | -0.00044241 | 5.7955e-08 | -1.3401e-07 | 0.0027088 | 0.0027088 | 0.0027088 | 0.97017 | -0.2113 | 0.97014 | -0.21154 | 1.0033
35 | 0.0042576 | 0.001064 | -0.0042559 | -0.0010642 | 1.6555e-06 | -1.3314e-07 | 0.0065254 | 0.0065257 | 0.0065257 | 0.9707 | -0.20743 | 0.97031 | -0.21026 | 2.4169
36 | -0.0030617 | -0.00076514 | 0.0030621 | 0.00076497 | 3.1289e-07 | -1.6061e-07 | 0.004695 | 0.0046949 | 0.004695 | 0.97021 | -0.211 | 0.97031 | -0.21026 | 1.7389
37 | 0.0011474 | 0.00028734 | -0.0011473 | -0.00028752 | 3.0408e-08 | -1.8259e-07 | 0.0017598 | 0.0017598 | 0.0017598 | 0.97014 | -0.21154 | 0.97011 | -0.21173 | 0.65179
38 | 0.00072306 | 0.00018119 | -0.00072306 | -0.00018121 | 1.8128e-09 | -2.8464e-08 | 0.0011091 | 0.0011091 | 0.0011091 | 0.97011 | -0.21173 | 0.97011 | -0.21175 | 0.41077
39 | 0.00035812 | 8.8099e-05 | -0.00035812 | -8.8525e-05 | 5.8558e-09 | -4.257e-07 | 0.0005343 | 0.00053445 | 0.00053445 | 0.99629 | -0.026432 | 0.99628 | -0.026554 | 0.19794
40 | 0.00024726 | 6.1294e-05 | -0.00024726 | -6.1969e-05 | 4.419e-09 | -6.7492e-07 | 0.00036906 | 0.0003693 | 0.0003693 | 0.99629 | -0.026432 | 0.99628 | -0.026562 | 0.13678
41 | -0.0013294 | -0.00033084 | 0.0013298 | 0.00032891 | 3.9179e-07 | -1.9265e-06 | 0.0019847 | 0.0019839 | 0.0019847 | 0.99629 | -0.026432 | 0.9966 | -0.024261 | 0.73506
42 | 0.00019404 | 4.7677e-05 | -0.00019403 | -4.8392e-05 | 2.8795e-09 | -7.1537e-07 | 0.00028948 | 0.00028972 | 0.00028972 | 0.99628 | -0.026554 | 0.99626 | -0.026664 | 0.10731
43 | 0.00016408 | 4.0848e-05 | -0.00016408 | -4.1122e-05 | 7.8983e-10 | -2.7424e-07 | 0.00024497 | 0.00024507 | 0.00024507 | 0.99628 | -0.026554 | 0.99627 | -0.026589 | 0.090766
44 | 0.0082145 | 0.002041 | -0.0081997 | -0.0020373 | 1.4846e-05 | 3.6511e-06 | 0.012259 | 0.01226 | 0.01226 | 0.9966 | -0.024261 | 0.99474 | -0.037552 | 4.5406
45 | -0.0095443 | -0.0023699 | 0.0095661 | 0.002376 | 2.1848e-05 | 6.1485e-06 | 0.014243 | 0.014242 | 0.014243 | 0.9966 | -0.024261 | 0.99895 | -0.0074454 | 5.2751
46 | 0.00019403 | 4.8392e-05 | -0.00019403 | -4.8629e-05 | 9.5382e-10 | -2.3668e-07 | 0.00028972 | 0.00028981 | 0.00028981 | 0.99626 | -0.026664 | 0.99626 | -0.026699 | 0.10734
47 | 0.020043 | 0.0050487 | -0.020015 | -0.0050386 | 2.7789e-05 | 1.0036e-05 | 0.029867 | 0.029867 | 0.029867 | 0.99887 | -0.0078541 | 0.99744 | -0.017781 | 11.0618
48 | -0.020043 | -0.0050487 | 0.020065 | 0.0050551 | 2.203e-05 | 6.3985e-06 | 0.029867 | 0.029866 | 0.029867 | 0.99887 | -0.0078541 | 1 | 0 | 5.5309
49 | 0.020015 | 0.0050386 | -0.019981 | -0.0050264 | 3.3789e-05 | 1.2205e-05 | 0.029867 | 0.029867 | 0.029867 | 0.99744 | -0.017781 | 0.9957 | -0.029887 | 11.0619
50 | 0.012424 | 0.0030932 | -0.012413 | -0.0030896 | 1.1153e-05 | 3.6038e-06 | 0.01848 | 0.01848 | 0.01848 | 1 | 0 | 0.99907 | -0.0065747 | 6.8446
51 | 0.017958 | 0.0045193 | -0.017956 | -0.0045188 | 1.326e-06 | 4.7165e-07 | 0.026843 | 0.026843 | 0.026843 | 0.9957 | -0.029887 | 0.99563 | -0.030416 | 9.9419
52 | 0.010237 | 0.0025443 | -0.010236 | -0.002544 | 1.2139e-06 | 3.572e-07 | 0.01524 | 0.01524 | 0.01524 | 0.99907 | -0.0065747 | 0.99895 | -0.0074454 | 5.6445
53 | 0.0081997 | 0.0020373 | -0.0081825 | -0.0020331 | 1.7192e-05 | 4.238e-06 | 0.01226 | 0.01226 | 0.01226 | 0.99474 | -0.037552 | 0.99259 | -0.052973 | 4.5409
54 | 0.0079367 | 0.0019715 | -0.0079338 | -0.0019708 | 2.9426e-06 | 7.0092e-07 | 0.011892 | 0.011892 | 0.011892 | 0.99259 | -0.052973 | 0.99221 | -0.055699 | 4.4045
55 | -0.0065601 | -0.0016273 | 0.0065618 | 0.0016276 | 1.6236e-06 | 2.785e-07 | 0.0098447 | 0.0098446 | 0.0098447 | 0.99096 | -0.06465 | 0.99122 | -0.062826 | 3.6462
56 | 0.0013371 | 0.0003339 | -0.0013371 | -0.00033405 | 3.1852e-08 | -1.5095e-07 | 0.0020073 | 0.0020074 | 0.0020074 | 0.99096 | -0.06465 | 0.99094 | -0.064824 | 0.74347
57 | -0.0069091 | -0.0017146 | 0.0069094 | 0.0017147 | 3.4834e-07 | 6.7009e-08 | 0.010366 | 0.010366 | 0.010366 | 0.99122 | -0.062826 | 0.99127 | -0.062455 | 3.8392
58 | 0.0013371 | 0.00033405 | -0.001337 | -0.00033418 | 2.7321e-08 | -1.2946e-07 | 0.0020074 | 0.0020074 | 0.0020074 | 0.99094 | -0.064824 | 0.99092 | -0.064972 | 0.74349
59 | 0.01735 | 0.0043658 | -0.017346 | -0.0043646 | 3.3198e-06 | 1.1742e-06 | 0.025951 | 0.025951 | 0.025951 | 0.99507 | -0.034326 | 0.99487 | -0.035697 | 9.6115
60 | -0.017947 | -0.0045153 | 0.017956 | 0.0045188 | 9.7956e-06 | 3.4844e-06 | 0.026843 | 0.026843 | 0.026843 | 0.99507 | -0.034326 | 0.99563 | -0.030416 | 9.942
61 | 0.0077485 | 0.0019243 | -0.0077466 | -0.0019239 | 1.8872e-06 | 4.3634e-07 | 0.011614 | 0.011614 | 0.011614 | 0.99221 | -0.055699 | 0.99196 | -0.05749 | 4.3016
62 | 0.0076165 | 0.0018917 | -0.0076139 | -0.0018911 | 2.6459e-06 | 5.9804e-07 | 0.011419 | 0.01142 | 0.01142 | 0.99196 | -0.05749 | 0.9916 | -0.060045 | 4.2295
63 | 0.00013002 | 3.2168e-05 | -0.00013002 | -3.2587e-05 | 7.7064e-10 | -4.1909e-07 | 0.0001949 | 0.00019505 | 0.00019505 | 0.99196 | -0.05749 | 0.99195 | -0.057534 | 0.07224
64 | 0.0070179 | 0.0017418 | -0.0070156 | -0.0017413 | 2.2971e-06 | 4.5498e-07 | 0.010525 | 0.010525 | 0.010525 | 0.9916 | -0.060045 | 0.99127 | -0.062455 | 3.8983
65 | 0.0012703 | 0.00031746 | -0.0012703 | -0.00031762 | 3.0302e-08 | -1.6031e-07 | 0.0019072 | 0.0019073 | 0.0019073 | 0.99092 | -0.064972 | 0.99089 | -0.065145 | 0.70641
66 | 0.00080234 | 0.00020034 | -0.00080233 | -0.00020049 | 1.06e-08 | -1.4671e-07 | 0.0012046 | 0.0012047 | 0.0012047 | 0.99089 | -0.065145 | 0.99088 | -0.065241 | 0.44617
67 | -0.00062945 | -0.00015749 | 0.00062946 | 0.00015717 | 1.4475e-08 | -3.2895e-07 | 0.00094518 | 0.00094506 | 0.00094518 | 0.99086 | -0.065408 | 0.99088 | -0.065241 | 0.35007
68 | 0.00026383 | 6.5862e-05 | -0.00026383 | -6.5898e-05 | 2.8068e-10 | -3.6817e-08 | 0.00039611 | 0.00039612 | 0.00039612 | 0.99086 | -0.065408 | 0.99085 | -0.065416 | 0.14671
69 | 0.00020953 | 5.2291e-05 | -0.00020953 | -5.2513e-05 | 1.0684e-09 | -2.2238e-07 | 0.00031458 | 0.00031466 | 0.00031466 | 0.99085 | -0.065416 | 0.99085 | -0.065453 | 0.11654
70 | 0.0014067 | 0.00035103 | -0.0014066 | -0.00035125 | 5.4062e-08 | -2.2391e-07 | 0.0021236 | 0.0021237 | 0.0021237 | 0.98538 | -0.10499 | 0.98534 | -0.10527 | 0.78656
71 | -0.0016598 | -0.00041447 | 0.0016598 | 0.00041431 | 5.4899e-08 | -1.5737e-07 | 0.0025059 | 0.0025058 | 0.0025059 | 0.98538 | -0.10499 | 0.98542 | -0.10475 | 0.9281
72 | 0.0012059 | 0.00030095 | -0.0012059 | -0.00030097 | 3.261e-09 | -1.8828e-08 | 0.0018206 | 0.0018206 | 0.0018206 | 0.98534 | -0.10527 | 0.98534 | -0.10529 | 0.67431
73 | 0.00030009 | 7.45e-05 | -0.00030009 | -7.4982e-05 | 4.8591e-09 | -4.8159e-07 | 0.0004529 | 0.00045307 | 0.00045307 | 0.98542 | -0.10475 | 0.9854 | -0.10487 | 0.1678
74 | -0.0019599 | -0.00048881 | 0.0019602 | 0.0004882 | 3.1331e-07 | -6.1038e-07 | 0.0029587 | 0.0029584 | 0.0029587 | 0.98542 | -0.10475 | 0.98558 | -0.10358 | 1.0958
75 | 0.0005915 | 0.00014699 | -0.00059147 | -0.00014777 | 3.1206e-08 | -7.8684e-07 | 0.00089281 | 0.00089309 | 0.00089309 | 0.98534 | -0.10529 | 0.98529 | -0.10568 | 0.33077
76 | 0.00030009 | 7.4982e-05 | -0.00030008 | -7.5208e-05 | 2.2854e-09 | -2.2637e-07 | 0.00045307 | 0.00045315 | 0.00045315 | 0.9854 | -0.10487 | 0.98539 | -0.10492 | 0.16783
77 | 0.00039568 | 9.8705e-05 | -0.00039567 | -9.9164e-05 | 8.0771e-09 | -4.5868e-07 | 0.0005974 | 0.00059757 | 0.00059757 | 0.98529 | -0.10568 | 0.98527 | -0.10582 | 0.22132

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.034008 | 0.0083286

## res_load
| p_mw | q_mvar
0 | 0.0002609 | 6.5387e-05
1 | 0.0008147 | 0.00020418
2 | 0.0016769 | 0.00042028
3 | 0.00077232 | 0.00019356
4 | 0.00019948 | 4.9996e-05
5 | 0.00056312 | 0.00014113
6 | 0.00014789 | 3.7064e-05
7 | 8.9818e-05 | 2.2511e-05
8 | 0.00018251 | 4.5742e-05
9 | 0.00057259 | 0.0001435
10 | 0.00017123 | 4.2915e-05
11 | 5.9732e-05 | 1.497e-05
12 | 0.00051165 | 0.00012823
13 | 0.0002537 | 6.3583e-05
14 | 5.4618e-05 | 1.3689e-05
15 | 0.00015402 | 3.8601e-05
16 | 8.3688e-05 | 2.0974e-05
17 | 0.00031411 | 7.8725e-05
18 | 0.00078764 | 0.0001974
19 | 0.0056886 | 0.0014257
20 | 0.0001936 | 4.852e-05
21 | 0.00061875 | 0.00015507
22 | 0.00042428 | 0.00010633
23 | 0.00072306 | 0.00018121
24 | 0.0011938 | 0.0002992
25 | 0.00072398 | 0.00018145
26 | 0.00024726 | 6.1969e-05
27 | 0.00016408 | 4.1122e-05
28 | 0.00019403 | 4.8629e-05
29 | 0.00071938 | 0.00018029
30 | 0.0020235 | 0.00050713
31 | 0.0021756 | 0.00054525
32 | 0.00067006 | 0.00016793
33 | 0.00024576 | 6.1593e-05
34 | 0.0003473 | 8.7042e-05
35 | 0.00059673 | 0.00014955
36 | 0.0033855 | 0.00084847
37 | 0.00018533 | 4.6449e-05
38 | 0.00059595 | 0.00014936
39 | 0.00013002 | 3.2587e-05
40 | 0.00010624 | 2.6627e-05
41 | 6.672e-05 | 1.6722e-05
42 | 0.00046794 | 0.00011728
43 | 0.00036562 | 9.1633e-05
44 | 0.00017287 | 4.3325e-05
45 | 5.4295e-05 | 1.3608e-05
46 | 0.00020953 | 5.2513e-05
47 | 0.00025312 | 6.3439e-05
48 | 0.00020069 | 5.0299e-05
49 | 0.0006144 | 0.00015398
50 | 0.00039742 | 9.9602e-05
51 | 0.00019579 | 4.9069e-05
52 | 0.00030008 | 7.5208e-05
53 | 0.00039567 | 9.9164e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1