## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1098-32_1_2_node_7 | 0.4 | n |  | TRUE
1 | bus_LV_1098-32_1_2_node_72 | 0.4 | n |  | TRUE
2 | bus_LV_1098-32_1_2_node_73 | 0.4 | n |  | TRUE
3 | bus_LV_1098-32_1_2_node_9 | 0.4 | n |  | TRUE
4 | bus_LV_1098-32_1_2_node_44 | 0.4 | n |  | TRUE
5 | bus_LV_1098-32_1_2_node_69 | 0.4 | n |  | TRUE
6 | bus_LV_1098-32_1_2_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1098-32_1_2_node_67 | 0.4 | n |  | TRUE
8 | bus_LV_1098-32_1_2_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_1098-32_1_2_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_1098-32_1_2_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1098-32_1_2_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1098-32_1_2_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_1098-32_1_2_node_41 | 0.4 | n |  | TRUE
14 | bus_LV_1098-32_1_2_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1098-32_1_2_node_51 | 0.4 | n |  | TRUE
16 | bus_LV_1098-32_1_2_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_1098-32_1_2_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_1098-32_1_2_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1098-32_1_2_node_19 | 0.4 | n |  | TRUE
20 | bus_LV_1098-32_1_2_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_1098-32_1_2_node_32 | 0.4 | n |  | TRUE
22 | bus_LV_1098-32_1_2_node_75 | 0.4 | n |  | TRUE
23 | bus_LV_1098-32_1_2_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1098-32_1_2_node_23 | 0.4 | n |  | TRUE
25 | bus_LV_1098-32_1_2_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1098-32_1_2_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1098-32_1_2_node_39 | 0.4 | n |  | TRUE
28 | bus_LV_1098-32_1_2_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_1098-32_1_2_node_47 | 0.4 | n |  | TRUE
30 | bus_LV_1098-32_1_2_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1098-32_1_2_node_35 | 0.4 | n |  | TRUE
32 | bus_LV_1098-32_1_2_node_36 | 0.4 | n |  | TRUE
33 | bus_LV_1098-32_1_2_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_1098-32_1_2_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1098-32_1_2_node_43 | 0.4 | n |  | TRUE
36 | bus_LV_1098-32_1_2_node_49 | 0.4 | n |  | TRUE
37 | bus_LV_1098-32_1_2_node_45 | 0.4 | n |  | TRUE
38 | bus_LV_1098-32_1_2_node_48 | 0.4 | n |  | TRUE
39 | bus_LV_1098-32_1_2_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_1098-32_1_2_node_50 | 0.4 | n |  | TRUE
41 | bus_LV_1098-32_1_2_node_68 | 0.4 | n |  | TRUE
42 | bus_LV_1098-32_1_2_node_70 | 0.4 | n |  | TRUE
43 | bus_LV_1098-32_1_2_node_71 | 0.4 | n |  | TRUE
44 | bus_MV_2_1_node_195 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1098-32_1_2_load_7 | 0 | 0.0010479 | 0.00026263 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1098-32_1_2_load_72 | 1 | 0.0016472 | 0.00041283 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1098-32_1_2_load_44 | 4 | 0.002687 | 0.00067342 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1098-32_1_2_load_69 | 5 | 0.0009724 | 0.00024371 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1098-32_1_2_load_67 | 7 | 0.0010643 | 0.00026675 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1098-32_1_2_load_12 | 8 | 0.0021527 | 0.00053951 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1098-32_1_2_load_13 | 9 | 0.0017484 | 0.00043819 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1098-32_1_2_load_14 | 10 | 0.0016727 | 0.00041921 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1098-32_1_2_load_15 | 11 | 0.0016401 | 0.00041104 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1098-32_1_2_load_42 | 12 | 0.0018914 | 0.00047402 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1098-32_1_2_load_20 | 14 | 0.0022004 | 0.00055147 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1098-32_1_2_load_40 | 16 | 0.0055232 | 0.0013842 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1098-32_1_2_load_17 | 17 | 0.0021711 | 0.00054413 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1098-32_1_2_load_18 | 18 | 0.0021108 | 0.00052902 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1098-32_1_2_load_19 | 19 | 0.0020235 | 0.00050715 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1098-32_1_2_load_21 | 20 | 0.0021013 | 0.00052663 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1098-32_1_2_load_32 | 21 | 0.0022353 | 0.00056022 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1098-32_1_2_load_75 | 22 | 0.010187 | 0.0025531 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1098-32_1_2_load_22 | 23 | 0.0018075 | 0.00045301 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1098-32_1_2_load_23 | 24 | 0.0017736 | 0.00044452 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1098-32_1_2_load_24 | 25 | 0.002159 | 0.0005411 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1098-32_1_2_load_26 | 26 | 0.0057431 | 0.0014394 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1098-32_1_2_load_39 | 27 | 0.0068927 | 0.0017275 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1098-32_1_2_load_33 | 28 | 0.0052877 | 0.0013252 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1098-32_1_2_load_34 | 30 | 0.0013772 | 0.00034515 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1098-32_1_2_load_35 | 31 | 0.0041436 | 0.0010385 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1098-32_1_2_load_36 | 32 | 0.0013784 | 0.00034546 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1098-32_1_2_load_37 | 33 | 0.0014358 | 0.00035984 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1098-32_1_2_load_38 | 34 | 0.0044074 | 0.0011046 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1098-32_1_2_load_43 | 35 | 0.0014361 | 0.00035991 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1098-32_1_2_load_49 | 36 | 0.0056201 | 0.0014085 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1098-32_1_2_load_45 | 37 | 0.0038831 | 0.0009732 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1098-32_1_2_load_48 | 38 | 0.0022735 | 0.0005698 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1098-32_1_2_load_46 | 39 | 0.0039815 | 0.00099785 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1098-32_1_2_load_50 | 40 | 0.0017992 | 0.00045093 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1098-32_1_2_load_68 | 41 | 0.0025025 | 0.00062718 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1098-32_1_2_load_70 | 42 | 0.00095967 | 0.00024052 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1098-32_1_2_load_71 | 43 | 0.0010872 | 0.00027247 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1098-32_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.25972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1098-32_1_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.03689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1098-32_1_2_line_2 | NAYY 4x150 SE | 2 | 22 | 0.26716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1098-32_1_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.050067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1098-32_1_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.026381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1098-32_1_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.014842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1098-32_1_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0064028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1098-32_1_2_line_7 | NAYY 4x150 SE | 6 | 13 | 0.045836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1098-32_1_2_line_8 | NAYY 4x150 SE | 6 | 10 | 0.018314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1098-32_1_2_line_9 | NAYY 4x150 SE | 7 | 41 | 0.010965 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1098-32_1_2_line_10 | NAYY 4x150 SE | 8 | 9 | 0.016925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1098-32_1_2_line_11 | NAYY 4x150 SE | 8 | 10 | 0.0054413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1098-32_1_2_line_12 | NAYY 4x150 SE | 9 | 11 | 0.001115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1098-32_1_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.0080067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1098-32_1_2_line_14 | NAYY 4x150 SE | 12 | 14 | 0.01591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1098-32_1_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.024932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1098-32_1_2_line_16 | NAYY 4x150 SE | 13 | 16 | 0.017856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1098-32_1_2_line_17 | NAYY 4x150 SE | 14 | 18 | 0.00063447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1098-32_1_2_line_18 | NAYY 4x150 SE | 15 | 29 | 0.045391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1098-32_1_2_line_19 | NAYY 4x150 SE | 15 | 28 | 0.0031467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1098-32_1_2_line_20 | NAYY 4x150 SE | 16 | 27 | 0.012086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1098-32_1_2_line_21 | NAYY 4x150 SE | 17 | 18 | 0.0090994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1098-32_1_2_line_22 | NAYY 4x150 SE | 17 | 19 | 0.013487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1098-32_1_2_line_23 | NAYY 4x150 SE | 19 | 20 | 0.0029566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1098-32_1_2_line_24 | NAYY 4x150 SE | 20 | 21 | 0.007457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1098-32_1_2_line_25 | NAYY 4x150 SE | 21 | 22 | 0.047712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1098-32_1_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.017716 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1098-32_1_2_line_27 | NAYY 4x150 SE | 23 | 25 | 0.0037305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1098-32_1_2_line_28 | NAYY 4x150 SE | 25 | 26 | 0.0072862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1098-32_1_2_line_29 | NAYY 4x150 SE | 26 | 27 | 0.010264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1098-32_1_2_line_30 | NAYY 4x150 SE | 29 | 39 | 0.0038066 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1098-32_1_2_line_31 | NAYY 4x150 SE | 30 | 31 | 0.016109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1098-32_1_2_line_32 | NAYY 4x150 SE | 30 | 32 | 0.0070765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1098-32_1_2_line_33 | NAYY 4x150 SE | 31 | 33 | 0.012782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1098-32_1_2_line_34 | NAYY 4x150 SE | 32 | 34 | 0.0017796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1098-32_1_2_line_35 | NAYY 4x150 SE | 33 | 35 | 0.0073986 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1098-32_1_2_line_36 | NAYY 4x150 SE | 34 | 36 | 0.022334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1098-32_1_2_line_37 | NAYY 4x150 SE | 35 | 37 | 0.010908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1098-32_1_2_line_38 | NAYY 4x150 SE | 36 | 38 | 0.0016913 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1098-32_1_2_line_39 | NAYY 4x150 SE | 37 | 39 | 0.014302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1098-32_1_2_line_40 | NAYY 4x150 SE | 38 | 40 | 0.011081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1098-32_1_2_line_41 | NAYY 4x150 SE | 41 | 42 | 0.0039841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1098-32_1_2_line_42 | NAYY 4x150 SE | 42 | 43 | 0.005026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1098-32_1_2_trafo_13 | 0.25 MVA 20/0.4 kV | 44 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2650892.3294 | 1215174.5936 | 2650958.6211 | 1214923.4749
1 | 2650880.1348 | 1215208.8164 | 2650886.431 | 1215198.9197 | 2650892.3635 | 1215178.2468 | 2650892.3294 | 1215174.5936
2 | 2651130.5685 | 1215301.869 | 2650880.1348 | 1215208.8164
3 | 2651278.116 | 1215208.813 | 2651266.6617 | 1215257.5524
4 | 2651278.116 | 1215208.813 | 2651256.6003 | 1215203.814 | 2651252.6002 | 1215205.3695 | 2651252.6002 | 1215205.3695
5 | 2651263.266 | 1215272.0011 | 2651266.6617 | 1215257.5524
6 | 2651250.5374 | 1215211.4309 | 2651252.6002 | 1215205.3695
7 | 2651263.266 | 1215272.0011 | 2651260.3542 | 1215284.7726 | 2651259.1082 | 1215288.3752 | 2651256.18 | 1215296.8662 | 2651251.4345 | 1215316.2371
8 | 2651263.266 | 1215272.0011 | 2651244.9679 | 1215271.2331
9 | 2651250.5374 | 1215211.4309 | 2651247.6922 | 1215219.7915 | 2651247.3992 | 1215221.9047
10 | 2651239.5313 | 1215271.005 | 2651222.6215 | 1215270.2953
11 | 2651244.9679 | 1215271.2331 | 2651239.5313 | 1215271.005
12 | 2651221.5074 | 1215270.2485 | 2651222.6215 | 1215270.2953
13 | 2651221.5074 | 1215270.2485 | 2651213.5078 | 1215269.9128
14 | 2651213.5078 | 1215269.9128 | 2651197.6115 | 1215269.2456
15 | 2651251.4345 | 1215316.2371 | 2651245.6144 | 1215340.4794
16 | 2651251.4345 | 1215316.2371 | 2651233.6296 | 1215314.8887
17 | 2651197.6115 | 1215269.2456 | 2651196.9776 | 1215269.219
18 | 2651284.0383 | 1215325.4339 | 2651280.6942 | 1215329.3075 | 2651266.5308 | 1215341.8266 | 2651264.3343 | 1215342.9306 | 2651260.8685 | 1215343.301 | 2651254.7179 | 1215342.3921 | 2651245.6144 | 1215340.4794
19 | 2651245.6144 | 1215340.4794 | 2651245.0713 | 1215343.5789
20 | 2651221.5785 | 1215313.9761 | 2651233.6296 | 1215314.8887
21 | 2651187.8862 | 1215268.8375 | 2651196.9776 | 1215269.219
22 | 2651187.8862 | 1215268.8375 | 2651174.4113 | 1215268.272
23 | 2651171.4573 | 1215268.148 | 2651174.4113 | 1215268.272
24 | 2651164.0068 | 1215267.8353 | 2651171.4573 | 1215268.148
25 | 2651164.0068 | 1215267.8353 | 2651130.5685 | 1215301.869
26 | 2651205.6647 | 1215322.2517 | 2651206.1044 | 1215339.9627
27 | 2651205.5721 | 1215318.5223 | 2651205.6647 | 1215322.2517
28 | 2651205.5721 | 1215318.5223 | 2651205.5721 | 1215318.5223 | 2651210.077 | 1215314.7699 | 2651211.4536 | 1215314.4087
29 | 2651221.5785 | 1215313.9761 | 2651215.0012 | 1215313.478 | 2651211.4536 | 1215314.4087
30 | 2651284.0383 | 1215325.4339 | 2651283.7011 | 1215323.1407 | 2651283.8143 | 1215321.6562
31 | 2651298.0783 | 1215261.8541 | 2651294.2769 | 1215277.5084
32 | 2651298.0783 | 1215261.8541 | 2651299.7483 | 1215254.9775
33 | 2651294.2769 | 1215277.5084 | 2651291.2607 | 1215289.9289
34 | 2651300.1682 | 1215253.2481 | 2651299.7483 | 1215254.9775
35 | 2651289.5148 | 1215297.1186 | 2651291.2607 | 1215289.9289
36 | 2651305.4386 | 1215231.5446 | 2651300.1682 | 1215253.2481
37 | 2651286.9407 | 1215307.7187 | 2651289.5148 | 1215297.1186
38 | 2651305.8377 | 1215229.9011 | 2651305.4386 | 1215231.5446
39 | 2651286.9407 | 1215307.7187 | 2651283.9323 | 1215320.1076 | 2651283.8143 | 1215321.6562
40 | 2651305.8377 | 1215229.9011 | 2651308.4527 | 1215219.1326
41 | 2651247.3992 | 1215221.9047 | 2651246.8522 | 1215225.851
42 | 2651246.1621 | 1215230.8294 | 2651246.8522 | 1215225.851

## bus_geodata
| x | y | coords
0 | 2650958.6211 | 1214923.4749
1 | 2650892.3294 | 1215174.5936
2 | 2650880.1348 | 1215208.8164
3 | 2651278.116 | 1215208.813
4 | 2651266.6617 | 1215257.5524
5 | 2651252.6002 | 1215205.3695
6 | 2651263.266 | 1215272.0011
7 | 2651250.5374 | 1215211.4309
8 | 2651239.5313 | 1215271.005
9 | 2651222.6215 | 1215270.2953
10 | 2651244.9679 | 1215271.2331
11 | 2651221.5074 | 1215270.2485
12 | 2651213.5078 | 1215269.9128
13 | 2651251.4345 | 1215316.2371
14 | 2651197.6115 | 1215269.2456
15 | 2651245.6144 | 1215340.4794
16 | 2651233.6296 | 1215314.8887
17 | 2651187.8862 | 1215268.8375
18 | 2651196.9776 | 1215269.219
19 | 2651174.4113 | 1215268.272
20 | 2651171.4573 | 1215268.148
21 | 2651164.0068 | 1215267.8353
22 | 2651130.5685 | 1215301.869
23 | 2651205.6647 | 1215322.2517
24 | 2651206.1044 | 1215339.9627
25 | 2651205.5721 | 1215318.5223
26 | 2651211.4536 | 1215314.4087
27 | 2651221.5785 | 1215313.9761
28 | 2651245.0713 | 1215343.5789
29 | 2651284.0383 | 1215325.4339
30 | 2651298.0783 | 1215261.8541
31 | 2651294.2769 | 1215277.5084
32 | 2651299.7483 | 1215254.9775
33 | 2651291.2607 | 1215289.9289
34 | 2651300.1682 | 1215253.2481
35 | 2651289.5148 | 1215297.1186
36 | 2651305.4386 | 1215231.5446
37 | 2651286.9407 | 1215307.7187
38 | 2651305.8377 | 1215229.9011
39 | 2651283.8143 | 1215321.6562
40 | 2651308.4527 | 1215219.1326
41 | 2651247.3992 | 1215221.9047
42 | 2651246.8522 | 1215225.851
43 | 2651246.1621 | 1215230.8294
44 | 2651263.266 | 1215272.0011

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99571 | -0.030311 | 0.0010479 | 0.00026263
1 | 0.9961 | -0.027539 | 0.0016472 | 0.00041283
2 | 0.99624 | -0.026529 | 0 | 0
3 | 0.99511 | -0.03409 | 0 | 0
4 | 0.99558 | -0.030765 | 0.002687 | 0.00067342
5 | 0.99486 | -0.035843 | 0.0009724 | 0.00024371
6 | 0.99578 | -0.029378 | 0 | 0
7 | 0.99481 | -0.036206 | 0.0010643 | 0.00026675
8 | 0.9982 | -0.012533 | 0.0021527 | 0.00053951
9 | 1 | 0 | -0.10487 | -0.026174
10 | 0.99763 | -0.016455 | 0.0016727 | 0.00041921
11 | 0.99995 | -0.00032631 | 0.0016401 | 0.00041104
12 | 0.99964 | -0.0025392 | 0.0018914 | 0.00047402
13 | 0.99175 | -0.05761 | 0 | 0
14 | 0.99905 | -0.0066394 | 0.0022004 | 0.00055147
15 | 0.99042 | -0.066993 | 0 | 0
16 | 0.99114 | -0.061944 | 0.0055232 | 0.0013842
17 | 0.99875 | -0.0087437 | 0.0021711 | 0.00054413
18 | 0.99903 | -0.006789 | 0.0021108 | 0.00052902
19 | 0.99838 | -0.011349 | 0.0020235 | 0.00050715
20 | 0.99831 | -0.011861 | 0.0021013 | 0.00052663
21 | 0.99815 | -0.012994 | 0.0022353 | 0.00056022
22 | 0.99727 | -0.019184 | 0.010187 | 0.0025531
23 | 0.99057 | -0.065962 | 0.0018075 | 0.00045301
24 | 0.99053 | -0.066282 | 0.0017736 | 0.00044452
25 | 0.99059 | -0.065826 | 0.002159 | 0.0005411
26 | 0.99065 | -0.0654 | 0.0057431 | 0.0014394
27 | 0.99082 | -0.064202 | 0.0068927 | 0.0017275
28 | 0.9904 | -0.067163 | 0.0052877 | 0.0013252
29 | 0.98834 | -0.081686 | 0 | 0
30 | 0.98619 | -0.096887 | 0.0013772 | 0.00034515
31 | 0.98659 | -0.094101 | 0.0041436 | 0.0010385
32 | 0.98604 | -0.098012 | 0.0013784 | 0.00034546
33 | 0.98698 | -0.091349 | 0.0014358 | 0.00035984
34 | 0.986 | -0.098269 | 0.0044074 | 0.0011046
35 | 0.98722 | -0.089649 | 0.0014361 | 0.00035991
36 | 0.98569 | -0.10049 | 0.0056201 | 0.0014085
37 | 0.98759 | -0.086982 | 0.0038831 | 0.0009732
38 | 0.98568 | -0.10056 | 0.0022735 | 0.0005698
39 | 0.98817 | -0.082921 | 0.0039815 | 0.00099785
40 | 0.98565 | -0.10077 | 0.0017992 | 0.00045093
41 | 0.99474 | -0.036709 | 0.0025025 | 0.00062718
42 | 0.99473 | -0.036791 | 0.00095967 | 0.00024052
43 | 0.99472 | -0.036846 | 0.0010872 | 0.00027247
44 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0010479 | -0.00026263 | 0.0010483 | 0.00025941 | 3.9717e-07 | -3.2267e-06 | 0.001566 | 0.0015649 | 0.001566 | 0.99571 | -0.030311 | 0.9961 | -0.027539 | 0.58002
1 | -0.0026955 | -0.00067224 | 0.0026959 | 0.0006719 | 3.7301e-07 | -3.3681e-07 | 0.0040255 | 0.0040254 | 0.0040255 | 0.9961 | -0.027539 | 0.99624 | -0.026529 | 1.4909
2 | -0.0026959 | -0.0006719 | 0.0026986 | 0.00066946 | 2.7005e-06 | -2.4436e-06 | 0.0040254 | 0.0040241 | 0.0040254 | 0.99624 | -0.026529 | 0.99727 | -0.019184 | 1.4909
3 | -0.0065883 | -0.0016508 | 0.0065913 | 0.0016513 | 3.032e-06 | 5.1541e-07 | 0.0098515 | 0.0098513 | 0.0098515 | 0.99511 | -0.03409 | 0.99558 | -0.030765 | 3.6487
4 | 0.0065883 | 0.0016508 | -0.0065867 | -0.0016505 | 1.5976e-06 | 2.7184e-07 | 0.0098515 | 0.0098516 | 0.0098516 | 0.99511 | -0.03409 | 0.99486 | -0.035843 | 3.6487
5 | -0.0092783 | -0.0023247 | 0.00928 | 0.0023252 | 1.781e-06 | 4.9196e-07 | 0.013867 | 0.013867 | 0.013867 | 0.99558 | -0.030765 | 0.99578 | -0.029378 | 5.136
6 | 0.0056143 | 0.0014068 | -0.005614 | -0.0014068 | 2.8172e-07 | 2.522e-08 | 0.0083972 | 0.0083972 | 0.0083972 | 0.99486 | -0.035843 | 0.99481 | -0.036206 | 3.1101
7 | 0.061355 | 0.015431 | -0.061114 | -0.015339 | 0.00024053 | 9.1916e-05 | 0.091703 | 0.091703 | 0.091703 | 0.99578 | -0.029378 | 0.99175 | -0.05761 | 33.9642
8 | -0.070635 | -0.017756 | 0.070762 | 0.017805 | 0.00012737 | 4.8749e-05 | 0.10557 | 0.10557 | 0.10557 | 0.99578 | -0.029378 | 0.99763 | -0.016455 | 39.1001
9 | 0.0045497 | 0.00114 | -0.0045493 | -0.0011401 | 3.1687e-07 | -2.0481e-08 | 0.0068052 | 0.0068053 | 0.0068053 | 0.99481 | -0.036206 | 0.99474 | -0.036709 | 2.5205
10 | -0.074627 | -0.018779 | 0.074758 | 0.018829 | 0.00013077 | 5.0073e-05 | 0.11127 | 0.11127 | 0.11127 | 0.9982 | -0.012533 | 1 | 0 | 41.2126
11 | 0.072475 | 0.018239 | -0.072435 | -0.018224 | 3.9651e-05 | 1.5179e-05 | 0.10807 | 0.10807 | 0.10807 | 0.9982 | -0.012533 | 0.99763 | -0.016455 | 40.0241
12 | 0.029312 | 0.0073449 | -0.02931 | -0.0073444 | 1.3236e-06 | 4.9446e-07 | 0.043616 | 0.043616 | 0.043616 | 1 | 0 | 0.99995 | -0.00032631 | 16.154
13 | 0.02767 | 0.0069334 | -0.027662 | -0.0069302 | 8.4706e-06 | 3.1529e-06 | 0.041175 | 0.041175 | 0.041175 | 0.99995 | -0.00032631 | 0.99964 | -0.0025392 | 15.2501
14 | 0.02577 | 0.0064562 | -0.025756 | -0.0064508 | 1.4609e-05 | 5.4103e-06 | 0.03836 | 0.03836 | 0.03836 | 0.99964 | -0.0025392 | 0.99905 | -0.0066394 | 14.2074
15 | 0.037193 | 0.0093417 | -0.037144 | -0.0093234 | 4.846e-05 | 1.8317e-05 | 0.055811 | 0.055811 | 0.055811 | 0.99175 | -0.05761 | 0.99042 | -0.066993 | 20.6708
16 | 0.023922 | 0.0059975 | -0.023907 | -0.0059922 | 1.4354e-05 | 5.2905e-06 | 0.035893 | 0.035893 | 0.035893 | 0.99175 | -0.05761 | 0.99114 | -0.061944 | 13.2936
17 | 0.023555 | 0.0058993 | -0.023555 | -0.0058992 | 4.8728e-07 | 1.7911e-07 | 0.035083 | 0.035083 | 0.035083 | 0.99905 | -0.0066394 | 0.99903 | -0.006789 | 12.9936
18 | 0.031857 | 0.0079982 | -0.031792 | -0.0079738 | 6.4896e-05 | 2.4377e-05 | 0.047866 | 0.047867 | 0.047867 | 0.99042 | -0.066993 | 0.98834 | -0.081686 | 17.7284
19 | 0.0052879 | 0.0013252 | -0.0052877 | -0.0013252 | 1.2393e-07 | 7.1711e-09 | 0.0079445 | 0.0079445 | 0.0079445 | 0.99042 | -0.066993 | 0.9904 | -0.067163 | 2.9424
20 | 0.018384 | 0.0046079 | -0.018378 | -0.0046059 | 5.745e-06 | 2.0539e-06 | 0.027601 | 0.027601 | 0.027601 | 0.99114 | -0.061944 | 0.99082 | -0.064202 | 10.2225
21 | -0.021438 | -0.005368 | 0.021444 | 0.0053701 | 5.792e-06 | 2.1086e-06 | 0.031939 | 0.031939 | 0.031939 | 0.99875 | -0.0087437 | 0.99903 | -0.006789 | 11.8291
22 | 0.019267 | 0.0048239 | -0.01926 | -0.0048214 | 6.9339e-06 | 2.4905e-06 | 0.028704 | 0.028704 | 0.028704 | 0.99875 | -0.0087437 | 0.99838 | -0.011349 | 10.6311
23 | 0.017237 | 0.0043143 | -0.017236 | -0.0043138 | 1.2174e-06 | 4.2958e-07 | 0.025688 | 0.025688 | 0.025688 | 0.99838 | -0.011349 | 0.99831 | -0.011861 | 9.5141
24 | 0.015134 | 0.0037872 | -0.015132 | -0.0037864 | 2.3674e-06 | 8.1306e-07 | 0.022556 | 0.022556 | 0.022556 | 0.99831 | -0.011861 | 0.99815 | -0.012994 | 8.3541
25 | 0.012897 | 0.0032262 | -0.012886 | -0.0032225 | 1.1002e-05 | 3.6086e-06 | 0.019224 | 0.019224 | 0.019224 | 0.99815 | -0.012994 | 0.99727 | -0.019184 | 7.12
26 | 0.0017737 | 0.00044432 | -0.0017736 | -0.00044452 | 7.848e-08 | -1.9787e-07 | 0.0026644 | 0.0026644 | 0.0026644 | 0.99057 | -0.065962 | 0.99053 | -0.066282 | 0.98683
27 | -0.0035813 | -0.00089733 | 0.0035813 | 0.00089731 | 6.7368e-08 | -2.2114e-08 | 0.0053796 | 0.0053796 | 0.0053796 | 0.99057 | -0.065962 | 0.99059 | -0.065826 | 1.9924
28 | -0.0057403 | -0.0014384 | 0.0057407 | 0.0014384 | 3.3805e-07 | 3.6213e-08 | 0.0086228 | 0.0086227 | 0.0086228 | 0.99059 | -0.065826 | 0.99065 | -0.0654 | 3.1936
29 | -0.011484 | -0.0028778 | 0.011486 | 0.0028784 | 1.9056e-06 | 6.0075e-07 | 0.017249 | 0.017249 | 0.017249 | 0.99065 | -0.0654 | 0.99082 | -0.064202 | 6.3886
30 | 0.031792 | 0.0079738 | -0.031786 | -0.0079718 | 5.4424e-06 | 2.0445e-06 | 0.047867 | 0.047867 | 0.047867 | 0.98834 | -0.081686 | 0.98817 | -0.082921 | 17.7284
31 | -0.016862 | -0.0042262 | 0.016868 | 0.0042285 | 6.5067e-06 | 2.2969e-06 | 0.025442 | 0.025442 | 0.025442 | 0.98619 | -0.096887 | 0.98659 | -0.094101 | 9.423
32 | 0.015485 | 0.0038811 | -0.015482 | -0.0038802 | 2.4105e-06 | 8.3683e-07 | 0.023364 | 0.023364 | 0.023364 | 0.98619 | -0.096887 | 0.98604 | -0.098012 | 8.6534
33 | -0.021012 | -0.005267 | 0.02102 | 0.0052699 | 8.0104e-06 | 2.9176e-06 | 0.031692 | 0.031691 | 0.031692 | 0.98659 | -0.094101 | 0.98698 | -0.091349 | 11.7376
34 | 0.014104 | 0.0035348 | -0.014103 | -0.0035346 | 5.0305e-07 | 1.7078e-07 | 0.021284 | 0.021284 | 0.021284 | 0.98604 | -0.098012 | 0.986 | -0.098269 | 7.8829
35 | -0.022456 | -0.0056298 | 0.022461 | 0.0056317 | 5.2919e-06 | 1.9408e-06 | 0.033856 | 0.033856 | 0.033856 | 0.98698 | -0.091349 | 0.98722 | -0.089649 | 12.5393
36 | 0.009696 | 0.00243 | -0.009693 | -0.0024291 | 2.984e-06 | 8.6293e-07 | 0.014633 | 0.014633 | 0.014633 | 0.986 | -0.098269 | 0.98569 | -0.10049 | 5.4195
37 | -0.023897 | -0.0059916 | 0.023906 | 0.0059949 | 8.8316e-06 | 3.2572e-06 | 0.036021 | 0.036021 | 0.036021 | 0.98722 | -0.089649 | 0.98759 | -0.086982 | 13.341
38 | 0.0040728 | 0.0010206 | -0.0040728 | -0.0010206 | 3.9897e-08 | -6.2133e-09 | 0.0061484 | 0.0061484 | 0.0061484 | 0.98569 | -0.10049 | 0.98568 | -0.10056 | 2.2772
39 | -0.027789 | -0.0069681 | 0.027805 | 0.0069739 | 1.5647e-05 | 5.8348e-06 | 0.041871 | 0.041871 | 0.041871 | 0.98759 | -0.086982 | 0.98817 | -0.082921 | 15.5079
40 | 0.0017993 | 0.00045081 | -0.0017992 | -0.00045093 | 5.1018e-08 | -1.2162e-07 | 0.0027162 | 0.0027163 | 0.0027163 | 0.98568 | -0.10056 | 0.98565 | -0.10077 | 1.006
41 | 0.0020469 | 0.00051288 | -0.0020468 | -0.00051292 | 2.3307e-08 | -4.2755e-08 | 0.0030618 | 0.0030619 | 0.0030619 | 0.99474 | -0.036709 | 0.99473 | -0.036791 | 1.134
42 | 0.0010872 | 0.00027241 | -0.0010872 | -0.00027247 | 8.2947e-09 | -6.2053e-08 | 0.0016263 | 0.0016263 | 0.0016263 | 0.99473 | -0.036791 | 0.99472 | -0.036846 | 0.60233

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10662 | 0.026612

## res_load
| p_mw | q_mvar
0 | 0.0010479 | 0.00026263
1 | 0.0016472 | 0.00041283
2 | 0.002687 | 0.00067342
3 | 0.0009724 | 0.00024371
4 | 0.0010643 | 0.00026675
5 | 0.0021527 | 0.00053951
6 | 0.0017484 | 0.00043819
7 | 0.0016727 | 0.00041921
8 | 0.0016401 | 0.00041104
9 | 0.0018914 | 0.00047402
10 | 0.0022004 | 0.00055147
11 | 0.0055232 | 0.0013842
12 | 0.0021711 | 0.00054413
13 | 0.0021108 | 0.00052902
14 | 0.0020235 | 0.00050715
15 | 0.0021013 | 0.00052663
16 | 0.0022353 | 0.00056022
17 | 0.010187 | 0.0025531
18 | 0.0018075 | 0.00045301
19 | 0.0017736 | 0.00044452
20 | 0.002159 | 0.0005411
21 | 0.0057431 | 0.0014394
22 | 0.0068927 | 0.0017275
23 | 0.0052877 | 0.0013252
24 | 0.0013772 | 0.00034515
25 | 0.0041436 | 0.0010385
26 | 0.0013784 | 0.00034546
27 | 0.0014358 | 0.00035984
28 | 0.0044074 | 0.0011046
29 | 0.0014361 | 0.00035991
30 | 0.0056201 | 0.0014085
31 | 0.0038831 | 0.0009732
32 | 0.0022735 | 0.0005698
33 | 0.0039815 | 0.00099785
34 | 0.0017992 | 0.00045093
35 | 0.0025025 | 0.00062718
36 | 0.00095967 | 0.00024052
37 | 0.0010872 | 0.00027247

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1