## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1098-35_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1098-35_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1098-35_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1098-35_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1098-35_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1098-35_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1098-35_0_3_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1098-35_0_3_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1098-35_0_3_node_20 | 0.4 | n |  | TRUE
9 | bus_LV_1098-35_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1098-35_0_3_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_1098-35_0_3_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1098-35_0_3_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_1098-35_0_3_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_1098-35_0_3_node_41 | 0.4 | n |  | TRUE
15 | bus_LV_1098-35_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1098-35_0_3_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_1098-35_0_3_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1098-35_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_1098-35_0_3_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_1098-35_0_3_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_1098-35_0_3_node_24 | 0.4 | n |  | TRUE
22 | bus_LV_1098-35_0_3_node_49 | 0.4 | n |  | TRUE
23 | bus_LV_1098-35_0_3_node_25 | 0.4 | n |  | TRUE
24 | bus_LV_1098-35_0_3_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_1098-35_0_3_node_47 | 0.4 | n |  | TRUE
26 | bus_LV_1098-35_0_3_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_1098-35_0_3_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_1098-35_0_3_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_1098-35_0_3_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_1098-35_0_3_node_15 | 0.4 | n |  | TRUE
31 | bus_LV_1098-35_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1098-35_0_3_node_18 | 0.4 | n |  | TRUE
33 | bus_LV_1098-35_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1098-35_0_3_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_1098-35_0_3_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1098-35_0_3_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1098-35_0_3_node_44 | 0.4 | n |  | TRUE
38 | bus_LV_1098-35_0_3_node_39 | 0.4 | n |  | TRUE
39 | bus_LV_1098-35_0_3_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_1098-35_0_3_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1098-35_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1098-35_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1098-35_0_3_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_1098-35_0_3_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_1098-35_0_3_node_38 | 0.4 | n |  | TRUE
46 | bus_MV_2_1_node_278 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1098-35_0_3_load_0 | 0 | 0.023439 | 0.0058743 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1098-35_0_3_load_1 | 1 | 0.018058 | 0.0045258 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1098-35_0_3_load_5 | 5 | 0.016635 | 0.0041692 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1098-35_0_3_load_8 | 7 | 0.0014379 | 0.00036036 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1098-35_0_3_load_50 | 10 | 0.0053908 | 0.0013511 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1098-35_0_3_load_46 | 12 | 0.00604 | 0.0015138 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1098-35_0_3_load_41 | 14 | 0.0069753 | 0.0017482 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1098-35_0_3_load_9 | 15 | 0.00044193 | 0.00011076 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1098-35_0_3_load_30 | 16 | 0.0063867 | 0.0016007 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1098-35_0_3_load_48 | 19 | 0.0053849 | 0.0013496 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1098-35_0_3_load_49 | 22 | 0.0053846 | 0.0013495 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1098-35_0_3_load_47 | 25 | 0.025821 | 0.0064713 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1098-35_0_3_load_11 | 26 | 0.0055034 | 0.0013793 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1098-35_0_3_load_12 | 27 | 0.010315 | 0.0025851 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1098-35_0_3_load_13 | 28 | 0.012307 | 0.0030845 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1098-35_0_3_load_14 | 29 | 0.004682 | 0.0011734 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1098-35_0_3_load_15 | 30 | 0.0043996 | 0.0011026 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1098-35_0_3_load_16 | 31 | 0.001322 | 0.00033133 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1098-35_0_3_load_27 | 33 | 0.0047616 | 0.0011934 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1098-35_0_3_load_31 | 34 | 0.013196 | 0.0033072 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1098-35_0_3_load_21 | 35 | 0.00064418 | 0.00016145 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1098-35_0_3_load_22 | 36 | 0.0026732 | 0.00066998 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1098-35_0_3_load_44 | 37 | 0.0015795 | 0.00039587 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1098-35_0_3_load_39 | 38 | 0.017284 | 0.0043317 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1098-35_0_3_load_35 | 39 | 0.0038054 | 0.00095372 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1098-35_0_3_load_32 | 40 | 0.012562 | 0.0031484 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1098-35_0_3_load_34 | 42 | 0.0081983 | 0.0020547 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1098-35_0_3_load_36 | 43 | 0.0044526 | 0.0011159 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1098-35_0_3_load_37 | 44 | 0.0040478 | 0.0010145 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1098-35_0_3_load_38 | 45 | 0.0016682 | 0.00041808 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 3 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1098-35_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.037546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1098-35_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.034462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1098-35_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.015388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1098-35_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.023938 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1098-35_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.021655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1098-35_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.032166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1098-35_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.034661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1098-35_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.037171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1098-35_0_3_line_8 | NAYY 4x150 SE | 6 | 13 | 0.017083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1098-35_0_3_line_9 | NAYY 4x150 SE | 6 | 14 | 0.023934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1098-35_0_3_line_10 | NAYY 4x150 SE | 7 | 15 | 0.077052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1098-35_0_3_line_11 | NAYY 4x150 SE | 8 | 16 | 0.00044103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1098-35_0_3_line_12 | NAYY 4x150 SE | 8 | 17 | 0.051179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1098-35_0_3_line_13 | NAYY 4x150 SE | 9 | 10 | 0.007148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1098-35_0_3_line_14 | NAYY 4x150 SE | 9 | 11 | 0.028407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1098-35_0_3_line_15 | NAYY 4x150 SE | 11 | 12 | 0.018657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1098-35_0_3_line_16 | NAYY 4x150 SE | 12 | 24 | 0.0055974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1098-35_0_3_line_17 | NAYY 4x150 SE | 13 | 25 | 0.002607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1098-35_0_3_line_18 | NAYY 4x150 SE | 13 | 24 | 0.010868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1098-35_0_3_line_19 | NAYY 4x150 SE | 14 | 21 | 0.008373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1098-35_0_3_line_20 | NAYY 4x150 SE | 16 | 34 | 0.019316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1098-35_0_3_line_21 | NAYY 4x150 SE | 17 | 30 | 0.013187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1098-35_0_3_line_22 | NAYY 4x150 SE | 18 | 19 | 0.010967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1098-35_0_3_line_23 | NAYY 4x150 SE | 18 | 20 | 0.039342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1098-35_0_3_line_24 | NAYY 4x150 SE | 18 | 21 | 0.028266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1098-35_0_3_line_25 | NAYY 4x150 SE | 20 | 22 | 0.022267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1098-35_0_3_line_26 | NAYY 4x150 SE | 20 | 23 | 0.045358 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1098-35_0_3_line_27 | NAYY 4x150 SE | 21 | 36 | 0.032058 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1098-35_0_3_line_28 | NAYY 4x150 SE | 23 | 37 | 0.0067372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1098-35_0_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.0093474 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1098-35_0_3_line_30 | NAYY 4x150 SE | 26 | 28 | 0.0080551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1098-35_0_3_line_31 | NAYY 4x150 SE | 27 | 29 | 0.008304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1098-35_0_3_line_32 | NAYY 4x150 SE | 28 | 30 | 0.023114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1098-35_0_3_line_33 | NAYY 4x150 SE | 28 | 31 | 0.068462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1098-35_0_3_line_34 | NAYY 4x150 SE | 29 | 32 | 0.0079091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1098-35_0_3_line_35 | NAYY 4x150 SE | 32 | 33 | 0.036373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1098-35_0_3_line_36 | NAYY 4x150 SE | 34 | 40 | 0.0044317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1098-35_0_3_line_37 | NAYY 4x150 SE | 35 | 36 | 0.0085615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1098-35_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.002092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1098-35_0_3_line_39 | NAYY 4x150 SE | 39 | 41 | 0.040204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1098-35_0_3_line_40 | NAYY 4x150 SE | 40 | 41 | 0.011428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1098-35_0_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.023699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1098-35_0_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.010858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1098-35_0_3_line_43 | NAYY 4x150 SE | 43 | 44 | 0.021211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1098-35_0_3_line_44 | NAYY 4x150 SE | 44 | 45 | 0.006946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1098-35_0_3_trafo_3 | 0.25 MVA 20/0.4 kV | 46 | 3 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2651126.8316 | 1215461.7327 | 2651160.9921 | 1215446.1516
1 | 2651099.7068 | 1215478.2993 | 2651123.918 | 1215466.3996 | 2651122.788 | 1215463.5771 | 2651126.8316 | 1215461.7327
2 | 2651174.9922 | 1215439.766 | 2651160.9921 | 1215446.1516
3 | 2651081.2334 | 1215463.0764 | 2651095.8312 | 1215475.1086 | 2651099.7068 | 1215478.2993
4 | 2651174.9922 | 1215439.766 | 2651180.3739 | 1215444.4261 | 2651186.7603 | 1215445.2814 | 2651194.7782 | 1215444.1854
5 | 2651081.2334 | 1215463.0764 | 2651098.0395 | 1215445.1429 | 2651101.0455 | 1215438.1756
6 | 2651081.2334 | 1215463.0764 | 2651078.0515 | 1215460.4475 | 2651054.7936 | 1215440.665
7 | 2651231.1882 | 1215440.1375 | 2651221.1858 | 1215439.4623 | 2651208.3618 | 1215443.7325 | 2651199.4638 | 1215443.5449 | 2651194.7782 | 1215444.1854
8 | 2651101.0455 | 1215438.1756 | 2651108.8724 | 1215434.8629 | 2651106.9342 | 1215430.6437 | 2651110.5247 | 1215429.018
9 | 2651101.0455 | 1215438.1756 | 2651099.4761 | 1215436.1164 | 2651086.5264 | 1215419.1483
10 | 2651054.7936 | 1215440.665 | 2650996.1011 | 1215390.7425
11 | 2651231.1882 | 1215440.1375 | 2651231.2409 | 1215439.6996
12 | 2651231.1882 | 1215440.1375 | 2651230.1493 | 1215448.8116 | 2651227.6053 | 1215470.0469 | 2651227.0818 | 1215474.4117 | 2651227.6424 | 1215481.6319 | 2651231.1895 | 1215490.3565
13 | 2651152.5129 | 1215404.6744 | 2651149.5008 | 1215398.1891
14 | 2651140.3261 | 1215421.4021 | 2651156.7666 | 1215414.2499 | 2651153.7655 | 1215407.3645 | 2651152.5129 | 1215404.6744
15 | 2651140.3261 | 1215421.4021 | 2651123.1723 | 1215428.738
16 | 2651118.0258 | 1215430.9389 | 2651123.1723 | 1215428.738
17 | 2651109.5278 | 1215426.608 | 2651110.5247 | 1215429.018
18 | 2651118.0258 | 1215430.9389 | 2651115.9453 | 1215426.4962 | 2651110.5247 | 1215429.018
19 | 2651081.4466 | 1215412.4923 | 2651086.5264 | 1215419.1483
20 | 2651231.2409 | 1215439.6996 | 2651233.1265 | 1215424.0111 | 2651233.5449 | 1215420.5219
21 | 2651231.1895 | 1215490.3565 | 2651242.7212 | 1215483.9589
22 | 2651099.6311 | 1215385.2539 | 2651103.9184 | 1215395.3523
23 | 2651103.9184 | 1215395.3523 | 2651117.9671 | 1215384.644 | 2651135.4435 | 1215371.8194
24 | 2651081.4466 | 1215412.4923 | 2651089.8774 | 1215406.0606 | 2651091.4201 | 1215405.0288 | 2651103.9184 | 1215395.3523
25 | 2651135.4435 | 1215371.8194 | 2651145.6191 | 1215363.8352 | 2651141.8121 | 1215355.2863
26 | 2651135.4435 | 1215371.8194 | 2651114.1169 | 1215346.5993 | 2651102.3889 | 1215342.5742
27 | 2651081.4466 | 1215412.4923 | 2651062.3277 | 1215386.7598
28 | 2651102.3889 | 1215342.5742 | 2651107.8116 | 1215338.5761
29 | 2651269.828 | 1215468.5741 | 2651275.2098 | 1215465.4754 | 2651277.826 | 1215463.7441
30 | 2651269.828 | 1215468.5741 | 2651262.8473 | 1215472.5935
31 | 2651284.751 | 1215459.1614 | 2651277.826 | 1215463.7441
32 | 2651242.7212 | 1215483.9589 | 2651253.3312 | 1215478.0727 | 2651262.8473 | 1215472.5935
33 | 2651262.8473 | 1215472.5935 | 2651298.621 | 1215530.965
34 | 2651291.3466 | 1215454.7966 | 2651284.751 | 1215459.1614
35 | 2651291.3466 | 1215454.7966 | 2651288.0572 | 1215443.4949 | 2651290.0274 | 1215421.91 | 2651290.8146 | 1215419.0897
36 | 2651233.5449 | 1215420.5219 | 2651234.0725 | 1215416.1218
37 | 2651062.3277 | 1215386.7598 | 2651057.2216 | 1215379.8876
38 | 2651241.6779 | 1215362.9473 | 2651241.3168 | 1215365.0079
39 | 2651235.4332 | 1215404.7749 | 2651239.6414 | 1215374.5707 | 2651241.3168 | 1215365.0079
40 | 2651235.4332 | 1215404.7749 | 2651234.0725 | 1215416.1218
41 | 2651235.4332 | 1215404.7749 | 2651221.1971 | 1215398.3822 | 2651215.2351 | 1215392.9089
42 | 2651207.2364 | 1215385.5657 | 2651207.2364 | 1215385.5657 | 2651215.2351 | 1215392.9089
43 | 2651207.2364 | 1215385.5657 | 2651206.71 | 1215364.361
44 | 2651206.71 | 1215364.361 | 2651206.5376 | 1215357.4171

## bus_geodata
| x | y | coords
0 | 2651126.8316 | 1215461.7327
1 | 2651160.9921 | 1215446.1516
2 | 2651099.7068 | 1215478.2993
3 | 2651174.9922 | 1215439.766
4 | 2651081.2334 | 1215463.0764
5 | 2651194.7782 | 1215444.1854
6 | 2651101.0455 | 1215438.1756
7 | 2651054.7936 | 1215440.665
8 | 2651231.1882 | 1215440.1375
9 | 2651152.5129 | 1215404.6744
10 | 2651149.5008 | 1215398.1891
11 | 2651140.3261 | 1215421.4021
12 | 2651123.1723 | 1215428.738
13 | 2651110.5247 | 1215429.018
14 | 2651086.5264 | 1215419.1483
15 | 2650996.1011 | 1215390.7425
16 | 2651231.2409 | 1215439.6996
17 | 2651231.1895 | 1215490.3565
18 | 2651103.9184 | 1215395.3523
19 | 2651099.6311 | 1215385.2539
20 | 2651135.4435 | 1215371.8194
21 | 2651081.4466 | 1215412.4923
22 | 2651141.8121 | 1215355.2863
23 | 2651102.3889 | 1215342.5742
24 | 2651118.0258 | 1215430.9389
25 | 2651109.5278 | 1215426.608
26 | 2651269.828 | 1215468.5741
27 | 2651277.826 | 1215463.7441
28 | 2651262.8473 | 1215472.5935
29 | 2651284.751 | 1215459.1614
30 | 2651242.7212 | 1215483.9589
31 | 2651298.621 | 1215530.965
32 | 2651291.3466 | 1215454.7966
33 | 2651290.8146 | 1215419.0897
34 | 2651233.5449 | 1215420.5219
35 | 2651057.2216 | 1215379.8876
36 | 2651062.3277 | 1215386.7598
37 | 2651107.8116 | 1215338.5761
38 | 2651241.6779 | 1215362.9473
39 | 2651241.3168 | 1215365.0079
40 | 2651234.0725 | 1215416.1218
41 | 2651235.4332 | 1215404.7749
42 | 2651215.2351 | 1215392.9089
43 | 2651207.2364 | 1215385.5657
44 | 2651206.71 | 1215364.361
45 | 2651206.5376 | 1215357.4171
46 | 2651156.7666 | 1215414.2499

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99308 | -0.04815 | 0.023439 | 0.0058743
1 | 0.99771 | -0.015904 | 0.018058 | 0.0045258
2 | 0.99 | -0.069777 | 0 | 0
3 | 1 | 0 | -0.23781 | -0.059685
4 | 0.98786 | -0.084878 | 0 | 0
5 | 0.99795 | -0.014247 | 0.016635 | 0.0041692
6 | 0.98507 | -0.10465 | 0 | 0
7 | 0.98776 | -0.085548 | 0.0014379 | 0.00036036
8 | 0.99488 | -0.035719 | 0 | 0
9 | 0.98351 | -0.11576 | 0 | 0
10 | 0.98345 | -0.11616 | 0.0053908 | 0.0013511
11 | 0.98373 | -0.11418 | 0 | 0
12 | 0.98387 | -0.11314 | 0.00604 | 0.0015138
13 | 0.98415 | -0.1112 | 0 | 0
14 | 0.98428 | -0.11023 | 0.0069753 | 0.0017482
15 | 0.98772 | -0.085899 | 0.00044193 | 0.00011076
16 | 0.99484 | -0.036037 | 0.0063867 | 0.0016007
17 | 0.99169 | -0.058141 | 0 | 0
18 | 0.98359 | -0.11519 | 0 | 0
19 | 0.9835 | -0.1158 | 0.0053849 | 0.0013496
20 | 0.98319 | -0.11802 | 0 | 0
21 | 0.98409 | -0.11158 | 0 | 0
22 | 0.98302 | -0.11926 | 0.0053846 | 0.0013495
23 | 0.98309 | -0.11876 | 0 | 0
24 | 0.98397 | -0.11248 | 0 | 0
25 | 0.98405 | -0.11189 | 0.025821 | 0.0064713
26 | 0.98928 | -0.075169 | 0.0055034 | 0.0013793
27 | 0.98901 | -0.077054 | 0.010315 | 0.0025851
28 | 0.98957 | -0.073094 | 0.012307 | 0.0030845
29 | 0.9889 | -0.077854 | 0.004682 | 0.0011734
30 | 0.99087 | -0.063941 | 0.0043996 | 0.0011026
31 | 0.98944 | -0.074019 | 0.001322 | 0.00033133
32 | 0.98885 | -0.078239 | 0 | 0
33 | 0.9886 | -0.080008 | 0.0047616 | 0.0011934
34 | 0.99303 | -0.048765 | 0.013196 | 0.0033072
35 | 0.98393 | -0.11274 | 0.00064418 | 0.00016145
36 | 0.98394 | -0.11268 | 0.0026732 | 0.00066998
37 | 0.98307 | -0.11887 | 0.0015795 | 0.00039587
38 | 0.99077 | -0.064648 | 0.017284 | 0.0043317
39 | 0.99083 | -0.06428 | 0.0038054 | 0.00095372
40 | 0.9927 | -0.0511 | 0.012562 | 0.0031484
41 | 0.99205 | -0.05567 | 0 | 0
42 | 0.99142 | -0.060089 | 0.0081983 | 0.0020547
43 | 0.99126 | -0.06121 | 0.0044526 | 0.0011159
44 | 0.99109 | -0.062442 | 0.0040478 | 0.0010145
45 | 0.99107 | -0.06256 | 0.0016682 | 0.00041808
46 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.085768 | -0.021563 | 0.086155 | 0.021712 | 0.00038708 | 0.00014839 | 0.12854 | 0.12854 | 0.12854 | 0.99308 | -0.04815 | 0.99771 | -0.015904 | 47.606
1 | 0.062329 | 0.015689 | -0.062141 | -0.015617 | 0.00018766 | 7.1733e-05 | 0.093416 | 0.093416 | 0.093416 | 0.99308 | -0.04815 | 0.99 | -0.069777 | 34.5987
2 | -0.10421 | -0.026237 | 0.10444 | 0.026327 | 0.00023208 | 8.9061e-05 | 0.15547 | 0.15547 | 0.15547 | 0.99771 | -0.015904 | 1 | 0 | 57.581
3 | 0.062141 | 0.015617 | -0.062011 | -0.015567 | 0.00013035 | 4.9828e-05 | 0.093416 | 0.093417 | 0.093417 | 0.99 | -0.069777 | 0.98786 | -0.084878 | 34.5987
4 | 0.13257 | 0.033359 | -0.13231 | -0.033258 | 0.00026304 | 0.0001006 | 0.19731 | 0.19731 | 0.19731 | 1 | 0 | 0.99795 | -0.014247 | 36.5394
5 | 0.060131 | 0.015098 | -0.059966 | -0.015035 | 0.0001647 | 6.2935e-05 | 0.090585 | 0.090585 | 0.090585 | 0.98786 | -0.084878 | 0.98507 | -0.10465 | 33.5502
6 | 0.00188 | 0.00046977 | -0.0018798 | -0.00047014 | 1.7339e-07 | -3.7702e-07 | 0.0028313 | 0.0028315 | 0.0028315 | 0.98786 | -0.084878 | 0.98776 | -0.085548 | 1.0487
7 | 0.11567 | 0.029089 | -0.11533 | -0.028957 | 0.00034513 | 0.00013177 | 0.17251 | 0.17251 | 0.17251 | 0.99795 | -0.014247 | 0.99488 | -0.035719 | 31.9461
8 | 0.037293 | 0.009351 | -0.037259 | -0.0093382 | 3.3832e-05 | 1.2795e-05 | 0.056335 | 0.056336 | 0.056336 | 0.98507 | -0.10465 | 0.98415 | -0.1112 | 20.865
9 | 0.022673 | 0.0056838 | -0.022656 | -0.0056773 | 1.752e-05 | 6.4338e-06 | 0.03425 | 0.03425 | 0.03425 | 0.98507 | -0.10465 | 0.98428 | -0.11023 | 12.6852
10 | 0.00044195 | 0.00010978 | -0.00044193 | -0.00011076 | 2.1301e-08 | -9.7805e-07 | 0.00066542 | 0.00066577 | 0.00066577 | 0.98776 | -0.085548 | 0.98772 | -0.085899 | 0.24658
11 | 0.071801 | 0.01802 | -0.071798 | -0.018019 | 3.1743e-06 | 1.2152e-06 | 0.1074 | 0.1074 | 0.1074 | 0.99488 | -0.035719 | 0.99484 | -0.036037 | 39.7776
12 | 0.043525 | 0.010937 | -0.04339 | -0.010886 | 0.00013538 | 5.1409e-05 | 0.06511 | 0.06511 | 0.06511 | 0.99488 | -0.035719 | 0.99169 | -0.058141 | 24.1147
13 | 0.0053911 | 0.0013511 | -0.0053908 | -0.0013511 | 2.9675e-07 | 2.3429e-08 | 0.0081566 | 0.0081566 | 0.0081566 | 0.98351 | -0.11576 | 0.98345 | -0.11616 | 3.021
14 | -0.0053911 | -0.0013511 | 0.0053923 | 0.0013512 | 1.1793e-06 | 9.3002e-08 | 0.0081566 | 0.0081564 | 0.0081566 | 0.98351 | -0.11576 | 0.98373 | -0.11418 | 3.0209
15 | -0.0053923 | -0.0013512 | 0.005393 | 0.0013512 | 7.7448e-07 | 6.0982e-08 | 0.0081564 | 0.0081563 | 0.0081564 | 0.98373 | -0.11418 | 0.98387 | -0.11314 | 3.0209
16 | -0.011433 | -0.002865 | 0.011434 | 0.0028653 | 1.0443e-06 | 3.3056e-07 | 0.017291 | 0.017291 | 0.017291 | 0.98387 | -0.11314 | 0.98397 | -0.11248 | 6.4041
17 | 0.025823 | 0.0064722 | -0.025821 | -0.0064713 | 2.48e-06 | 9.2071e-07 | 0.039044 | 0.039044 | 0.039044 | 0.98415 | -0.1112 | 0.98405 | -0.11189 | 14.4609
18 | 0.011436 | 0.002866 | -0.011434 | -0.0028653 | 2.0276e-06 | 6.4178e-07 | 0.017291 | 0.017291 | 0.017291 | 0.98415 | -0.1112 | 0.98397 | -0.11248 | 6.4041
19 | 0.01568 | 0.0039292 | -0.015677 | -0.0039281 | 2.9359e-06 | 1.0228e-06 | 0.023705 | 0.023705 | 0.023705 | 0.98428 | -0.11023 | 0.98409 | -0.11158 | 8.7796
20 | 0.065411 | 0.016418 | -0.065296 | -0.016374 | 0.00011539 | 4.4132e-05 | 0.097847 | 0.097847 | 0.097847 | 0.99484 | -0.036037 | 0.99303 | -0.048765 | 36.2396
21 | 0.04339 | 0.010886 | -0.043355 | -0.010872 | 3.4885e-05 | 1.3247e-05 | 0.06511 | 0.06511 | 0.06511 | 0.99169 | -0.058141 | 0.99087 | -0.063941 | 24.1147
22 | 0.0053853 | 0.0013496 | -0.0053849 | -0.0013496 | 4.5424e-07 | 3.5527e-08 | 0.0081472 | 0.0081472 | 0.0081472 | 0.98359 | -0.11519 | 0.9835 | -0.1158 | 3.0175
23 | 0.006968 | 0.0017454 | -0.0069653 | -0.0017449 | 2.7279e-06 | 5.5005e-07 | 0.010541 | 0.010541 | 0.010541 | 0.98359 | -0.11519 | 0.98319 | -0.11802 | 3.9042
24 | -0.012353 | -0.003095 | 0.01236 | 0.003097 | 6.1602e-06 | 2.0104e-06 | 0.018688 | 0.018688 | 0.018688 | 0.98359 | -0.11519 | 0.98409 | -0.11158 | 6.9216
25 | 0.0053855 | 0.0013496 | -0.0053846 | -0.0013495 | 9.231e-07 | 7.2699e-08 | 0.0081507 | 0.0081508 | 0.0081508 | 0.98319 | -0.11802 | 0.98302 | -0.11926 | 3.0188
26 | 0.0015797 | 0.00039528 | -0.0015796 | -0.00039579 | 1.6177e-07 | -5.1295e-07 | 0.0023906 | 0.0023908 | 0.0023908 | 0.98319 | -0.11802 | 0.98309 | -0.11876 | 0.88549
27 | 0.0033179 | 0.0008311 | -0.0033174 | -0.00083132 | 5.0348e-07 | -2.1359e-07 | 0.0050168 | 0.0050169 | 0.0050169 | 0.98409 | -0.11158 | 0.98394 | -0.11268 | 1.8581
28 | 0.0015796 | 0.00039579 | -0.0015795 | -0.00039587 | 2.403e-08 | -7.6179e-08 | 0.0023908 | 0.0023908 | 0.0023908 | 0.98309 | -0.11876 | 0.98307 | -0.11887 | 0.8855
29 | 0.019766 | 0.004954 | -0.019761 | -0.0049522 | 5.1557e-06 | 1.863e-06 | 0.029731 | 0.029731 | 0.029731 | 0.98928 | -0.075169 | 0.98901 | -0.077054 | 11.0114
30 | -0.025269 | -0.0063333 | 0.025276 | 0.006336 | 7.2614e-06 | 2.6894e-06 | 0.038009 | 0.038009 | 0.038009 | 0.98928 | -0.075169 | 0.98957 | -0.073094 | 14.0773
31 | 0.0094461 | 0.0023671 | -0.009445 | -0.0023668 | 1.0466e-06 | 2.9599e-07 | 0.014212 | 0.014212 | 0.014212 | 0.98901 | -0.077054 | 0.9889 | -0.077854 | 5.2637
32 | -0.038906 | -0.009751 | 0.038955 | 0.0097697 | 4.9365e-05 | 1.8689e-05 | 0.058503 | 0.058503 | 0.058503 | 0.98957 | -0.073094 | 0.99087 | -0.063941 | 21.6677
33 | 0.0013222 | 0.00033052 | -0.001322 | -0.00033133 | 1.6884e-07 | -8.1448e-07 | 0.0019879 | 0.0019882 | 0.0019882 | 0.98957 | -0.073094 | 0.98944 | -0.074019 | 0.73637
34 | 0.0047631 | 0.0011934 | -0.0047628 | -0.0011934 | 2.535e-07 | -3.9647e-09 | 0.0071669 | 0.007167 | 0.007167 | 0.9889 | -0.077854 | 0.98885 | -0.078239 | 2.6544
35 | 0.0047628 | 0.0011934 | -0.0047616 | -0.0011934 | 1.1659e-06 | -1.8078e-08 | 0.007167 | 0.0071671 | 0.0071671 | 0.98885 | -0.078239 | 0.9886 | -0.080008 | 2.6545
36 | 0.0521 | 0.013067 | -0.052083 | -0.01306 | 1.6856e-05 | 6.4258e-06 | 0.078073 | 0.078073 | 0.078073 | 0.99303 | -0.048765 | 0.9927 | -0.0511 | 28.916
37 | -0.00064418 | -0.00016145 | 0.00064419 | 0.00016134 | 5.0702e-09 | -1.0679e-07 | 0.00097421 | 0.00097417 | 0.00097421 | 0.98393 | -0.11274 | 0.98394 | -0.11268 | 0.36082
38 | -0.017284 | -0.0043317 | 0.017284 | 0.004332 | 8.7958e-07 | 3.1136e-07 | 0.025958 | 0.025958 | 0.025958 | 0.99077 | -0.064648 | 0.99083 | -0.06428 | 9.614
39 | -0.02109 | -0.0052857 | 0.021115 | 0.0052949 | 2.5167e-05 | 9.161e-06 | 0.031673 | 0.031672 | 0.031673 | 0.99083 | -0.06428 | 0.99205 | -0.05567 | 11.7306
40 | 0.039521 | 0.009912 | -0.039496 | -0.0099026 | 2.5028e-05 | 9.4786e-06 | 0.059243 | 0.059243 | 0.059243 | 0.9927 | -0.0511 | 0.99205 | -0.05567 | 21.9418
41 | 0.018381 | 0.0046077 | -0.01837 | -0.0046037 | 1.1241e-05 | 4.0177e-06 | 0.027571 | 0.027571 | 0.027571 | 0.99205 | -0.05567 | 0.99142 | -0.060089 | 10.2113
42 | 0.010171 | 0.002549 | -0.01017 | -0.0025485 | 1.579e-06 | 4.6732e-07 | 0.015266 | 0.015266 | 0.015266 | 0.99142 | -0.060089 | 0.99126 | -0.06121 | 5.654
43 | 0.005717 | 0.0014326 | -0.005716 | -0.0014325 | 9.7482e-07 | 1.0154e-07 | 0.0085819 | 0.008582 | 0.008582 | 0.99126 | -0.06121 | 0.99109 | -0.062442 | 3.1785
44 | 0.0016682 | 0.00041801 | -0.0016682 | -0.00041808 | 2.719e-08 | -7.905e-08 | 0.0025046 | 0.0025046 | 0.0025046 | 0.99109 | -0.062442 | 0.99107 | -0.06256 | 0.92764

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23781 | 0.059685

## res_load
| p_mw | q_mvar
0 | 0.023439 | 0.0058743
1 | 0.018058 | 0.0045258
2 | 0.016635 | 0.0041692
3 | 0.0014379 | 0.00036036
4 | 0.0053908 | 0.0013511
5 | 0.00604 | 0.0015138
6 | 0.0069753 | 0.0017482
7 | 0.00044193 | 0.00011076
8 | 0.0063867 | 0.0016007
9 | 0.0053849 | 0.0013496
10 | 0.0053846 | 0.0013495
11 | 0.025821 | 0.0064713
12 | 0.0055034 | 0.0013793
13 | 0.010315 | 0.0025851
14 | 0.012307 | 0.0030845
15 | 0.004682 | 0.0011734
16 | 0.0043996 | 0.0011026
17 | 0.001322 | 0.00033133
18 | 0.0047616 | 0.0011934
19 | 0.013196 | 0.0033072
20 | 0.00064418 | 0.00016145
21 | 0.0026732 | 0.00066998
22 | 0.0015795 | 0.00039587
23 | 0.017284 | 0.0043317
24 | 0.0038054 | 0.00095372
25 | 0.012562 | 0.0031484
26 | 0.0081983 | 0.0020547
27 | 0.0044526 | 0.0011159
28 | 0.0040478 | 0.0010145
29 | 0.0016682 | 0.00041808

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1