## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1098-5_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1098-5_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1098-5_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1098-5_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1098-5_0_2_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_1098-5_0_2_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1098-5_0_2_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1098-5_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1098-5_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1098-5_0_2_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_1098-5_0_2_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1098-5_0_2_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1098-5_0_2_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_1098-5_0_2_node_50 | 0.4 | n |  | TRUE
14 | bus_LV_1098-5_0_2_node_24 | 0.4 | n |  | TRUE
15 | bus_LV_1098-5_0_2_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_1098-5_0_2_node_27 | 0.4 | n |  | TRUE
17 | bus_LV_1098-5_0_2_node_31 | 0.4 | n |  | TRUE
18 | bus_LV_1098-5_0_2_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1098-5_0_2_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1098-5_0_2_node_30 | 0.4 | n |  | TRUE
21 | bus_LV_1098-5_0_2_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_1098-5_0_2_node_59 | 0.4 | n |  | TRUE
23 | bus_LV_1098-5_0_2_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_1098-5_0_2_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_1098-5_0_2_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_1098-5_0_2_node_34 | 0.4 | n |  | TRUE
27 | bus_LV_1098-5_0_2_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_1098-5_0_2_node_39 | 0.4 | n |  | TRUE
29 | bus_LV_1098-5_0_2_node_40 | 0.4 | n |  | TRUE
30 | bus_LV_1098-5_0_2_node_41 | 0.4 | n |  | TRUE
31 | bus_LV_1098-5_0_2_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_1098-5_0_2_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_1098-5_0_2_node_62 | 0.4 | n |  | TRUE
34 | bus_LV_1098-5_0_2_node_85 | 0.4 | n |  | TRUE
35 | bus_LV_1098-5_0_2_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_1098-5_0_2_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_1098-5_0_2_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_1098-5_0_2_node_47 | 0.4 | n |  | TRUE
39 | bus_LV_1098-5_0_2_node_48 | 0.4 | n |  | TRUE
40 | bus_LV_1098-5_0_2_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_1098-5_0_2_node_51 | 0.4 | n |  | TRUE
42 | bus_LV_1098-5_0_2_node_240 | 0.4 | n |  | TRUE
43 | bus_LV_1098-5_0_2_node_52 | 0.4 | n |  | TRUE
44 | bus_LV_1098-5_0_2_node_53 | 0.4 | n |  | TRUE
45 | bus_LV_1098-5_0_2_node_54 | 0.4 | n |  | TRUE
46 | bus_LV_1098-5_0_2_node_55 | 0.4 | n |  | TRUE
47 | bus_LV_1098-5_0_2_node_56 | 0.4 | n |  | TRUE
48 | bus_LV_1098-5_0_2_node_57 | 0.4 | n |  | TRUE
49 | bus_LV_1098-5_0_2_node_58 | 0.4 | n |  | TRUE
50 | bus_LV_1098-5_0_2_node_60 | 0.4 | n |  | TRUE
51 | bus_LV_1098-5_0_2_node_61 | 0.4 | n |  | TRUE
52 | bus_LV_1098-5_0_2_node_63 | 0.4 | n |  | TRUE
53 | bus_LV_1098-5_0_2_node_64 | 0.4 | n |  | TRUE
54 | bus_LV_1098-5_0_2_node_65 | 0.4 | n |  | TRUE
55 | bus_LV_1098-5_0_2_node_66 | 0.4 | n |  | TRUE
56 | bus_LV_1098-5_0_2_node_67 | 0.4 | n |  | TRUE
57 | bus_LV_1098-5_0_2_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_1098-5_0_2_node_69 | 0.4 | n |  | TRUE
59 | bus_LV_1098-5_0_2_node_70 | 0.4 | n |  | TRUE
60 | bus_LV_1098-5_0_2_node_71 | 0.4 | n |  | TRUE
61 | bus_LV_1098-5_0_2_node_72 | 0.4 | n |  | TRUE
62 | bus_LV_1098-5_0_2_node_73 | 0.4 | n |  | TRUE
63 | bus_LV_1098-5_0_2_node_74 | 0.4 | n |  | TRUE
64 | bus_LV_1098-5_0_2_node_84 | 0.4 | n |  | TRUE
65 | bus_LV_1098-5_0_2_node_81 | 0.4 | n |  | TRUE
66 | bus_LV_1098-5_0_2_node_76 | 0.4 | n |  | TRUE
67 | bus_LV_1098-5_0_2_node_77 | 0.4 | n |  | TRUE
68 | bus_LV_1098-5_0_2_node_78 | 0.4 | n |  | TRUE
69 | bus_LV_1098-5_0_2_node_79 | 0.4 | n |  | TRUE
70 | bus_LV_1098-5_0_2_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_1098-5_0_2_node_82 | 0.4 | n |  | TRUE
72 | bus_MV_124_0_node_143 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1098-5_0_2_load_0 | 0 | 0.007367 | 0.0018463 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1098-5_0_2_load_1 | 1 | 0.0037798 | 0.00094731 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1098-5_0_2_load_6 | 5 | 0.00073077 | 0.00018315 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1098-5_0_2_load_4 | 6 | 0.0010389 | 0.00026038 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1098-5_0_2_load_5 | 7 | 0.0010682 | 0.00026772 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1098-5_0_2_load_7 | 8 | 0.0022783 | 0.00057099 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1098-5_0_2_load_23 | 10 | 0.0011728 | 0.00029392 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1098-5_0_2_load_15 | 11 | 0.00045615 | 0.00011432 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1098-5_0_2_load_16 | 12 | 0.0016036 | 0.0004019 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1098-5_0_2_load_24 | 14 | 0.00202 | 0.00050626 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1098-5_0_2_load_25 | 15 | 0.0028778 | 0.00072125 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1098-5_0_2_load_31 | 17 | 0.00025474 | 6.3843e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1098-5_0_2_load_28 | 18 | 0.0026247 | 0.00065781 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1098-5_0_2_load_29 | 19 | 0.0018489 | 0.00046337 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1098-5_0_2_load_30 | 20 | 0.0031543 | 0.00079055 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1098-5_0_2_load_33 | 21 | 0.0019074 | 0.00047805 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1098-5_0_2_load_36 | 24 | 0.0035613 | 0.00089256 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1098-5_0_2_load_34 | 26 | 0.0031632 | 0.00079278 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1098-5_0_2_load_37 | 27 | 0.0025486 | 0.00063873 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1098-5_0_2_load_40 | 29 | 0.0029182 | 0.00073137 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1098-5_0_2_load_42 | 31 | 0.00026805 | 6.718e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1098-5_0_2_load_43 | 32 | 0.0034521 | 0.00086517 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1098-5_0_2_load_85 | 34 | 0.00078115 | 0.00019577 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1098-5_0_2_load_44 | 35 | 0.0013193 | 0.00033066 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1098-5_0_2_load_45 | 36 | 0.00093244 | 0.00023369 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1098-5_0_2_load_46 | 37 | 0.0024395 | 0.00061139 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1098-5_0_2_load_47 | 38 | 0.00080797 | 0.0002025 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1098-5_0_2_load_49 | 40 | 0.00082651 | 0.00020714 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1098-5_0_2_load_51 | 41 | 0.0010428 | 0.00026136 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1098-5_0_2_load_240 | 42 | 0.00061217 | 0.00015343 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1098-5_0_2_load_52 | 43 | 0.00049462 | 0.00012396 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1098-5_0_2_load_53 | 44 | 0.0017753 | 0.00044492 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1098-5_0_2_load_54 | 45 | 0.0011517 | 0.00028865 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1098-5_0_2_load_55 | 46 | 0.0057906 | 0.0014513 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1098-5_0_2_load_56 | 47 | 0.00052222 | 0.00013088 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1098-5_0_2_load_57 | 48 | 0.0014306 | 0.00035855 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1098-5_0_2_load_58 | 49 | 0.001496 | 0.00037494 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1098-5_0_2_load_60 | 50 | 0.0014883 | 0.000373 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1098-5_0_2_load_61 | 51 | 0.00064347 | 0.00016127 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1098-5_0_2_load_64 | 53 | 0.00040551 | 0.00010163 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1098-5_0_2_load_65 | 54 | 0.00078955 | 0.00019788 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1098-5_0_2_load_66 | 55 | 0.00023256 | 5.8285e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1098-5_0_2_load_67 | 56 | 0.00024193 | 6.0633e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1098-5_0_2_load_68 | 57 | 0.00079652 | 0.00019963 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1098-5_0_2_load_71 | 60 | 0.00079137 | 0.00019834 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1098-5_0_2_load_72 | 61 | 0.00048203 | 0.00012081 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1098-5_0_2_load_73 | 62 | 0.00030633 | 7.6772e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1098-5_0_2_load_84 | 64 | 0.00042617 | 0.00010681 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1098-5_0_2_load_81 | 65 | 0.00029234 | 7.3268e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1098-5_0_2_load_76 | 66 | 0.00093177 | 0.00023352 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1098-5_0_2_load_77 | 67 | 0.00049579 | 0.00012426 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1098-5_0_2_load_79 | 69 | 0.0031099 | 0.00077942 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1098-5_0_2_load_82 | 71 | 0.00015817 | 3.9641e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 23 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1098-5_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.027838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1098-5_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.012951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1098-5_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.003389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1098-5_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.023794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1098-5_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.056957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1098-5_0_2_line_5 | NAYY 4x150 SE | 4 | 10 | 0.026329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1098-5_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.0068839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1098-5_0_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.012532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1098-5_0_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.038568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1098-5_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.086576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1098-5_0_2_line_10 | NAYY 4x150 SE | 9 | 24 | 0.11808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1098-5_0_2_line_11 | NAYY 4x150 SE | 10 | 14 | 0.0178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1098-5_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.044073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1098-5_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.21848 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1098-5_0_2_line_14 | NAYY 4x150 SE | 13 | 42 | 0.27417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1098-5_0_2_line_15 | NAYY 4x150 SE | 13 | 39 | 0.30203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1098-5_0_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.028667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1098-5_0_2_line_17 | NAYY 4x150 SE | 16 | 17 | 0.12645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1098-5_0_2_line_18 | NAYY 4x150 SE | 16 | 18 | 0.064534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1098-5_0_2_line_19 | NAYY 4x150 SE | 17 | 22 | 0.017204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1098-5_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.029305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1098-5_0_2_line_21 | NAYY 4x150 SE | 19 | 20 | 0.018594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1098-5_0_2_line_22 | NAYY 4x150 SE | 20 | 21 | 0.021388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1098-5_0_2_line_23 | NAYY 4x150 SE | 21 | 26 | 0.01455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1098-5_0_2_line_24 | NAYY 4x150 SE | 22 | 31 | 0.021612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1098-5_0_2_line_25 | NAYY 4x150 SE | 22 | 49 | 0.075178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1098-5_0_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.036896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1098-5_0_2_line_27 | NAYY 4x150 SE | 23 | 25 | 0.00352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1098-5_0_2_line_28 | NAYY 4x150 SE | 25 | 29 | 0.019794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1098-5_0_2_line_29 | NAYY 4x150 SE | 25 | 27 | 0.045928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1098-5_0_2_line_30 | NAYY 4x150 SE | 27 | 28 | 0.13048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1098-5_0_2_line_31 | NAYY 4x150 SE | 28 | 30 | 0.010513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1098-5_0_2_line_32 | NAYY 4x150 SE | 28 | 31 | 0.011543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1098-5_0_2_line_33 | NAYY 4x150 SE | 29 | 32 | 0.046311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1098-5_0_2_line_34 | NAYY 4x150 SE | 30 | 33 | 0.15866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1098-5_0_2_line_35 | NAYY 4x150 SE | 30 | 34 | 0.078817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1098-5_0_2_line_36 | NAYY 4x150 SE | 32 | 35 | 0.021291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1098-5_0_2_line_37 | NAYY 4x150 SE | 33 | 52 | 0.018459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1098-5_0_2_line_38 | NAYY 4x150 SE | 33 | 50 | 0.060514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1098-5_0_2_line_39 | NAYY 4x150 SE | 34 | 64 | 0.23333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1098-5_0_2_line_40 | NAYY 4x150 SE | 35 | 36 | 0.018968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1098-5_0_2_line_41 | NAYY 4x150 SE | 36 | 37 | 0.0046141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1098-5_0_2_line_42 | NAYY 4x150 SE | 37 | 38 | 0.024089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1098-5_0_2_line_43 | NAYY 4x150 SE | 38 | 39 | 0.058312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1098-5_0_2_line_44 | NAYY 4x150 SE | 39 | 40 | 0.038744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1098-5_0_2_line_45 | NAYY 4x150 SE | 40 | 41 | 0.016666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1098-5_0_2_line_46 | NAYY 4x150 SE | 41 | 43 | 0.09379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1098-5_0_2_line_47 | NAYY 4x150 SE | 43 | 44 | 0.016842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1098-5_0_2_line_48 | NAYY 4x150 SE | 45 | 46 | 0.022592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1098-5_0_2_line_49 | NAYY 4x150 SE | 46 | 47 | 0.026529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1098-5_0_2_line_50 | NAYY 4x150 SE | 47 | 48 | 0.014506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1098-5_0_2_line_51 | NAYY 4x150 SE | 48 | 49 | 0.0026863 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1098-5_0_2_line_52 | NAYY 4x150 SE | 50 | 51 | 0.03561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1098-5_0_2_line_53 | NAYY 4x150 SE | 52 | 53 | 0.059154 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1098-5_0_2_line_54 | NAYY 4x150 SE | 53 | 54 | 0.069495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1098-5_0_2_line_55 | NAYY 4x150 SE | 54 | 55 | 0.038713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1098-5_0_2_line_56 | NAYY 4x150 SE | 56 | 57 | 0.039286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1098-5_0_2_line_57 | NAYY 4x150 SE | 56 | 58 | 0.32608 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1098-5_0_2_line_58 | NAYY 4x150 SE | 57 | 59 | 0.0039842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1098-5_0_2_line_59 | NAYY 4x150 SE | 58 | 60 | 0.023554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1098-5_0_2_line_60 | NAYY 4x150 SE | 58 | 61 | 0.02157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1098-5_0_2_line_61 | NAYY 4x150 SE | 59 | 62 | 0.0077676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1098-5_0_2_line_62 | NAYY 4x150 SE | 59 | 63 | 0.30291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1098-5_0_2_line_63 | NAYY 4x150 SE | 61 | 64 | 0.062537 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1098-5_0_2_line_64 | NAYY 4x150 SE | 63 | 65 | 0.16676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1098-5_0_2_line_65 | NAYY 4x150 SE | 65 | 70 | 0.0068505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1098-5_0_2_line_66 | NAYY 4x150 SE | 66 | 67 | 0.019559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1098-5_0_2_line_67 | NAYY 4x150 SE | 67 | 68 | 0.03822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1098-5_0_2_line_68 | NAYY 4x150 SE | 68 | 69 | 0.0083569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1098-5_0_2_line_69 | NAYY 4x150 SE | 69 | 70 | 0.025525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1098-5_0_2_line_70 | NAYY 4x150 SE | 70 | 71 | 0.0094384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1098-5_0_2_trafo_32 | 0.25 MVA 20/0.4 kV | 72 | 23 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2650337.4287 | 1212051.6102 | 2650336.3428 | 1212047.9433 | 2650333.3745 | 1212043.1488 | 2650326.1518 | 1212035.6167 | 2650320.2765 | 1212030.2776
1 | 2650311.0396 | 1212021.2253 | 2650313.9144 | 1212024.4959 | 2650320.2765 | 1212030.2776
2 | 2650311.6679 | 1212017.8953 | 2650311.0396 | 1212021.2253
3 | 2650311.6679 | 1212017.8953 | 2650305.6297 | 1212016.7548 | 2650299.8935 | 1212016.7398 | 2650294.4783 | 1212015.5935 | 2650288.5815 | 1212012.9978
4 | 2650311.6679 | 1212017.8953 | 2650337.2608 | 1212028.295 | 2650346.9716 | 1212030.0001 | 2650361.9014 | 1212028.1805 | 2650366.3199 | 1212027.8289
5 | 2650288.5815 | 1212012.9978 | 2650283.3176 | 1212016.4333 | 2650270.3351 | 1212018.8809 | 2650264.5212 | 1212019.977 | 2650263.623 | 1212020.1529
6 | 2650373.1821 | 1212027.2827 | 2650366.3199 | 1212027.8289
7 | 2650373.1821 | 1212027.2827 | 2650378.4453 | 1212026.8638 | 2650385.5682 | 1212028.2248
8 | 2650385.5682 | 1212028.2248 | 2650385.5682 | 1212028.2248 | 2650388.4487 | 1212032.6072 | 2650387.7216 | 1212041.3285 | 2650384.1938 | 1212056.0074 | 2650384.6323 | 1212061.6589 | 2650387.6424 | 1212063.99
9 | 2650462.1497 | 1212029.6281 | 2650456.242 | 1212027.4324 | 2650451.5809 | 1212027.8599 | 2650437.0074 | 1212036.0527 | 2650424.3241 | 1212045.3511 | 2650410.2835 | 1212057.0283 | 2650400.0169 | 1212063.5677 | 2650392.5503 | 1212065.1278 | 2650388.014 | 1212064.2779 | 2650387.6424 | 1212063.99
10 | 2650462.1497 | 1212029.6281 | 2650449.0349 | 1212053.9984 | 2650446.1278 | 1212060.8556 | 2650443.3159 | 1212072.6166 | 2650439.2755 | 1212118.254 | 2650438.7709 | 1212129.4119 | 2650436.6042 | 1212143.1177
11 | 2650263.623 | 1212020.1529 | 2650246.1549 | 1212023.5722
12 | 2651078.1318 | 1211998.8384 | 2651078.7156 | 1212004.3133 | 2651079.6515 | 1212013.0265 | 2651082.4737 | 1212023.2679 | 2651083.0191 | 1212025.2404 | 2651089.1056 | 1212041.2569
13 | 2650862.933 | 1211961.1116 | 2651078.1318 | 1211998.8384
14 | 2650862.933 | 1211961.1116 | 2650860.1365 | 1211966.5132 | 2650828.06 | 1212005.5298 | 2650778.9734 | 1212053.3737 | 2650767.9922 | 1212068.8339 | 2650748.3646 | 1212106.6449 | 2650736.7149 | 1212138.1979 | 2650733.8446 | 1212164.8004 | 2650735.3157 | 1212178.5322 | 2650737.147 | 1212181.1827 | 2650741.8991 | 1212182.5461 | 2650747.1912 | 1212182.0575
15 | 2650588.8098 | 1212077.4398 | 2650600.3571 | 1212069.533 | 2650716.7926 | 1211997.145 | 2650724.1225 | 1211993.8164 | 2650731.9257 | 1211991.1033 | 2650804.222 | 1211978.2996 | 2650829.1746 | 1211971.9193 | 2650862.933 | 1211961.1116
16 | 2650246.1549 | 1212023.5722 | 2650231.5227 | 1212026.4364 | 2650217.8118 | 1212027.561
17 | 2650334.9214 | 1212149.7583 | 2650333.1023 | 1212152.8448 | 2650337.0981 | 1212159.2156 | 2650340.2958 | 1212171.9279 | 2650345.6276 | 1212183.8355 | 2650351.815 | 1212199.686 | 2650353.8384 | 1212227.2972 | 2650356.3905 | 1212233.6669 | 2650363.38 | 1212244.499 | 2650365.2624 | 1212250.1071 | 2650364.7916 | 1212258.1746 | 2650362.4192 | 1212268.6531
18 | 2650334.9214 | 1212149.7583 | 2650321.1492 | 1212135.9785 | 2650306.2875 | 1212124.3463 | 2650305.3364 | 1212123.6045 | 2650300.1963 | 1212119.581 | 2650283.9365 | 1212110.8711
19 | 2650358.552 | 1212285.4158 | 2650359.149 | 1212283.0973 | 2650362.4192 | 1212268.6531
20 | 2650283.9365 | 1212110.8711 | 2650278.5193 | 1212107.9693 | 2650261.1678 | 1212101.4526 | 2650256.837 | 1212099.83
21 | 2650256.837 | 1212099.83 | 2650253.6092 | 1212098.6206 | 2650238.7623 | 1212095.618
22 | 2650238.7623 | 1212095.618 | 2650231.181 | 1212094.0847 | 2650217.5354 | 1212093.6415
23 | 2650202.9936 | 1212093.1692 | 2650217.5354 | 1212093.6415
24 | 2650358.552 | 1212285.4158 | 2650361.9886 | 1212288.7135 | 2650373.3249 | 1212301.1787
25 | 2650358.552 | 1212285.4158 | 2650351.9916 | 1212284.0708 | 2650293.231 | 1212291.4798 | 2650283.9826 | 1212291.8303
26 | 2650433.5507 | 1212179.7976 | 2650433.8985 | 1212160.2334 | 2650436.6042 | 1212143.1177
27 | 2650433.5507 | 1212179.7976 | 2650437.0412 | 1212180.3274
28 | 2650437.0412 | 1212180.3274 | 2650440.259 | 1212171.7607 | 2650446.3895 | 1212163.0614
29 | 2650437.0412 | 1212180.3274 | 2650441.7287 | 1212183.0464 | 2650443.5463 | 1212187.331 | 2650444.1514 | 1212192.139 | 2650442.349 | 1212223.0959
30 | 2650379.6717 | 1212310.7535 | 2650392.7151 | 1212306.4278 | 2650415.141 | 1212303.0374 | 2650421.3256 | 1212302.1002 | 2650425.1227 | 1212300.498 | 2650431.3979 | 1212297.8383 | 2650435.5918 | 1212292.4372 | 2650438.8094 | 1212283.8927 | 2650442.349 | 1212223.0959
31 | 2650370.8031 | 1212316.4376 | 2650379.6717 | 1212310.7535
32 | 2650379.6717 | 1212310.7535 | 2650375.5909 | 1212303.6705 | 2650373.3249 | 1212301.1787
33 | 2650446.3895 | 1212163.0614 | 2650463.9825 | 1212138.0968 | 2650474.6019 | 1212126.4386
34 | 2650370.8031 | 1212316.4376 | 2650363.2304 | 1212323.4001 | 2650355.5276 | 1212332.2848 | 2650349.5503 | 1212342.8628 | 2650344.8319 | 1212358.221 | 2650343.3452 | 1212374.1402 | 2650342.2299 | 1212404.5599 | 2650338.4453 | 1212424.5065 | 2650331.0392 | 1212446.8684 | 2650324.4313 | 1212463.7671
35 | 2650370.8031 | 1212316.4376 | 2650374.8977 | 1212323.6765 | 2650380.4159 | 1212355.7643 | 2650382.4214 | 1212362.9855 | 2650389.9048 | 1212389.9758 | 2650390.9069 | 1212392.199
36 | 2650474.6019 | 1212126.4386 | 2650474.9566 | 1212126.0491 | 2650482.733 | 1212117.5098 | 2650490.6049 | 1212112.7207
37 | 2650324.4313 | 1212463.7671 | 2650318.1961 | 1212479.724 | 2650317.7146 | 1212480.9652
38 | 2650324.4313 | 1212463.7671 | 2650330.4701 | 1212462.9843 | 2650342.7675 | 1212456.9844 | 2650343.1099 | 1212456.9206 | 2650348.8855 | 1212455.8242 | 2650354.3846 | 1212456.8824 | 2650359.1895 | 1212459.1687 | 2650365.9169 | 1212465.9184 | 2650369.2618 | 1212472.8618 | 2650371.7097 | 1212478.7277
39 | 2650512.3178 | 1212590.4045 | 2650510.5457 | 1212588.8025 | 2650476.7813 | 1212546.0692 | 2650440.4133 | 1212489.5282 | 2650422.5928 | 1212456.8693 | 2650403.5073 | 1212420.153 | 2650398.7942 | 1212409.6959 | 2650390.9069 | 1212392.199
40 | 2650506.8091 | 1212102.8623 | 2650490.6049 | 1212112.7207
41 | 2650506.8091 | 1212102.8623 | 2650510.751 | 1212100.4641
42 | 2650532.4653 | 1212090.0941 | 2650514.2739 | 1212098.3209 | 2650510.751 | 1212100.4641
43 | 2650588.8098 | 1212077.4398 | 2650568.9525 | 1212084.2311 | 2650560.9974 | 1212086.9542 | 2650535.8963 | 1212088.5425 | 2650532.4653 | 1212090.0941
44 | 2650588.8098 | 1212077.4398 | 2650591.0352 | 1212088.2762 | 2650588.4052 | 1212105.4418 | 2650584.9502 | 1212110.5823 | 2650582.7515 | 1212114.069
45 | 2650582.7515 | 1212114.069 | 2650575.0618 | 1212126.2633 | 2650574.0348 | 1212128.2113 | 2650574.0273 | 1212128.258
46 | 2650574.0273 | 1212128.258 | 2650572.1094 | 1212140.2355 | 2650570.401 | 1212150.8606 | 2650565.7181 | 1212172.7006 | 2650563.2575 | 1212182.4411 | 2650553.0591 | 1212199.7538 | 2650546.5917 | 1212213.4183 | 2650545.741 | 1212216.6113
47 | 2650541.4048 | 1212232.8859 | 2650545.741 | 1212216.6113
48 | 2650219.2095 | 1212283.1941 | 2650226.9798 | 1212286.2299 | 2650234.6962 | 1212289.2521 | 2650238.0071 | 1212290.3362 | 2650240.4559 | 1212290.7211
49 | 2650240.4559 | 1212290.7211 | 2650254.6008 | 1212292.9441 | 2650266.8029 | 1212292.4816
50 | 2650281.2982 | 1212291.9321 | 2650266.8029 | 1212292.4816
51 | 2650281.2982 | 1212291.9321 | 2650283.9826 | 1212291.8303
52 | 2650371.7097 | 1212478.7277 | 2650384.9665 | 1212510.4945 | 2650385.3612 | 1212511.615
53 | 2650317.7146 | 1212480.9652 | 2650312.1085 | 1212495.3042 | 2650300.4165 | 1212520.5206 | 2650299.3176 | 1212522.9016 | 2650292.9345 | 1212534.6163
54 | 2650292.9345 | 1212534.6163 | 2650284.3629 | 1212550.3474 | 2650260.1669 | 1212595.9006
55 | 2650260.1669 | 1212595.9006 | 2650254.8741 | 1212605.8653 | 2650242.6748 | 1212626.4193 | 2650241.3217 | 1212629.6779
56 | 2650848.4383 | 1212814.2679 | 2650859.2941 | 1212818.1895 | 2650878.1123 | 1212824.3202 | 2650886.0549 | 1212824.7139
57 | 2650577.8903 | 1212642.9828 | 2650615.8488 | 1212676.5579 | 2650658.0153 | 1212702.998 | 2650691.222 | 1212723.5033 | 2650705.12 | 1212735.6397 | 2650735.2591 | 1212769.3158 | 2650746.4046 | 1212779.0275 | 2650760.3079 | 1212786.0499 | 2650782.304 | 1212791.9072 | 2650803.788 | 1212798.1382 | 2650848.4383 | 1212814.2679
58 | 2650890.0342 | 1212824.9111 | 2650886.0549 | 1212824.7139
59 | 2650577.8903 | 1212642.9828 | 2650586.7745 | 1212638.1107 | 2650592.9189 | 1212635.6169 | 2650599.447 | 1212634.4604 | 2650599.606 | 1212634.4851
60 | 2650577.8903 | 1212642.9828 | 2650560.7514 | 1212629.8854
61 | 2650890.0342 | 1212824.9111 | 2650895.8155 | 1212830.0989
62 | 2650890.0342 | 1212824.9111 | 2650903.2856 | 1212821.9335 | 2650912.8961 | 1212816.5345 | 2650940.9486 | 1212792.8042 | 2650951.631 | 1212778.4313 | 2650958.102 | 1212769.7147 | 2650964.0713 | 1212759.2706 | 2650966.6137 | 1212751.5655 | 2650968.2552 | 1212742.6075 | 2650969.0552 | 1212716.5544 | 2650970.502 | 1212691.274 | 2650971.0265 | 1212675.2356 | 2650967.9635 | 1212629.1709 | 2650966.1973 | 1212618.0381 | 2650951.2067 | 1212561.3097
63 | 2650560.7514 | 1212629.8854 | 2650529.9746 | 1212606.3663 | 2650512.3178 | 1212590.4045
64 | 2650951.2067 | 1212561.3097 | 2650949.7495 | 1212555.8051 | 2650936.553 | 1212512.2444 | 2650927.3743 | 1212488.3741 | 2650927.9144 | 1212482.9533 | 2650930.5801 | 1212478.6179 | 2650936.6756 | 1212476.5353 | 2650943.0499 | 1212477.4014 | 2650988.0724 | 1212503.9127 | 2650995.1288 | 1212506.7525 | 2651001.836 | 1212506.8765
65 | 2651008.03 | 1212503.9499 | 2651001.836 | 1212506.8765
66 | 2650962.6855 | 1212436.2229 | 2650972.0314 | 1212450.077 | 2650974.1678 | 1212451.9587
67 | 2651006.5047 | 1212470.8728 | 2650999.2667 | 1212464.396 | 2650995.0141 | 1212461.5135 | 2650979.5643 | 1212456.712 | 2650974.1678 | 1212451.9587
68 | 2651006.5047 | 1212470.8728 | 2651007.9079 | 1212479.111
69 | 2651008.03 | 1212503.9499 | 2651010.1974 | 1212499.2434 | 2651010.3677 | 1212493.5526 | 2651007.9079 | 1212479.111
70 | 2651008.03 | 1212503.9499 | 2651016.3113 | 1212508.4779

## bus_geodata
| x | y | coords
0 | 2650320.2765 | 1212030.2776
1 | 2650337.4287 | 1212051.6102
2 | 2650311.0396 | 1212021.2253
3 | 2650311.6679 | 1212017.8953
4 | 2650288.5815 | 1212012.9978
5 | 2650366.3199 | 1212027.8289
6 | 2650373.1821 | 1212027.2827
7 | 2650385.5682 | 1212028.2248
8 | 2650387.6424 | 1212063.99
9 | 2650462.1497 | 1212029.6281
10 | 2650263.623 | 1212020.1529
11 | 2651078.1318 | 1211998.8384
12 | 2651089.1056 | 1212041.2569
13 | 2650862.933 | 1211961.1116
14 | 2650246.1549 | 1212023.5722
15 | 2650217.8118 | 1212027.561
16 | 2650334.9214 | 1212149.7583
17 | 2650362.4192 | 1212268.6531
18 | 2650283.9365 | 1212110.8711
19 | 2650256.837 | 1212099.83
20 | 2650238.7623 | 1212095.618
21 | 2650217.5354 | 1212093.6415
22 | 2650358.552 | 1212285.4158
23 | 2650433.5507 | 1212179.7976
24 | 2650436.6042 | 1212143.1177
25 | 2650437.0412 | 1212180.3274
26 | 2650202.9936 | 1212093.1692
27 | 2650442.349 | 1212223.0959
28 | 2650379.6717 | 1212310.7535
29 | 2650446.3895 | 1212163.0614
30 | 2650370.8031 | 1212316.4376
31 | 2650373.3249 | 1212301.1787
32 | 2650474.6019 | 1212126.4386
33 | 2650324.4313 | 1212463.7671
34 | 2650390.9069 | 1212392.199
35 | 2650490.6049 | 1212112.7207
36 | 2650506.8091 | 1212102.8623
37 | 2650510.751 | 1212100.4641
38 | 2650532.4653 | 1212090.0941
39 | 2650588.8098 | 1212077.4398
40 | 2650582.7515 | 1212114.069
41 | 2650574.0273 | 1212128.258
42 | 2650747.1912 | 1212182.0575
43 | 2650545.741 | 1212216.6113
44 | 2650541.4048 | 1212232.8859
45 | 2650219.2095 | 1212283.1941
46 | 2650240.4559 | 1212290.7211
47 | 2650266.8029 | 1212292.4816
48 | 2650281.2982 | 1212291.9321
49 | 2650283.9826 | 1212291.8303
50 | 2650371.7097 | 1212478.7277
51 | 2650385.3612 | 1212511.615
52 | 2650317.7146 | 1212480.9652
53 | 2650292.9345 | 1212534.6163
54 | 2650260.1669 | 1212595.9006
55 | 2650241.3217 | 1212629.6779
56 | 2650848.4383 | 1212814.2679
57 | 2650886.0549 | 1212824.7139
58 | 2650577.8903 | 1212642.9828
59 | 2650890.0342 | 1212824.9111
60 | 2650599.606 | 1212634.4851
61 | 2650560.7514 | 1212629.8854
62 | 2650895.8155 | 1212830.0989
63 | 2650951.2067 | 1212561.3097
64 | 2650512.3178 | 1212590.4045
65 | 2651001.836 | 1212506.8765
66 | 2650962.6855 | 1212436.2229
67 | 2650974.1678 | 1212451.9587
68 | 2651006.5047 | 1212470.8728
69 | 2651007.9079 | 1212479.111
70 | 2651008.03 | 1212503.9499
71 | 2651016.3113 | 1212508.4779
72 | 2650437.0412 | 1212180.3274

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98873 | -0.079085 | 0.007367 | 0.0018463
1 | 0.98858 | -0.08016 | 0.0037798 | 0.00094731
2 | 0.98893 | -0.077611 | 0 | 0
3 | 0.98899 | -0.077225 | 0 | 0
4 | 0.98878 | -0.078701 | 0 | 0
5 | 0.9904 | -0.067224 | 0.00073077 | 0.00018315
6 | 0.99058 | -0.065965 | 0.0010389 | 0.00026038
7 | 0.99092 | -0.063544 | 0.0010682 | 0.00026772
8 | 0.99204 | -0.055682 | 0.0022783 | 0.00057099
9 | 0.99483 | -0.036103 | 0 | 0
10 | 0.98855 | -0.080335 | 0.0011728 | 0.00029392
11 | 0.99477 | -0.037133 | 0.00045615 | 0.00011432
12 | 0.99467 | -0.037847 | 0.0016036 | 0.0004019
13 | 0.99541 | -0.032565 | 0 | 0
14 | 0.98842 | -0.081226 | 0.00202 | 0.00050626
15 | 0.98831 | -0.082069 | 0.0028778 | 0.00072125
16 | 0.98659 | -0.094259 | 0 | 0
17 | 0.98892 | -0.077807 | 0.00025474 | 6.3843e-05
18 | 0.98541 | -0.10268 | 0.0026247 | 0.00065781
19 | 0.98498 | -0.10572 | 0.0018489 | 0.00046337
20 | 0.98476 | -0.10729 | 0.0031543 | 0.00079055
21 | 0.9846 | -0.10841 | 0.0019074 | 0.00047805
22 | 0.98924 | -0.075529 | 0 | 0
23 | 1 | 0 | -0.084728 | -0.021091
24 | 0.99863 | -0.0095654 | 0.0035613 | 0.00089256
25 | 0.99971 | -0.0020229 | 0 | 0
26 | 0.98453 | -0.10888 | 0.0031632 | 0.00079278
27 | 0.99715 | -0.019849 | 0.0025486 | 0.00063873
28 | 0.99036 | -0.067598 | 0 | 0
29 | 0.99918 | -0.0057401 | 0.0029182 | 0.00073137
30 | 0.99017 | -0.06894 | 0 | 0
31 | 0.98997 | -0.070378 | 0.00026805 | 6.718e-05
32 | 0.99814 | -0.013097 | 0.0034521 | 0.00086517
33 | 0.98936 | -0.07475 | 0 | 0
34 | 0.98916 | -0.07612 | 0.00078115 | 0.00019577
35 | 0.99776 | -0.015747 | 0.0013193 | 0.00033066
36 | 0.99747 | -0.017858 | 0.00093244 | 0.00023369
37 | 0.9974 | -0.018328 | 0.0024395 | 0.00061139
38 | 0.99714 | -0.020195 | 0.00080797 | 0.0002025
39 | 0.99657 | -0.024243 | 0 | 0
40 | 0.99634 | -0.02586 | 0.00082651 | 0.00020714
41 | 0.99626 | -0.026417 | 0.0010428 | 0.00026136
42 | 0.99517 | -0.034292 | 0.00061217 | 0.00015343
43 | 0.99596 | -0.028565 | 0.00049462 | 0.00012396
44 | 0.99591 | -0.028866 | 0.0017753 | 0.00044492
45 | 0.98762 | -0.087016 | 0.0011517 | 0.00028865
46 | 0.98765 | -0.086749 | 0.0057906 | 0.0014513
47 | 0.98792 | -0.084865 | 0.00052222 | 0.00013088
48 | 0.98808 | -0.083757 | 0.0014306 | 0.00035855
49 | 0.98811 | -0.083512 | 0.001496 | 0.00037494
50 | 0.98917 | -0.076069 | 0.0014883 | 0.000373
51 | 0.98914 | -0.076304 | 0.00064347 | 0.00016127
52 | 0.98932 | -0.075022 | 0 | 0
53 | 0.9892 | -0.075891 | 0.00040551 | 0.00010163
54 | 0.9891 | -0.07662 | 0.00078955 | 0.00019788
55 | 0.98908 | -0.076713 | 0.00023256 | 5.8285e-05
56 | 0.98252 | -0.12363 | 0.00024193 | 6.0633e-05
57 | 0.98218 | -0.12613 | 0.00079652 | 0.00019963
58 | 0.98553 | -0.1021 | 0 | 0
59 | 0.98214 | -0.12635 | 0 | 0
60 | 0.9855 | -0.10229 | 0.00079137 | 0.00019834
61 | 0.98575 | -0.1005 | 0.00048203 | 0.00012081
62 | 0.98214 | -0.12638 | 0.00030633 | 7.6772e-05
63 | 0.97994 | -0.14215 | 0 | 0
64 | 0.98644 | -0.095556 | 0.00042617 | 0.00010681
65 | 0.97873 | -0.15083 | 0.00029234 | 7.3268e-05
66 | 0.97839 | -0.15326 | 0.00093177 | 0.00023352
67 | 0.97842 | -0.15307 | 0.00049579 | 0.00012426
68 | 0.9785 | -0.1525 | 0 | 0
69 | 0.97852 | -0.15238 | 0.0031099 | 0.00077942
70 | 0.97869 | -0.15117 | 0 | 0
71 | 0.97868 | -0.15118 | 0.00015817 | 3.9641e-05
72 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0037804 | 0.00094716 | -0.0037798 | -0.00094731 | 5.6226e-07 | -1.4071e-07 | 0.0056893 | 0.0056894 | 0.0056894 | 0.98873 | -0.079085 | 0.98858 | -0.08016 | 2.1072
1 | -0.011147 | -0.0027935 | 0.01115 | 0.0027942 | 2.2745e-06 | 7.0869e-07 | 0.016776 | 0.016776 | 0.016776 | 0.98873 | -0.079085 | 0.98893 | -0.077611 | 6.2135
2 | -0.01115 | -0.0027942 | 0.01115 | 0.0027944 | 5.9519e-07 | 1.8543e-07 | 0.016776 | 0.016776 | 0.016776 | 0.98893 | -0.077611 | 0.98899 | -0.077225 | 6.2135
3 | 0.0060741 | 0.0015216 | -0.0060729 | -0.0015214 | 1.24e-06 | 1.7168e-07 | 0.0091388 | 0.0091389 | 0.0091389 | 0.98899 | -0.077225 | 0.98878 | -0.078701 | 3.3848
4 | -0.017224 | -0.004316 | 0.017248 | 0.0043244 | 2.3869e-05 | 8.4485e-06 | 0.025915 | 0.025915 | 0.025915 | 0.98899 | -0.077225 | 0.9904 | -0.067224 | 9.5982
5 | 0.0060729 | 0.0015214 | -0.0060715 | -0.0015212 | 1.3722e-06 | 1.9013e-07 | 0.0091389 | 0.009139 | 0.009139 | 0.98878 | -0.078701 | 0.98855 | -0.080335 | 3.3848
6 | -0.017979 | -0.0045076 | 0.017982 | 0.0045087 | 3.1344e-06 | 1.117e-06 | 0.027013 | 0.027013 | 0.027013 | 0.9904 | -0.067224 | 0.99058 | -0.065965 | 10.0048
7 | -0.019021 | -0.0047691 | 0.019027 | 0.0047714 | 6.3843e-06 | 2.2941e-06 | 0.028573 | 0.028573 | 0.028573 | 0.99058 | -0.065965 | 0.99092 | -0.063544 | 10.5828
8 | -0.020096 | -0.0050391 | 0.020118 | 0.005047 | 2.1917e-05 | 7.9322e-06 | 0.030177 | 0.030177 | 0.030177 | 0.99092 | -0.063544 | 0.99204 | -0.055682 | 11.1768
9 | -0.022396 | -0.005618 | 0.022457 | 0.0056403 | 6.097e-05 | 2.2329e-05 | 0.033595 | 0.033594 | 0.033595 | 0.99204 | -0.055682 | 0.99483 | -0.036103 | 12.4424
10 | -0.022457 | -0.0056403 | 0.02254 | 0.0056708 | 8.3152e-05 | 3.0442e-05 | 0.033594 | 0.033594 | 0.033594 | 0.99483 | -0.036103 | 0.99863 | -0.0095654 | 12.4423
11 | 0.0048988 | 0.0012273 | -0.0048982 | -0.0012273 | 6.0391e-07 | 4.0996e-09 | 0.0073737 | 0.0073738 | 0.0073738 | 0.98855 | -0.080335 | 0.98842 | -0.081226 | 2.731
12 | 0.0016037 | 0.00040139 | -0.0016036 | -0.0004019 | 1.5826e-07 | -5.1125e-07 | 0.0023988 | 0.002399 | 0.002399 | 0.99477 | -0.037133 | 0.99467 | -0.037847 | 0.8885
13 | -0.0020599 | -0.00051571 | 0.0020612 | 0.00051337 | 1.2938e-06 | -2.3406e-06 | 0.0030811 | 0.0030801 | 0.0030811 | 0.99477 | -0.037133 | 0.99541 | -0.032565 | 1.1411
14 | 0.00061232 | 0.00014992 | -0.00061217 | -0.00015343 | 1.4315e-07 | -3.5081e-06 | 0.0009141 | 0.00091534 | 0.00091534 | 0.99541 | -0.032565 | 0.99517 | -0.034292 | 0.33902
15 | -0.0026735 | -0.00066328 | 0.0026765 | 0.00066051 | 3.0057e-06 | -2.7747e-06 | 0.0039942 | 0.0039928 | 0.0039942 | 0.99541 | -0.032565 | 0.99657 | -0.024243 | 1.4793
16 | 0.0028782 | 0.00072101 | -0.0028778 | -0.00072125 | 3.3582e-07 | -2.3823e-07 | 0.0043328 | 0.0043329 | 0.0043329 | 0.98842 | -0.081226 | 0.98831 | -0.082069 | 1.6048
17 | -0.01272 | -0.0031891 | 0.012749 | 0.0031986 | 2.9044e-05 | 9.5522e-06 | 0.019186 | 0.019185 | 0.019186 | 0.98659 | -0.094259 | 0.98892 | -0.077807 | 7.1058
18 | 0.01272 | 0.0031891 | -0.012706 | -0.0031842 | 1.4823e-05 | 4.8781e-06 | 0.019186 | 0.019186 | 0.019186 | 0.98659 | -0.094259 | 0.98541 | -0.10268 | 7.106
19 | -0.013004 | -0.0032625 | 0.013008 | 0.0032638 | 4.1108e-06 | 1.3603e-06 | 0.019569 | 0.019568 | 0.019569 | 0.98892 | -0.077807 | 0.98924 | -0.075529 | 7.2476
20 | 0.010081 | 0.0025264 | -0.010077 | -0.0025251 | 4.2375e-06 | 1.2567e-06 | 0.015223 | 0.015223 | 0.015223 | 0.98541 | -0.10268 | 0.98498 | -0.10572 | 5.6381
21 | 0.0082278 | 0.0020618 | -0.008226 | -0.0020613 | 1.7926e-06 | 4.5285e-07 | 0.01243 | 0.01243 | 0.01243 | 0.98498 | -0.10572 | 0.98476 | -0.10729 | 4.6036
22 | 0.0050717 | 0.0012708 | -0.0050709 | -0.0012707 | 7.8378e-07 | 2.9396e-08 | 0.0076634 | 0.0076635 | 0.0076635 | 0.98476 | -0.10729 | 0.9846 | -0.10841 | 2.8383
23 | 0.0031634 | 0.00079267 | -0.0031632 | -0.00079278 | 2.0751e-07 | -1.0522e-07 | 0.0047808 | 0.0047809 | 0.0047809 | 0.9846 | -0.10841 | 0.98453 | -0.10888 | 1.7707
24 | -0.023414 | -0.005872 | 0.023431 | 0.0058781 | 1.673e-05 | 6.1568e-06 | 0.035221 | 0.035221 | 0.035221 | 0.98924 | -0.075529 | 0.98997 | -0.070378 | 13.0449
25 | 0.010406 | 0.0026082 | -0.010395 | -0.0026047 | 1.1494e-05 | 3.4567e-06 | 0.015653 | 0.015653 | 0.015653 | 0.98924 | -0.075529 | 0.98811 | -0.083512 | 5.7975
26 | 0.026136 | 0.0065762 | -0.026101 | -0.0065633 | 3.4839e-05 | 1.2916e-05 | 0.0389 | 0.0389 | 0.0389 | 1 | 0 | 0.99863 | -0.0095654 | 14.4075
27 | 0.057792 | 0.014514 | -0.057776 | -0.014508 | 1.6247e-05 | 6.2029e-06 | 0.086006 | 0.086006 | 0.086006 | 1 | 0 | 0.99971 | -0.0020229 | 31.8541
28 | 0.018727 | 0.004684 | -0.018717 | -0.0046805 | 9.594e-06 | 3.4306e-06 | 0.027871 | 0.027871 | 0.027871 | 0.99971 | -0.0020229 | 0.99918 | -0.0057401 | 10.3224
29 | 0.039049 | 0.0098241 | -0.038952 | -0.0097875 | 9.6862e-05 | 3.6654e-05 | 0.058136 | 0.058136 | 0.058136 | 0.99971 | -0.0020229 | 0.99715 | -0.019849 | 21.5318
30 | 0.036404 | 0.0091487 | -0.036163 | -0.009058 | 0.00024036 | 9.0756e-05 | 0.054333 | 0.054333 | 0.054333 | 0.99715 | -0.019849 | 0.99036 | -0.067598 | 20.1234
31 | 0.012455 | 0.0031093 | -0.012453 | -0.0031085 | 2.2963e-06 | 7.4793e-07 | 0.018709 | 0.018709 | 0.018709 | 0.99036 | -0.067598 | 0.99017 | -0.06894 | 6.9294
32 | 0.023708 | 0.0059487 | -0.023699 | -0.0059453 | 9.1406e-06 | 3.3671e-06 | 0.035624 | 0.035624 | 0.035624 | 0.99036 | -0.067598 | 0.98997 | -0.070378 | 13.1941
33 | 0.015799 | 0.0039492 | -0.015783 | -0.0039436 | 1.5993e-05 | 5.545e-06 | 0.023525 | 0.023525 | 0.023525 | 0.99918 | -0.0057401 | 0.99814 | -0.013097 | 8.7129
34 | 0.0035629 | 0.00088778 | -0.0035601 | -0.00088873 | 2.8368e-06 | -9.4808e-07 | 0.0053525 | 0.0053532 | 0.0053532 | 0.99017 | -0.06894 | 0.98936 | -0.07475 | 1.9827
35 | 0.0088897 | 0.0022208 | -0.008881 | -0.0022184 | 8.7745e-06 | 2.362e-06 | 0.013357 | 0.013357 | 0.013357 | 0.99017 | -0.06894 | 0.98916 | -0.07612 | 4.9471
36 | 0.012331 | 0.0030784 | -0.012326 | -0.003077 | 4.4874e-06 | 1.4478e-06 | 0.018379 | 0.018379 | 0.018379 | 0.99814 | -0.013097 | 0.99776 | -0.015747 | 6.8069
37 | 0.001428 | 0.00035554 | -0.0014279 | -0.00035575 | 5.309e-08 | -2.1661e-07 | 0.0021468 | 0.0021469 | 0.0021469 | 0.98936 | -0.07475 | 0.98932 | -0.075022 | 0.79516
38 | 0.0021322 | 0.00053319 | -0.0021318 | -0.00053382 | 3.8824e-07 | -6.2762e-07 | 0.0032064 | 0.0032067 | 0.0032067 | 0.98936 | -0.07475 | 0.98917 | -0.076069 | 1.1877
39 | 0.0080998 | 0.0020226 | -0.0080782 | -0.0020173 | 2.1609e-05 | 5.3242e-06 | 0.012182 | 0.012183 | 0.012183 | 0.98916 | -0.07612 | 0.98644 | -0.095556 | 4.5123
40 | 0.011007 | 0.0027463 | -0.011004 | -0.0027454 | 3.1877e-06 | 9.7837e-07 | 0.016411 | 0.016411 | 0.016411 | 0.99776 | -0.015747 | 0.99747 | -0.017858 | 6.0782
41 | 0.010071 | 0.0025117 | -0.010071 | -0.0025115 | 6.4956e-07 | 1.8961e-07 | 0.01502 | 0.01502 | 0.01502 | 0.99747 | -0.017858 | 0.9974 | -0.018328 | 5.563
42 | 0.0076313 | 0.0019001 | -0.0076294 | -0.0018997 | 1.9469e-06 | 4.3451e-07 | 0.011381 | 0.011381 | 0.011381 | 0.9974 | -0.018328 | 0.99714 | -0.020195 | 4.2151
43 | 0.0068214 | 0.0016972 | -0.0068176 | -0.0016965 | 3.7673e-06 | 6.8877e-07 | 0.010175 | 0.010175 | 0.010175 | 0.99714 | -0.020195 | 0.99657 | -0.024243 | 3.7687
44 | 0.0041411 | 0.001036 | -0.0041402 | -0.0010361 | 9.2417e-07 | -1.4925e-07 | 0.0061826 | 0.0061828 | 0.0061828 | 0.99657 | -0.024243 | 0.99634 | -0.02586 | 2.2899
45 | 0.0033137 | 0.00082897 | -0.0033134 | -0.00082909 | 2.5465e-07 | -1.1908e-07 | 0.0049484 | 0.0049485 | 0.0049485 | 0.99634 | -0.02586 | 0.99626 | -0.026417 | 1.8328
46 | 0.0022706 | 0.00056773 | -0.0022699 | -0.00056869 | 6.7303e-07 | -9.6204e-07 | 0.0033909 | 0.0033914 | 0.0033914 | 0.99626 | -0.026417 | 0.99596 | -0.028565 | 1.2561
47 | 0.0017753 | 0.00044473 | -0.0017753 | -0.00044492 | 7.3938e-08 | -1.9073e-07 | 0.0026524 | 0.0026524 | 0.0026524 | 0.99596 | -0.028565 | 0.99591 | -0.028866 | 0.98239
48 | -0.0011517 | -0.00028865 | 0.0011518 | 0.00028838 | 4.2448e-08 | -2.7278e-07 | 0.0017353 | 0.0017352 | 0.0017353 | 0.98762 | -0.087016 | 0.98765 | -0.086749 | 0.6427
49 | -0.0069424 | -0.0017396 | 0.0069442 | 0.00174 | 1.811e-06 | 3.5695e-07 | 0.010459 | 0.010459 | 0.010459 | 0.98765 | -0.086749 | 0.98792 | -0.084865 | 3.8739
50 | -0.0074664 | -0.0018709 | 0.0074676 | 0.0018711 | 1.1447e-06 | 2.5452e-07 | 0.011246 | 0.011246 | 0.011246 | 0.98792 | -0.084865 | 0.98808 | -0.083757 | 4.1651
51 | -0.0088982 | -0.0022297 | 0.0088985 | 0.0022298 | 3.01e-07 | 8.1362e-08 | 0.0134 | 0.0134 | 0.0134 | 0.98808 | -0.083757 | 0.98811 | -0.083512 | 4.9631
52 | 0.00064349 | 0.00016082 | -0.00064347 | -0.00016127 | 2.0818e-08 | -4.4909e-07 | 0.00096784 | 0.000968 | 0.000968 | 0.98917 | -0.076069 | 0.98914 | -0.076304 | 0.35852
53 | 0.0014279 | 0.00035575 | -0.0014277 | -0.00035645 | 1.7016e-07 | -6.9404e-07 | 0.0021469 | 0.0021472 | 0.0021472 | 0.98932 | -0.075022 | 0.9892 | -0.075891 | 0.79526
54 | 0.0010222 | 0.00025482 | -0.0010221 | -0.00025567 | 1.0249e-07 | -8.5263e-07 | 0.0015372 | 0.0015375 | 0.0015375 | 0.9892 | -0.075891 | 0.9891 | -0.07662 | 0.56945
55 | 0.00023256 | 5.7789e-05 | -0.00023256 | -5.8285e-05 | 2.9556e-09 | -4.9573e-07 | 0.0003497 | 0.00034987 | 0.00034987 | 0.9891 | -0.07662 | 0.98908 | -0.076713 | 0.12958
56 | 0.0061111 | 0.0015264 | -0.006109 | -0.0015261 | 2.0991e-06 | 3.0996e-07 | 0.0092533 | 0.0092535 | 0.0092535 | 0.98252 | -0.12363 | 0.98218 | -0.12613 | 3.4272
57 | -0.006353 | -0.001587 | 0.0063718 | 0.0015901 | 1.8827e-05 | 3.0986e-06 | 0.0096197 | 0.0096182 | 0.0096197 | 0.98252 | -0.12363 | 0.98553 | -0.1021 | 3.5628
58 | 0.0053125 | 0.0013264 | -0.0053123 | -0.0013264 | 1.6098e-07 | 1.1493e-08 | 0.0080467 | 0.0080467 | 0.0080467 | 0.98218 | -0.12613 | 0.98214 | -0.12635 | 2.9803
59 | 0.00079139 | 0.00019804 | -0.00079137 | -0.00019834 | 2.0983e-08 | -2.9206e-07 | 0.0011948 | 0.0011949 | 0.0011949 | 0.98553 | -0.1021 | 0.9855 | -0.10229 | 0.44255
60 | -0.0071632 | -0.0017881 | 0.0071648 | 0.0017885 | 1.5737e-06 | 3.3036e-07 | 0.010813 | 0.010813 | 0.010813 | 0.98553 | -0.1021 | 0.98575 | -0.1005 | 4.0048
61 | 0.00030633 | 7.6675e-05 | -0.00030633 | -7.6772e-05 | 1.0439e-09 | -9.7897e-08 | 0.00046407 | 0.00046411 | 0.00046411 | 0.98214 | -0.12635 | 0.98214 | -0.12638 | 0.17189
62 | 0.005006 | 0.0012497 | -0.0049951 | -0.0012494 | 1.087e-05 | 3.5595e-07 | 0.0075827 | 0.007584 | 0.007584 | 0.98214 | -0.12635 | 0.97994 | -0.14215 | 2.8089
63 | -0.0076468 | -0.0019093 | 0.007652 | 0.0019105 | 5.1971e-06 | 1.2011e-06 | 0.011541 | 0.01154 | 0.011541 | 0.98575 | -0.1005 | 0.98644 | -0.095556 | 4.2743
64 | 0.0049951 | 0.0012494 | -0.0049891 | -0.0012492 | 5.9857e-06 | 2.0392e-07 | 0.007584 | 0.0075848 | 0.0075848 | 0.97994 | -0.14215 | 0.97873 | -0.15083 | 2.8092
65 | 0.0046968 | 0.0011759 | -0.0046966 | -0.0011759 | 2.1795e-07 | -2.263e-09 | 0.0071403 | 0.0071404 | 0.0071404 | 0.97873 | -0.15083 | 0.97869 | -0.15117 | 2.6446
66 | -0.00093177 | -0.00023352 | 0.00093179 | 0.00023329 | 2.4508e-08 | -2.3621e-07 | 0.0014171 | 0.001417 | 0.0014171 | 0.97839 | -0.15326 | 0.97842 | -0.15307 | 0.52485
67 | -0.0014276 | -0.00035754 | 0.0014277 | 0.00035711 | 1.124e-07 | -4.3682e-07 | 0.002171 | 0.0021709 | 0.002171 | 0.97842 | -0.15307 | 0.9785 | -0.1525 | 0.80409
68 | -0.0014277 | -0.00035711 | 0.0014277 | 0.00035701 | 2.4575e-08 | -9.5523e-08 | 0.0021709 | 0.0021708 | 0.0021709 | 0.9785 | -0.1525 | 0.97852 | -0.15238 | 0.80402
69 | -0.0045376 | -0.0011364 | 0.0045384 | 0.0011364 | 7.5829e-07 | -2.9035e-08 | 0.0069 | 0.0068999 | 0.0069 | 0.97852 | -0.15238 | 0.97869 | -0.15117 | 2.5556
70 | 0.00015817 | 3.9522e-05 | -0.00015817 | -3.9641e-05 | 3.4055e-10 | -1.1847e-07 | 0.00024044 | 0.00024048 | 0.00024048 | 0.97869 | -0.15117 | 0.97868 | -0.15118 | 0.089068

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.084728 | 0.021091

## res_load
| p_mw | q_mvar
0 | 0.007367 | 0.0018463
1 | 0.0037798 | 0.00094731
2 | 0.00073077 | 0.00018315
3 | 0.0010389 | 0.00026038
4 | 0.0010682 | 0.00026772
5 | 0.0022783 | 0.00057099
6 | 0.0011728 | 0.00029392
7 | 0.00045615 | 0.00011432
8 | 0.0016036 | 0.0004019
9 | 0.00202 | 0.00050626
10 | 0.0028778 | 0.00072125
11 | 0.00025474 | 6.3843e-05
12 | 0.0026247 | 0.00065781
13 | 0.0018489 | 0.00046337
14 | 0.0031543 | 0.00079055
15 | 0.0019074 | 0.00047805
16 | 0.0035613 | 0.00089256
17 | 0.0031632 | 0.00079278
18 | 0.0025486 | 0.00063873
19 | 0.0029182 | 0.00073137
20 | 0.00026805 | 6.718e-05
21 | 0.0034521 | 0.00086517
22 | 0.00078115 | 0.00019577
23 | 0.0013193 | 0.00033066
24 | 0.00093244 | 0.00023369
25 | 0.0024395 | 0.00061139
26 | 0.00080797 | 0.0002025
27 | 0.00082651 | 0.00020714
28 | 0.0010428 | 0.00026136
29 | 0.00061217 | 0.00015343
30 | 0.00049462 | 0.00012396
31 | 0.0017753 | 0.00044492
32 | 0.0011517 | 0.00028865
33 | 0.0057906 | 0.0014513
34 | 0.00052222 | 0.00013088
35 | 0.0014306 | 0.00035855
36 | 0.001496 | 0.00037494
37 | 0.0014883 | 0.000373
38 | 0.00064347 | 0.00016127
39 | 0.00040551 | 0.00010163
40 | 0.00078955 | 0.00019788
41 | 0.00023256 | 5.8285e-05
42 | 0.00024193 | 6.0633e-05
43 | 0.00079652 | 0.00019963
44 | 0.00079137 | 0.00019834
45 | 0.00048203 | 0.00012081
46 | 0.00030633 | 7.6772e-05
47 | 0.00042617 | 0.00010681
48 | 0.00029234 | 7.3268e-05
49 | 0.00093177 | 0.00023352
50 | 0.00049579 | 0.00012426
51 | 0.0031099 | 0.00077942
52 | 0.00015817 | 3.9641e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1