## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1098-8_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1098-8_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1098-8_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1098-8_0_2_node_32 | 0.4 | n |  | TRUE
4 | bus_LV_1098-8_0_2_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_1098-8_0_2_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1098-8_0_2_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1098-8_0_2_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_1098-8_0_2_node_23 | 0.4 | n |  | TRUE
9 | bus_LV_1098-8_0_2_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_1098-8_0_2_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1098-8_0_2_node_18 | 0.4 | n |  | TRUE
12 | bus_LV_1098-8_0_2_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1098-8_0_2_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_1098-8_0_2_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_1098-8_0_2_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_1098-8_0_2_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_1098-8_0_2_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_1098-8_0_2_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_1098-8_0_2_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1098-8_0_2_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_1098-8_0_2_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1098-8_0_2_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1098-8_0_2_node_34 | 0.4 | n |  | TRUE
24 | bus_MV_0_node_22 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1098-8_0_2_load_0 | 0 | 0.00053722 | 0.00013464 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1098-8_0_2_load_1 | 1 | 0.00062905 | 0.00015765 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1098-8_0_2_load_2 | 2 | 0.00070427 | 0.00017651 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1098-8_0_2_load_5 | 6 | 0.001552 | 0.00038896 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1098-8_0_2_load_26 | 7 | 0.0011774 | 0.00029509 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1098-8_0_2_load_23 | 8 | 0.0017737 | 0.00044454 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1098-8_0_2_load_16 | 9 | 0.00055668 | 0.00013952 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1098-8_0_2_load_17 | 10 | 0.0036062 | 0.0009038 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1098-8_0_2_load_19 | 13 | 0.0025302 | 0.00063413 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1098-8_0_2_load_21 | 15 | 0.00057699 | 0.00014461 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1098-8_0_2_load_30 | 17 | 0.0010077 | 0.00025255 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1098-8_0_2_load_31 | 18 | 0.00040344 | 0.00010111 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1098-8_0_2_load_29 | 19 | 0.00027433 | 6.8752e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1098-8_0_2_load_25 | 20 | 0.0025381 | 0.00063611 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1098-8_0_2_load_27 | 21 | 0.00053024 | 0.00013289 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1098-8_0_2_load_33 | 22 | 0.00045326 | 0.0001136 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1098-8_0_2_load_34 | 23 | 0.00053051 | 0.00013296 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 16 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1098-8_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.02759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1098-8_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.023752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1098-8_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0033217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1098-8_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.17864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1098-8_0_2_line_4 | NAYY 4x150 SE | 3 | 22 | 0.039538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1098-8_0_2_line_5 | NAYY 4x150 SE | 4 | 21 | 0.10033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1098-8_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.056881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1098-8_0_2_line_7 | NAYY 4x150 SE | 5 | 7 | 0.34785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1098-8_0_2_line_8 | NAYY 4x150 SE | 6 | 8 | 0.011367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1098-8_0_2_line_9 | NAYY 4x150 SE | 7 | 20 | 0.027618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1098-8_0_2_line_10 | NAYY 4x150 SE | 8 | 15 | 0.0074521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1098-8_0_2_line_11 | NAYY 4x150 SE | 9 | 10 | 0.025238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1098-8_0_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.082897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1098-8_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.19463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1098-8_0_2_line_14 | NAYY 4x150 SE | 12 | 18 | 0.088266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1098-8_0_2_line_15 | NAYY 4x150 SE | 12 | 19 | 0.0030643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1098-8_0_2_line_16 | NAYY 4x150 SE | 13 | 14 | 0.041419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1098-8_0_2_line_17 | NAYY 4x150 SE | 14 | 15 | 0.013514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1098-8_0_2_line_18 | NAYY 4x150 SE | 14 | 16 | 0.25073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1098-8_0_2_line_19 | NAYY 4x150 SE | 16 | 17 | 0.12319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1098-8_0_2_line_20 | NAYY 4x150 SE | 17 | 19 | 0.029274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1098-8_0_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.025525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1098-8_0_2_line_22 | NAYY 4x150 SE | 22 | 23 | 0.029532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1098-8_0_2_trafo_22 | 0.25 MVA 20/0.4 kV | 24 | 16 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2650709.2016 | 1216086.3552 | 2650732.4666 | 1216076.9906 | 2650734.6656 | 1216075.7778
1 | 2650734.6656 | 1216075.7778 | 2650755.4643 | 1216064.3067
2 | 2650758.3729 | 1216062.7024 | 2650755.4643 | 1216064.3067
3 | 2650755.4643 | 1216064.3067 | 2650842.8196 | 1216220.1274
4 | 2650758.3729 | 1216062.7024 | 2650781.427 | 1216047.2227 | 2650790.566 | 1216039.8076
5 | 2650842.8196 | 1216220.1274 | 2650832.2593 | 1216227.1527 | 2650777.6796 | 1216275.0055 | 2650765.8675 | 1216284.3427
6 | 2650373.6405 | 1216327.422 | 2650369.9254 | 1216330.4146 | 2650347.022 | 1216341.7948 | 2650334.9861 | 1216344.7394 | 2650329.8886 | 1216345.0966 | 2650321.1542 | 1216342.7882
7 | 2650373.6405 | 1216327.422 | 2650719.7027 | 1216292.1965
8 | 2650310.3625 | 1216344.954 | 2650316.0861 | 1216342.3674 | 2650321.1542 | 1216342.7882
9 | 2650745.843 | 1216300.1719 | 2650745.843 | 1216300.1719 | 2650732.1313 | 1216293.9181 | 2650719.7027 | 1216292.1965
10 | 2650304.5323 | 1216349.5953 | 2650310.3625 | 1216344.954 | 2650310.3625 | 1216344.954
11 | 2649982.3812 | 1215943.1305 | 2649979.0726 | 1215939.3032 | 2649978.3872 | 1215935.9288 | 2649979.2319 | 1215932.078 | 2649988.6272 | 1215923.3957
12 | 2649989.8767 | 1216015.4171 | 2649987.6017 | 1216002.4014 | 2649989.4901 | 1215996.3247 | 2649998.7544 | 1215984.4174 | 2650001.2433 | 1215979.1684 | 2650001.895 | 1215973.893 | 2650000.1283 | 1215966.3625 | 2649996.2179 | 1215959.1365 | 2649982.3812 | 1215943.1305
13 | 2649989.8767 | 1216015.4171 | 2650005.7387 | 1216023.466 | 2650022.1925 | 1216036.9899 | 2650035.3351 | 1216050.5972 | 2650057.5594 | 1216076.7438 | 2650071.3682 | 1216088.7558 | 2650078.6075 | 1216093.7529 | 2650091.8231 | 1216104.07 | 2650129.015 | 1216128.0413 | 2650141.2236 | 1216135.2927
14 | 2650141.2236 | 1216135.2927 | 2650168.5287 | 1216215.3148 | 2650169.9443 | 1216218.7482
15 | 2650141.2236 | 1216135.2927 | 2650143.9734 | 1216136.6451
16 | 2650293.9592 | 1216358.0124 | 2650309.9673 | 1216374.6796 | 2650323.6107 | 1216386.8898
17 | 2650293.9592 | 1216358.0124 | 2650304.5323 | 1216349.5953
18 | 2650287.4274 | 1216183.7082 | 2650287.7957 | 1216188.6587 | 2650285.9856 | 1216194.4247 | 2650270.3785 | 1216213.8715 | 2650211.349 | 1216300.1705 | 2650206.7894 | 1216309.6934 | 2650275.9165 | 1216348.5212 | 2650293.9592 | 1216358.0124
19 | 2650287.4274 | 1216183.7082 | 2650283.5033 | 1216179.0723 | 2650258.4608 | 1216168.5438 | 2650219.0447 | 1216158.1389 | 2650180.927 | 1216150.4023 | 2650171.0782 | 1216147.4383
20 | 2650143.9734 | 1216136.6451 | 2650157.7828 | 1216143.4368 | 2650171.0782 | 1216147.4383
21 | 2650745.843 | 1216300.1719 | 2650765.8675 | 1216284.3427
22 | 2650790.566 | 1216039.8076 | 2650801.9706 | 1216030.5543 | 2650812.1936 | 1216019.7889

## bus_geodata
| x | y | coords
0 | 2650709.2016 | 1216086.3552
1 | 2650734.6656 | 1216075.7778
2 | 2650755.4643 | 1216064.3067
3 | 2650758.3729 | 1216062.7024
4 | 2650842.8196 | 1216220.1274
5 | 2650373.6405 | 1216327.422
6 | 2650321.1542 | 1216342.7882
7 | 2650719.7027 | 1216292.1965
8 | 2650310.3625 | 1216344.954
9 | 2649988.6272 | 1215923.3957
10 | 2649982.3812 | 1215943.1305
11 | 2649989.8767 | 1216015.4171
12 | 2650141.2236 | 1216135.2927
13 | 2650323.6107 | 1216386.8898
14 | 2650293.9592 | 1216358.0124
15 | 2650304.5323 | 1216349.5953
16 | 2650287.4274 | 1216183.7082
17 | 2650171.0782 | 1216147.4383
18 | 2650169.9443 | 1216218.7482
19 | 2650143.9734 | 1216136.6451
20 | 2650745.843 | 1216300.1719
21 | 2650765.8675 | 1216284.3427
22 | 2650790.566 | 1216039.8076
23 | 2650812.1936 | 1216019.7889
24 | 2650287.4274 | 1216183.7082

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98896 | -0.078145 | 0.00053722 | 0.00013464
1 | 0.98898 | -0.077993 | 0.00062905 | 0.00015765
2 | 0.98902 | -0.077709 | 0.00070427 | 0.00017651
3 | 0.98901 | -0.077743 | 0 | 0
4 | 0.98975 | -0.072474 | 0 | 0
5 | 0.99408 | -0.041711 | 0 | 0
6 | 0.99466 | -0.037589 | 0.001552 | 0.00038896
7 | 0.99052 | -0.066957 | 0.0011774 | 0.00029509
8 | 0.9948 | -0.036587 | 0.0017737 | 0.00044454
9 | 0.99708 | -0.02059 | 0.00055668 | 0.00013952
10 | 0.9971 | -0.020449 | 0.0036062 | 0.0009038
11 | 0.99759 | -0.016981 | 0 | 0
12 | 0.99875 | -0.0088261 | 0 | 0
13 | 0.99498 | -0.035344 | 0.0025302 | 0.00063413
14 | 0.99513 | -0.034287 | 0 | 0
15 | 0.99491 | -0.035797 | 0.00057699 | 0.00014461
16 | 1 | 0 | -0.020298 | -0.00488
17 | 0.99897 | -0.0072558 | 0.0010077 | 0.00025255
18 | 0.9987 | -0.0091862 | 0.00040344 | 0.00010111
19 | 0.99877 | -0.0086849 | 0.00027433 | 6.8752e-05
20 | 0.99029 | -0.068633 | 0.0025381 | 0.00063611
21 | 0.99016 | -0.069523 | 0.00053024 | 0.00013289
22 | 0.98896 | -0.078142 | 0.00045326 | 0.0001136
23 | 0.98893 | -0.078302 | 0.00053051 | 0.00013296
24 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00053722 | -0.00013464 | 0.00053723 | 0.00013429 | 1.1247e-08 | -3.497e-07 | 0.00080832 | 0.0008082 | 0.00080832 | 0.98896 | -0.078145 | 0.98898 | -0.077993 | 0.29938
1 | -0.0011663 | -0.00029194 | 0.0011663 | 0.00029166 | 4.563e-08 | -2.8724e-07 | 0.0017547 | 0.0017546 | 0.0017547 | 0.98898 | -0.077993 | 0.98902 | -0.077709 | 0.64987
2 | 0.00098383 | 0.00024565 | -0.00098383 | -0.00024569 | 4.5395e-09 | -4.088e-08 | 0.0014799 | 0.0014799 | 0.0014799 | 0.98902 | -0.077709 | 0.98901 | -0.077743 | 0.54811
3 | -0.0028544 | -0.00071381 | 0.0028565 | 0.00071231 | 2.055e-06 | -1.5037e-06 | 0.004294 | 0.0042932 | 0.004294 | 0.98902 | -0.077709 | 0.98975 | -0.072474 | 1.5904
4 | 0.00098383 | 0.00024569 | -0.00098377 | -0.00024618 | 5.404e-08 | -4.8656e-07 | 0.0014799 | 0.0014801 | 0.0014801 | 0.98901 | -0.077743 | 0.98896 | -0.078142 | 0.54818
5 | -0.0028565 | -0.00071231 | 0.0028576 | 0.00071146 | 1.1538e-06 | -8.4615e-07 | 0.0042932 | 0.0042928 | 0.0042932 | 0.98975 | -0.072474 | 0.99016 | -0.069523 | 1.5901
6 | -0.0071299 | -0.0017806 | 0.0071339 | 0.0017814 | 4.0411e-06 | 8.1641e-07 | 0.01067 | 0.01067 | 0.01067 | 0.99408 | -0.041711 | 0.99466 | -0.037589 | 3.952
7 | 0.0071299 | 0.0017806 | -0.0071052 | -0.0017756 | 2.4717e-05 | 5.0131e-06 | 0.01067 | 0.010672 | 0.010672 | 0.99408 | -0.041711 | 0.99052 | -0.066957 | 3.9526
8 | -0.0086859 | -0.0021703 | 0.0086871 | 0.0021707 | 1.1972e-06 | 3.1289e-07 | 0.012992 | 0.012992 | 0.012992 | 0.99466 | -0.037589 | 0.9948 | -0.036587 | 4.8118
9 | 0.0059278 | 0.0014805 | -0.0059264 | -0.0014803 | 1.3661e-06 | 1.7e-07 | 0.0089032 | 0.0089033 | 0.0089033 | 0.99052 | -0.066957 | 0.99029 | -0.068633 | 3.2975
10 | -0.010461 | -0.0026152 | 0.010462 | 0.0026155 | 1.1382e-06 | 3.41e-07 | 0.015645 | 0.015645 | 0.015645 | 0.9948 | -0.036587 | 0.99491 | -0.035797 | 5.7944
11 | -0.00055668 | -0.00013952 | 0.00055669 | 0.00013919 | 1.0868e-08 | -3.2499e-07 | 0.00083077 | 0.00083066 | 0.00083077 | 0.99708 | -0.02059 | 0.9971 | -0.020449 | 0.30769
12 | -0.0041629 | -0.001043 | 0.0041649 | 0.0010427 | 1.9962e-06 | -3.1399e-07 | 0.0062124 | 0.006212 | 0.0062124 | 0.9971 | -0.020449 | 0.99759 | -0.016981 | 2.3009
13 | -0.0041649 | -0.0010427 | 0.0041696 | 0.0010419 | 4.686e-06 | -7.4179e-07 | 0.006212 | 0.0062111 | 0.006212 | 0.99759 | -0.016981 | 0.99875 | -0.0088261 | 2.3007
14 | 0.00040346 | 9.9965e-05 | -0.00040344 | -0.00010111 | 1.9888e-08 | -1.1474e-06 | 0.00060071 | 0.00060111 | 0.00060111 | 0.99875 | -0.0088261 | 0.9987 | -0.0091862 | 0.22263
15 | -0.0045731 | -0.0011419 | 0.0045731 | 0.0011419 | 8.8725e-08 | -5.9771e-09 | 0.0068118 | 0.0068118 | 0.0068118 | 0.99875 | -0.0088261 | 0.99877 | -0.0086849 | 2.5229
16 | -0.0025302 | -0.00063413 | 0.0025306 | 0.00063373 | 3.7005e-07 | -3.957e-07 | 0.003784 | 0.0037838 | 0.003784 | 0.99498 | -0.035344 | 0.99513 | -0.034287 | 1.4015
17 | 0.011041 | 0.0027609 | -0.011039 | -0.0027601 | 2.298e-06 | 7.0832e-07 | 0.016508 | 0.016508 | 0.016508 | 0.99513 | -0.034287 | 0.99491 | -0.035797 | 6.114
18 | -0.013572 | -0.0033946 | 0.013636 | 0.0034161 | 6.4417e-05 | 2.1502e-05 | 0.020292 | 0.02029 | 0.020292 | 0.99513 | -0.034287 | 1 | 0 | 7.5154
19 | 0.005862 | 0.0014638 | -0.0058561 | -0.0014632 | 5.8464e-06 | 6.3417e-07 | 0.0087208 | 0.0087214 | 0.0087214 | 1 | 0 | 0.99897 | -0.0072558 | 3.2301
20 | 0.0048484 | 0.0012106 | -0.0048475 | -0.0012107 | 9.5234e-07 | -1.6899e-08 | 0.0072204 | 0.0072205 | 0.0072205 | 0.99897 | -0.0072558 | 0.99877 | -0.0086849 | 2.6743
21 | 0.0033883 | 0.00084418 | -0.0033879 | -0.00084435 | 4.1259e-07 | -1.6967e-07 | 0.0050895 | 0.0050896 | 0.0050896 | 0.99029 | -0.068633 | 0.99016 | -0.069523 | 1.885
22 | 0.00053052 | 0.00013258 | -0.00053051 | -0.00013296 | 1.174e-08 | -3.7441e-07 | 0.0007981 | 0.00079824 | 0.00079824 | 0.98896 | -0.078142 | 0.98893 | -0.078302 | 0.29564

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.020298 | 0.00488

## res_load
| p_mw | q_mvar
0 | 0.00053722 | 0.00013464
1 | 0.00062905 | 0.00015765
2 | 0.00070427 | 0.00017651
3 | 0.001552 | 0.00038896
4 | 0.0011774 | 0.00029509
5 | 0.0017737 | 0.00044454
6 | 0.00055668 | 0.00013952
7 | 0.0036062 | 0.0009038
8 | 0.0025302 | 0.00063413
9 | 0.00057699 | 0.00014461
10 | 0.0010077 | 0.00025255
11 | 0.00040344 | 0.00010111
12 | 0.00027433 | 6.8752e-05
13 | 0.0025381 | 0.00063611
14 | 0.00053024 | 0.00013289
15 | 0.00045326 | 0.0001136
16 | 0.00053051 | 0.00013296

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1