## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1107-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1107-11_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1107-11_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1107-11_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1107-11_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1107-11_0_4_node_50 | 0.4 | n |  | TRUE
6 | bus_LV_1107-11_0_4_node_51 | 0.4 | n |  | TRUE
7 | bus_LV_1107-11_0_4_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_1107-11_0_4_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_1107-11_0_4_node_16 | 0.4 | n |  | TRUE
10 | bus_LV_1107-11_0_4_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_1107-11_0_4_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_1107-11_0_4_node_84 | 0.4 | n |  | TRUE
13 | bus_LV_1107-11_0_4_node_86 | 0.4 | n |  | TRUE
14 | bus_LV_1107-11_0_4_node_82 | 0.4 | n |  | TRUE
15 | bus_LV_1107-11_0_4_node_20 | 0.4 | n |  | TRUE
16 | bus_LV_1107-11_0_4_node_83 | 0.4 | n |  | TRUE
17 | bus_LV_1107-11_0_4_node_26 | 0.4 | n |  | TRUE
18 | bus_LV_1107-11_0_4_node_27 | 0.4 | n |  | TRUE
19 | bus_LV_1107-11_0_4_node_39 | 0.4 | n |  | TRUE
20 | bus_LV_1107-11_0_4_node_40 | 0.4 | n |  | TRUE
21 | bus_LV_1107-11_0_4_node_41 | 0.4 | n |  | TRUE
22 | bus_LV_1107-11_0_4_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_1107-11_0_4_node_87 | 0.4 | n |  | TRUE
24 | bus_LV_1107-11_0_4_node_88 | 0.4 | n |  | TRUE
25 | bus_LV_1107-11_0_4_node_52 | 0.4 | n |  | TRUE
26 | bus_LV_1107-11_0_4_node_53 | 0.4 | n |  | TRUE
27 | bus_LV_1107-11_0_4_node_54 | 0.4 | n |  | TRUE
28 | bus_LV_1107-11_0_4_node_55 | 0.4 | n |  | TRUE
29 | bus_LV_1107-11_0_4_node_56 | 0.4 | n |  | TRUE
30 | bus_LV_1107-11_0_4_node_100 | 0.4 | n |  | TRUE
31 | bus_LV_1107-11_0_4_node_101 | 0.4 | n |  | TRUE
32 | bus_LV_1107-11_0_4_node_60 | 0.4 | n |  | TRUE
33 | bus_LV_1107-11_0_4_node_61 | 0.4 | n |  | TRUE
34 | bus_LV_1107-11_0_4_node_62 | 0.4 | n |  | TRUE
35 | bus_LV_1107-11_0_4_node_64 | 0.4 | n |  | TRUE
36 | bus_LV_1107-11_0_4_node_65 | 0.4 | n |  | TRUE
37 | bus_LV_1107-11_0_4_node_69 | 0.4 | n |  | TRUE
38 | bus_LV_1107-11_0_4_node_70 | 0.4 | n |  | TRUE
39 | bus_LV_1107-11_0_4_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_1107-11_0_4_node_67 | 0.4 | n |  | TRUE
41 | bus_LV_1107-11_0_4_node_107 | 0.4 | n |  | TRUE
42 | bus_LV_1107-11_0_4_node_108 | 0.4 | n |  | TRUE
43 | bus_LV_1107-11_0_4_node_71 | 0.4 | n |  | TRUE
44 | bus_LV_1107-11_0_4_node_72 | 0.4 | n |  | TRUE
45 | bus_LV_1107-11_0_4_node_73 | 0.4 | n |  | TRUE
46 | bus_LV_1107-11_0_4_node_74 | 0.4 | n |  | TRUE
47 | bus_LV_1107-11_0_4_node_75 | 0.4 | n |  | TRUE
48 | bus_LV_1107-11_0_4_node_76 | 0.4 | n |  | TRUE
49 | bus_LV_1107-11_0_4_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_1107-11_0_4_node_80 | 0.4 | n |  | TRUE
51 | bus_LV_1107-11_0_4_node_99 | 0.4 | n |  | TRUE
52 | bus_LV_1107-11_0_4_node_78 | 0.4 | n |  | TRUE
53 | bus_LV_1107-11_0_4_node_81 | 0.4 | n |  | TRUE
54 | bus_LV_1107-11_0_4_node_77 | 0.4 | n |  | TRUE
55 | bus_LV_1107-11_0_4_node_103 | 0.4 | n |  | TRUE
56 | bus_LV_1107-11_0_4_node_97 | 0.4 | n |  | TRUE
57 | bus_LV_1107-11_0_4_node_104 | 0.4 | n |  | TRUE
58 | bus_LV_1107-11_0_4_node_85 | 0.4 | n |  | TRUE
59 | bus_LV_1107-11_0_4_node_98 | 0.4 | n |  | TRUE
60 | bus_LV_1107-11_0_4_node_89 | 0.4 | n |  | TRUE
61 | bus_LV_1107-11_0_4_node_90 | 0.4 | n |  | TRUE
62 | bus_LV_1107-11_0_4_node_91 | 0.4 | n |  | TRUE
63 | bus_LV_1107-11_0_4_node_92 | 0.4 | n |  | TRUE
64 | bus_LV_1107-11_0_4_node_102 | 0.4 | n |  | TRUE
65 | bus_LV_1107-11_0_4_node_110 | 0.4 | n |  | TRUE
66 | bus_LV_1107-11_0_4_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_1107-11_0_4_node_94 | 0.4 | n |  | TRUE
68 | bus_LV_1107-11_0_4_node_95 | 0.4 | n |  | TRUE
69 | bus_LV_1107-11_0_4_node_96 | 0.4 | n |  | TRUE
70 | bus_LV_1107-11_0_4_node_106 | 0.4 | n |  | TRUE
71 | bus_LV_1107-11_0_4_node_112 | 0.4 | n |  | TRUE
72 | bus_LV_1107-11_0_4_node_105 | 0.4 | n |  | TRUE
73 | bus_LV_1107-11_0_4_node_111 | 0.4 | n |  | TRUE
74 | bus_LV_1107-11_0_4_node_109 | 0.4 | n |  | TRUE
75 | bus_MV_124_0_node_140 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1107-11_0_4_load_0 | 0 | 0.0013929 | 0.00034909 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1107-11_0_4_load_1 | 1 | 0.00055565 | 0.00013926 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1107-11_0_4_load_2 | 2 | 0.0015067 | 0.00037762 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1107-11_0_4_load_3 | 3 | 0.00052895 | 0.00013257 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1107-11_0_4_load_50 | 5 | 0.00075978 | 0.00019042 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1107-11_0_4_load_15 | 7 | 0.00034775 | 8.7153e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1107-11_0_4_load_22 | 8 | 0.00041996 | 0.00010525 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1107-11_0_4_load_16 | 9 | 0.00045942 | 0.00011514 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1107-11_0_4_load_21 | 11 | 0.0014413 | 0.00036122 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1107-11_0_4_load_82 | 14 | 0.00028364 | 7.1087e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1107-11_0_4_load_20 | 15 | 0.0022644 | 0.00056751 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1107-11_0_4_load_83 | 16 | 0.00061711 | 0.00015466 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1107-11_0_4_load_26 | 17 | 0.00039284 | 9.8455e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1107-11_0_4_load_27 | 18 | 0.00069777 | 0.00017488 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1107-11_0_4_load_40 | 20 | 0.00037994 | 9.5222e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1107-11_0_4_load_41 | 21 | 0.0018622 | 0.0004667 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1107-11_0_4_load_43 | 22 | 0.0016006 | 0.00040115 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1107-11_0_4_load_87 | 23 | 0.0015661 | 0.00039249 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1107-11_0_4_load_88 | 24 | 0.00062485 | 0.0001566 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1107-11_0_4_load_52 | 25 | 0.0052829 | 0.001324 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1107-11_0_4_load_55 | 28 | 0.0077506 | 0.0019425 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1107-11_0_4_load_56 | 29 | 0.0042671 | 0.0010694 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1107-11_0_4_load_100 | 30 | 0.0070448 | 0.0017656 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1107-11_0_4_load_60 | 32 | 0.0072677 | 0.0018215 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1107-11_0_4_load_61 | 33 | 0.0072356 | 0.0018134 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1107-11_0_4_load_64 | 35 | 0.0082093 | 0.0020574 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1107-11_0_4_load_65 | 36 | 0.028234 | 0.0070761 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1107-11_0_4_load_70 | 38 | 0.0051195 | 0.0012831 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1107-11_0_4_load_68 | 39 | 0.0032973 | 0.00082638 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1107-11_0_4_load_67 | 40 | 0.0026172 | 0.00065592 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1107-11_0_4_load_107 | 41 | 0.012871 | 0.0032257 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1107-11_0_4_load_108 | 42 | 0.0065947 | 0.0016528 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1107-11_0_4_load_71 | 43 | 0.0049407 | 0.0012383 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1107-11_0_4_load_72 | 44 | 0.001691 | 0.0004238 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1107-11_0_4_load_74 | 46 | 0.0028746 | 0.00072045 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1107-11_0_4_load_75 | 47 | 0.0026224 | 0.00065724 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1107-11_0_4_load_76 | 48 | 0.0020818 | 0.00052175 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1107-11_0_4_load_79 | 49 | 0.0012502 | 0.00031333 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1107-11_0_4_load_80 | 50 | 0.016174 | 0.0040535 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1107-11_0_4_load_99 | 51 | 0.0012582 | 0.00031533 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1107-11_0_4_load_77 | 54 | 0.002539 | 0.00063634 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1107-11_0_4_load_103 | 55 | 0.0079916 | 0.0020029 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1107-11_0_4_load_97 | 56 | 0.0052865 | 0.0013249 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1107-11_0_4_load_104 | 57 | 0.0027854 | 0.00069808 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1107-11_0_4_load_85 | 58 | 0.0011304 | 0.00028331 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1107-11_0_4_load_98 | 59 | 0.0056656 | 0.0014199 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1107-11_0_4_load_89 | 60 | 0.0011537 | 0.00028914 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1107-11_0_4_load_90 | 61 | 0.0015648 | 0.00039217 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1107-11_0_4_load_91 | 62 | 0.0020194 | 0.00050612 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1107-11_0_4_load_92 | 63 | 0.0025356 | 0.00063548 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1107-11_0_4_load_102 | 64 | 0.0021128 | 0.00052952 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1107-11_0_4_load_110 | 65 | 0.0027481 | 0.00068875 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1107-11_0_4_load_93 | 66 | 0.0032352 | 0.00081083 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1107-11_0_4_load_94 | 67 | 0.0045027 | 0.0011285 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1107-11_0_4_load_95 | 68 | 0.002472 | 0.00061955 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1107-11_0_4_load_96 | 69 | 0.0010384 | 0.00026025 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1107-11_0_4_load_112 | 71 | 0.0016426 | 0.00041169 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1107-11_0_4_load_105 | 72 | 0.0025156 | 0.00063047 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1107-11_0_4_load_111 | 73 | 0.0010392 | 0.00026046 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1107-11_0_4_load_109 | 74 | 0.0016956 | 0.00042497 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 70 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1107-11_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1107-11_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.045215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1107-11_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.018405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1107-11_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.022752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1107-11_0_4_line_4 | NAYY 4x150 SE | 3 | 7 | 0.10027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1107-11_0_4_line_5 | NAYY 4x150 SE | 4 | 8 | 0.0075865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1107-11_0_4_line_6 | NAYY 4x150 SE | 5 | 6 | 0.04308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1107-11_0_4_line_7 | NAYY 4x150 SE | 6 | 23 | 0.030317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1107-11_0_4_line_8 | NAYY 4x150 SE | 6 | 12 | 0.056133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1107-11_0_4_line_9 | NAYY 4x150 SE | 7 | 9 | 0.036235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1107-11_0_4_line_10 | NAYY 4x150 SE | 8 | 10 | 0.075856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1107-11_0_4_line_11 | NAYY 4x150 SE | 9 | 11 | 0.0032157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1107-11_0_4_line_12 | NAYY 4x150 SE | 10 | 17 | 0.061081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1107-11_0_4_line_13 | NAYY 4x150 SE | 10 | 18 | 0.074074 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1107-11_0_4_line_14 | NAYY 4x150 SE | 11 | 15 | 0.036306 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1107-11_0_4_line_15 | NAYY 4x150 SE | 12 | 13 | 0.1822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1107-11_0_4_line_16 | NAYY 4x150 SE | 12 | 14 | 0.082038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1107-11_0_4_line_17 | NAYY 4x150 SE | 13 | 59 | 0.13505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1107-11_0_4_line_18 | NAYY 4x150 SE | 13 | 51 | 0.049725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1107-11_0_4_line_19 | NAYY 4x150 SE | 14 | 16 | 0.017736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1107-11_0_4_line_20 | NAYY 4x150 SE | 14 | 15 | 0.16302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1107-11_0_4_line_21 | NAYY 4x150 SE | 16 | 58 | 0.028994 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1107-11_0_4_line_22 | NAYY 4x150 SE | 17 | 19 | 0.017202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1107-11_0_4_line_23 | NAYY 4x150 SE | 19 | 20 | 0.11518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1107-11_0_4_line_24 | NAYY 4x150 SE | 19 | 21 | 0.0074156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1107-11_0_4_line_25 | NAYY 4x150 SE | 20 | 22 | 0.020613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1107-11_0_4_line_26 | NAYY 4x150 SE | 23 | 24 | 0.0042578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1107-11_0_4_line_27 | NAYY 4x150 SE | 25 | 26 | 0.01317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1107-11_0_4_line_28 | NAYY 4x150 SE | 25 | 27 | 0.019929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1107-11_0_4_line_29 | NAYY 4x150 SE | 26 | 28 | 0.02061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1107-11_0_4_line_30 | NAYY 4x150 SE | 27 | 29 | 0.039925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1107-11_0_4_line_31 | NAYY 4x150 SE | 28 | 30 | 0.0038478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1107-11_0_4_line_32 | NAYY 4x150 SE | 30 | 31 | 0.0033251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1107-11_0_4_line_33 | NAYY 4x150 SE | 31 | 56 | 0.022067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
34 | LV_1107-11_0_4_line_34 | NAYY 4x150 SE | 31 | 53 | 0.023558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_1107-11_0_4_line_35 | NAYY 4x150 SE | 32 | 33 | 0.0090804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1107-11_0_4_line_36 | NAYY 4x150 SE | 32 | 34 | 0.019523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1107-11_0_4_line_37 | NAYY 4x150 SE | 34 | 35 | 0.0093131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1107-11_0_4_line_38 | NAYY 4x150 SE | 34 | 36 | 0.028472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1107-11_0_4_line_39 | NAYY 4x150 SE | 36 | 37 | 0.018053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1107-11_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.02181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1107-11_0_4_line_41 | NAYY 4x150 SE | 37 | 39 | 0.013956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1107-11_0_4_line_42 | NAYY 4x150 SE | 38 | 41 | 0.02562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1107-11_0_4_line_43 | NAYY 4x150 SE | 39 | 40 | 0.009875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1107-11_0_4_line_44 | NAYY 4x150 SE | 41 | 42 | 0.0077812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1107-11_0_4_line_45 | NAYY 4x150 SE | 42 | 74 | 0.022959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1107-11_0_4_line_46 | NAYY 4x150 SE | 43 | 44 | 0.0071996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1107-11_0_4_line_47 | NAYY 4x150 SE | 43 | 45 | 0.0157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1107-11_0_4_line_48 | NAYY 4x150 SE | 44 | 46 | 0.013326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1107-11_0_4_line_49 | NAYY 4x150 SE | 45 | 47 | 0.013111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_1107-11_0_4_line_50 | NAYY 4x150 SE | 45 | 48 | 0.01698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
51 | LV_1107-11_0_4_line_51 | NAYY 4x150 SE | 46 | 49 | 0.037288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1107-11_0_4_line_52 | NAYY 4x150 SE | 47 | 50 | 0.013757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1107-11_0_4_line_53 | NAYY 4x150 SE | 48 | 51 | 0.087498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1107-11_0_4_line_54 | NAYY 4x150 SE | 49 | 52 | 0.072195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1107-11_0_4_line_55 | NAYY 4x150 SE | 50 | 53 | 0.0098886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_1107-11_0_4_line_56 | NAYY 4x150 SE | 52 | 54 | 0.024417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1107-11_0_4_line_57 | NAYY 4x150 SE | 53 | 55 | 0.041442 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1107-11_0_4_line_58 | NAYY 4x150 SE | 55 | 57 | 0.018922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1107-11_0_4_line_59 | NAYY 4x150 SE | 56 | 68 | 0.014349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
60 | LV_1107-11_0_4_line_60 | NAYY 4x150 SE | 57 | 72 | 0.0082968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1107-11_0_4_line_61 | NAYY 4x150 SE | 60 | 61 | 0.057162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1107-11_0_4_line_62 | NAYY 4x150 SE | 60 | 62 | 0.0079684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1107-11_0_4_line_63 | NAYY 4x150 SE | 61 | 63 | 0.17523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1107-11_0_4_line_64 | NAYY 4x150 SE | 63 | 64 | 0.029893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1107-11_0_4_line_65 | NAYY 4x150 SE | 64 | 65 | 0.074034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1107-11_0_4_line_66 | NAYY 4x150 SE | 65 | 70 | 0.032277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1107-11_0_4_line_67 | NAYY 4x150 SE | 66 | 67 | 0.027257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
68 | LV_1107-11_0_4_line_68 | NAYY 4x150 SE | 66 | 68 | 0.020137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
69 | LV_1107-11_0_4_line_69 | NAYY 4x150 SE | 67 | 69 | 0.086922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
70 | LV_1107-11_0_4_line_70 | NAYY 4x150 SE | 69 | 70 | 0.012551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
71 | LV_1107-11_0_4_line_71 | NAYY 4x150 SE | 70 | 71 | 0.037885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1107-11_0_4_line_72 | NAYY 4x150 SE | 71 | 73 | 0.021368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1107-11_0_4_line_73 | NAYY 4x150 SE | 73 | 74 | 0.0064235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1107-11_0_4_trafo_106 | 0.25 MVA 20/0.4 kV | 75 | 70 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27
0 | 2647407.4221 | 1212039.7566 | 2647409.58 | 1212047.8234 | 2647417.3387 | 1212058.9094
1 | 2647407.4221 | 1212039.7566 | 2647406.09 | 1212034.7769 | 2647407.8217 | 1212022.4167 | 2647418.4179 | 1212004.5904 | 2647421.3996 | 1211998.4327
2 | 2647417.3387 | 1212058.9094 | 2647427.8921 | 1212073.9886
3 | 2647405.4695 | 1211989.512 | 2647415.2726 | 1211989.2675 | 2647421.1247 | 1211991.9156 | 2647421.3996 | 1211998.4327
4 | 2647484.7442 | 1212156.4242 | 2647477.0482 | 1212147.9964 | 2647441.9807 | 1212094.1192 | 2647427.8921 | 1212073.9886
5 | 2647405.4695 | 1211989.512 | 2647401.1045 | 1211983.3071
6 | 2647640.037 | 1211998.9073 | 2647636.5242 | 1211997.3339 | 2647622.1518 | 1211975.1172 | 2647612.4715 | 1211966.7874
7 | 2647640.037 | 1211998.9073 | 2647639.9492 | 1211994.6819 | 2647639.3204 | 1211987.795 | 2647637.1271 | 1211976.0595 | 2647637.3231 | 1211968.8252
8 | 2647648.2586 | 1212053.027 | 2647644.5686 | 1212045.104 | 2647639.4306 | 1212029.1758 | 2647638.0998 | 1212023.6175 | 2647637.4963 | 1212018.3095 | 2647637.7241 | 1212013.5752 | 2647638.3065 | 1212008.1989 | 2647640.037 | 1211998.9073
9 | 2647484.7442 | 1212156.4242 | 2647485.1375 | 1212156.8549 | 2647494.8807 | 1212164.0922 | 2647516.5658 | 1212173.186
10 | 2647329.3876 | 1211970.0746 | 2647339.7168 | 1211978.2169 | 2647347.5483 | 1211980.3581 | 2647356.7977 | 1211979.0418 | 2647368.8291 | 1211976.6136 | 2647384.2753 | 1211979.4934 | 2647401.1045 | 1211983.3071
11 | 2647516.5658 | 1212173.186 | 2647519.5312 | 1212174.4296
12 | 2647329.3876 | 1211970.0746 | 2647363.5572 | 1211942.0292 | 2647378.1076 | 1211933.4808
13 | 2647329.3876 | 1211970.0746 | 2647274.3185 | 1212011.3181 | 2647269.7022 | 1212013.8654
14 | 2647519.5312 | 1212174.4296 | 2647553.0121 | 1212188.47
15 | 2647811.9523 | 1212029.1997 | 2647804.1071 | 1212024.0449 | 2647799.5454 | 1212021.5847 | 2647796.3342 | 1212020.3027 | 2647793.042 | 1212019.6537 | 2647789.685 | 1212019.5045 | 2647785.8574 | 1212020.241 | 2647780.6239 | 1212021.9668 | 2647766.7412 | 1212027.8702 | 2647761.8888 | 1212029.4434 | 2647757.9374 | 1212030.468 | 2647753.2225 | 1212030.9972 | 2647738.1592 | 1212031.5771 | 2647733.2848 | 1212032.1051 | 2647729.7224 | 1212032.9327 | 2647726.1559 | 1212034.2827 | 2647721.7387 | 1212036.5487 | 2647706.0812 | 1212047.7746 | 2647694.813 | 1212055.4669 | 2647685.5598 | 1212061.074 | 2647679.9877 | 1212063.3531 | 2647675.6995 | 1212064.6863 | 2647670.2137 | 1212065.6653 | 2647664.0453 | 1212065.5493 | 2647660.3047 | 1212064.919 | 2647656.2948 | 1212062.808 | 2647652.8249 | 1212059.6785 | 2647648.2586 | 1212053.027
16 | 2647648.2586 | 1212053.027 | 2647633.8098 | 1212067.0421 | 2647629.2593 | 1212075.5442 | 2647631.0383 | 1212082.0622 | 2647638.0018 | 1212085.3641 | 2647661.0402 | 1212084.1251 | 2647675.3824 | 1212080.7627
17 | 2647811.9523 | 1212029.1997 | 2647811.9032 | 1212037.2151 | 2647812.5718 | 1212041.0116 | 2647814.4018 | 1212048.7308 | 2647816.8486 | 1212054.3759 | 2647821.5397 | 1212062.4849 | 2647824.1445 | 1212068.3315 | 2647826.2286 | 1212074.663 | 2647828.6704 | 1212080.9307 | 2647841.1954 | 1212104.1225 | 2647842.7746 | 1212108.0486 | 2647843.4229 | 1212111.5225 | 2647843.8138 | 1212114.8832 | 2647844.0433 | 1212119.4322 | 2647842.6683 | 1212130.7723 | 2647835.5974 | 1212156.2626
18 | 2647811.9523 | 1212029.1997 | 2647834.3255 | 1212043.6763 | 2647841.2003 | 1212050.4576 | 2647849.1799 | 1212061.2471
19 | 2647675.3824 | 1212080.7627 | 2647677.7788 | 1212080.2009 | 2647685.1129 | 1212080.8599 | 2647692.6035 | 1212083.403
20 | 2647675.3824 | 1212080.7627 | 2647553.0121 | 1212188.47
21 | 2647720.0585 | 1212092.7239 | 2647692.6035 | 1212083.403
22 | 2647389.5627 | 1211921.2345 | 2647386.0771 | 1211927.6995 | 2647379.8013 | 1211932.4858 | 2647378.1076 | 1211933.4808
23 | 2647389.5627 | 1211921.2345 | 2647387.0987 | 1211914.8222 | 2647382.0877 | 1211906.7221 | 2647379.8604 | 1211896.3428 | 2647380.7711 | 1211868.7227 | 2647386.0915 | 1211838.8362 | 2647389.0162 | 1211818.8255 | 2647387.0645 | 1211809.0622
24 | 2647389.5627 | 1211921.2345 | 2647393.9788 | 1211915.2771
25 | 2647383.0239 | 1211788.8492 | 2647387.0645 | 1211809.0622
26 | 2647637.3231 | 1211968.8252 | 2647637.4385 | 1211964.569
27 | 2648009.9353 | 1212089.491 | 2648012.6491 | 1212094.0377 | 2648015.204 | 1212097.5492 | 2648017.5928 | 1212100.1518
28 | 2648033.451 | 1212112.0268 | 2648028.1038 | 1212109.0042 | 2648022.7554 | 1212105.1922 | 2648018.7816 | 1212101.4469 | 2648017.5928 | 1212100.1518
29 | 2648009.9353 | 1212089.491 | 2648000.096 | 1212090.4791 | 2647989.4641 | 1212089.0946
30 | 2648033.451 | 1212112.0268 | 2648029.8545 | 1212118.0458 | 2648026.5797 | 1212122.7889 | 2648011.4901 | 1212139.8665 | 2648010.1585 | 1212142.0015 | 2648009.8628 | 1212143.8224
31 | 2647985.6486 | 1212088.5978 | 2647989.4641 | 1212089.0946
32 | 2647982.3512 | 1212088.1684 | 2647985.6486 | 1212088.5978
33 | 2647982.3512 | 1212088.1684 | 2647973.6981 | 1212084.3188 | 2647963.2235 | 1212077.323
34 | 2647960.4648 | 1212096.3751 | 2647969.9441 | 1212091.0259 | 2647982.3512 | 1212088.1684
35 | 2647847.8798 | 1211772.226 | 2647851.4649 | 1211771.0087 | 2647854.663 | 1211769.2 | 2647855.8028 | 1211768.0486
36 | 2647829.3932 | 1211778.5029 | 2647847.8798 | 1211772.226
37 | 2647829.3932 | 1211778.5029 | 2647826.3497 | 1211769.7012
38 | 2647829.3932 | 1211778.5029 | 2647838.3599 | 1211805.5259
39 | 2647845.6716 | 1211821.6588 | 2647844.1385 | 1211820.5013 | 2647842.4799 | 1211817.9421 | 2647838.3599 | 1211805.5259
40 | 2647845.6716 | 1211821.6588 | 2647843.9333 | 1211827.1481 | 2647843.3273 | 1211843.1886
41 | 2647845.6716 | 1211821.6588 | 2647847.2406 | 1211822.1383 | 2647859.4939 | 1211823.3707
42 | 2647842.36 | 1211868.7899 | 2647843.3273 | 1211843.1886
43 | 2647869.2659 | 1211824.7337 | 2647864.7778 | 1211823.9021 | 2647859.4939 | 1211823.3707
44 | 2647842.36 | 1211868.7899 | 2647842.0663 | 1211876.5656
45 | 2647842.5267 | 1211899.4784 | 2647841.6184 | 1211888.4211 | 2647842.0663 | 1211876.5656
46 | 2647934.7041 | 1212133.7015 | 2647938.3455 | 1212139.9123
47 | 2647931.8269 | 1212119.3475 | 2647930.3355 | 1212126.2507 | 2647934.7041 | 1212133.7015
48 | 2647943.6215 | 1212152.1279 | 2647939.4718 | 1212141.8332 | 2647938.3455 | 1212139.9123
49 | 2647931.8269 | 1212119.3475 | 2647942.3675 | 1212111.55
50 | 2647931.8269 | 1212119.3475 | 2647927.1588 | 1212119.7436 | 2647915.6218 | 1212115.4926
51 | 2647943.6215 | 1212152.1279 | 2647948.3064 | 1212163.7505 | 2647955.3543 | 1212171.6339 | 2647966.4572 | 1212180.4582
52 | 2647942.3675 | 1212111.55 | 2647949.727 | 1212106.1057 | 2647953.1373 | 1212103.0153
53 | 2647915.6218 | 1212115.4926 | 2647901.8349 | 1212110.4126 | 2647896.0221 | 1212107.6421 | 2647886.2343 | 1212099.3809 | 2647871.1895 | 1212087.2531 | 2647864.1266 | 1212081.204 | 2647851.4899 | 1212064.3705 | 2647849.1799 | 1212061.2471
54 | 2647950.5205 | 1212194.5419 | 2647942.6231 | 1212190.2538 | 2647934.4366 | 1212183.1838 | 2647931.7999 | 1212174.7132 | 2647933.9349 | 1212173.7632 | 2647935.2279 | 1212173.5845 | 2647950.1877 | 1212179.2303 | 2647964.2319 | 1212183.4678 | 2647967.5789 | 1212183.9061 | 2647968.7499 | 1212183.7821 | 2647969.158 | 1212183.1072 | 2647968.9205 | 1212182.416 | 2647966.4572 | 1212180.4582
55 | 2647960.4648 | 1212096.3751 | 2647953.1373 | 1212103.0153
56 | 2647950.5205 | 1212194.5419 | 2647938.2754 | 1212215.6671
57 | 2647960.4648 | 1212096.3751 | 2647923.5809 | 1212077.4801
58 | 2647923.5809 | 1212077.4801 | 2647912.0692 | 1212071.5829 | 2647907.3116 | 1212067.947
59 | 2647963.2235 | 1212077.323 | 2647951.2915 | 1212069.3538
60 | 2647907.3116 | 1212067.947 | 2647900.7196 | 1212062.909
61 | 2647761.0923 | 1211922.6506 | 2647764.596 | 1211900.089 | 2647764.8708 | 1211865.7599
62 | 2647759.8696 | 1211930.5246 | 2647761.0923 | 1211922.6506
63 | 2647764.8708 | 1211865.7599 | 2647765.1116 | 1211835.6885 | 2647767.2175 | 1211795.6818 | 2647768.9827 | 1211779.2418 | 2647771.2501 | 1211776.0025 | 2647774.2966 | 1211776.038 | 2647776.5277 | 1211778.2794 | 2647781.4798 | 1211821.1888 | 2647788.8096 | 1211855.6202
64 | 2647798.3308 | 1211883.8893 | 2647790.3181 | 1211862.7062 | 2647788.8096 | 1211855.6202
65 | 2647798.3308 | 1211883.8893 | 2647808.279 | 1211910.189 | 2647821.7926 | 1211934.267 | 2647829.5286 | 1211950.8572
66 | 2647855.4268 | 1211963.8206 | 2647843.7196 | 1211963.6934 | 2647838.8334 | 1211962.8426 | 2647833.0117 | 1211958.3266 | 2647829.5286 | 1211950.8572
67 | 2647934.5461 | 1212058.1699 | 2647928.4082 | 1212054.0705 | 2647912.3566 | 1212042.3487
68 | 2647934.5461 | 1212058.1699 | 2647951.2915 | 1212069.3538
69 | 2647912.3566 | 1212042.3487 | 2647902.4698 | 1212035.1289 | 2647887.6144 | 1212022.102 | 2647872.6329 | 1212003.9489 | 2647862.5454 | 1211986.6134 | 2647859.1684 | 1211975.8008
70 | 2647855.4268 | 1211963.8206 | 2647859.1684 | 1211975.8008
71 | 2647855.4268 | 1211963.8206 | 2647847.4539 | 1211926.7842
72 | 2647843.0527 | 1211905.8803 | 2647843.1136 | 1211906.6216 | 2647847.4539 | 1211926.7842
73 | 2647843.0527 | 1211905.8803 | 2647842.5267 | 1211899.4784

## bus_geodata
| x | y | coords
0 | 2647407.4221 | 1212039.7566
1 | 2647417.3387 | 1212058.9094
2 | 2647421.3996 | 1211998.4327
3 | 2647427.8921 | 1212073.9886
4 | 2647405.4695 | 1211989.512
5 | 2647612.4715 | 1211966.7874
6 | 2647640.037 | 1211998.9073
7 | 2647484.7442 | 1212156.4242
8 | 2647401.1045 | 1211983.3071
9 | 2647516.5658 | 1212173.186
10 | 2647329.3876 | 1211970.0746
11 | 2647519.5312 | 1212174.4296
12 | 2647648.2586 | 1212053.027
13 | 2647811.9523 | 1212029.1997
14 | 2647675.3824 | 1212080.7627
15 | 2647553.0121 | 1212188.47
16 | 2647692.6035 | 1212083.403
17 | 2647378.1076 | 1211933.4808
18 | 2647269.7022 | 1212013.8654
19 | 2647389.5627 | 1211921.2345
20 | 2647387.0645 | 1211809.0622
21 | 2647393.9788 | 1211915.2771
22 | 2647383.0239 | 1211788.8492
23 | 2647637.3231 | 1211968.8252
24 | 2647637.4385 | 1211964.569
25 | 2648017.5928 | 1212100.1518
26 | 2648009.9353 | 1212089.491
27 | 2648033.451 | 1212112.0268
28 | 2647989.4641 | 1212089.0946
29 | 2648009.8628 | 1212143.8224
30 | 2647985.6486 | 1212088.5978
31 | 2647982.3512 | 1212088.1684
32 | 2647847.8798 | 1211772.226
33 | 2647855.8028 | 1211768.0486
34 | 2647829.3932 | 1211778.5029
35 | 2647826.3497 | 1211769.7012
36 | 2647838.3599 | 1211805.5259
37 | 2647845.6716 | 1211821.6588
38 | 2647843.3273 | 1211843.1886
39 | 2647859.4939 | 1211823.3707
40 | 2647869.2659 | 1211824.7337
41 | 2647842.36 | 1211868.7899
42 | 2647842.0663 | 1211876.5656
43 | 2647934.7041 | 1212133.7015
44 | 2647938.3455 | 1212139.9123
45 | 2647931.8269 | 1212119.3475
46 | 2647943.6215 | 1212152.1279
47 | 2647942.3675 | 1212111.55
48 | 2647915.6218 | 1212115.4926
49 | 2647966.4572 | 1212180.4582
50 | 2647953.1373 | 1212103.0153
51 | 2647849.1799 | 1212061.2471
52 | 2647950.5205 | 1212194.5419
53 | 2647960.4648 | 1212096.3751
54 | 2647938.2754 | 1212215.6671
55 | 2647923.5809 | 1212077.4801
56 | 2647963.2235 | 1212077.323
57 | 2647907.3116 | 1212067.947
58 | 2647720.0585 | 1212092.7239
59 | 2647835.5974 | 1212156.2626
60 | 2647761.0923 | 1211922.6506
61 | 2647764.8708 | 1211865.7599
62 | 2647759.8696 | 1211930.5246
63 | 2647788.8096 | 1211855.6202
64 | 2647798.3308 | 1211883.8893
65 | 2647829.5286 | 1211950.8572
66 | 2647934.5461 | 1212058.1699
67 | 2647912.3566 | 1212042.3487
68 | 2647951.2915 | 1212069.3538
69 | 2647859.1684 | 1211975.8008
70 | 2647855.4268 | 1211963.8206
71 | 2647847.4539 | 1211926.7842
72 | 2647900.7196 | 1212062.909
73 | 2647843.0527 | 1211905.8803
74 | 2647842.5267 | 1211899.4784
75 | 2647845.6716 | 1211821.6588

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97225 | -0.19641 | 0.0013929 | 0.00034909
1 | 0.97251 | -0.1945 | 0.00055565 | 0.00013926
2 | 0.97179 | -0.19971 | 0.0015067 | 0.00037762
3 | 0.97275 | -0.19278 | 0.00052895 | 0.00013257
4 | 0.97161 | -0.201 | 0 | 0
5 | 0.97731 | -0.15991 | 0.00075978 | 0.00019042
6 | 0.97736 | -0.15957 | 0 | 0
7 | 0.97412 | -0.18286 | 0.00034775 | 8.7153e-05
8 | 0.97155 | -0.20144 | 0.00041996 | 0.00010525
9 | 0.97464 | -0.17915 | 0.00045942 | 0.00011514
10 | 0.971 | -0.20542 | 0 | 0
11 | 0.97469 | -0.17881 | 0.0014413 | 0.00036122
12 | 0.9776 | -0.15783 | 0 | 0
13 | 0.98011 | -0.13982 | 0 | 0
14 | 0.97665 | -0.16469 | 0.00028364 | 7.1087e-05
15 | 0.97499 | -0.17659 | 0.0022644 | 0.00056751
16 | 0.9766 | -0.16501 | 0.00061711 | 0.00015466
17 | 0.97062 | -0.20817 | 0.00039284 | 9.8455e-05
18 | 0.97093 | -0.20597 | 0.00069777 | 0.00017488
19 | 0.97053 | -0.20887 | 0 | 0
20 | 0.97019 | -0.2113 | 0.00037994 | 9.5222e-05
21 | 0.97051 | -0.20902 | 0.0018622 | 0.0004667
22 | 0.97014 | -0.21165 | 0.0016006 | 0.00040115
23 | 0.97726 | -0.16026 | 0.0015661 | 0.00039249
24 | 0.97726 | -0.16029 | 0.00062485 | 0.0001566
25 | 0.98483 | -0.10619 | 0.0052829 | 0.001324
26 | 0.98501 | -0.1049 | 0 | 0
27 | 0.98471 | -0.10707 | 0 | 0
28 | 0.9853 | -0.10287 | 0.0077506 | 0.0019425
29 | 0.98446 | -0.10882 | 0.0042671 | 0.0010694
30 | 0.9854 | -0.10219 | 0.0070448 | 0.0017656
31 | 0.98551 | -0.10136 | 0 | 0
32 | 0.98158 | -0.1293 | 0.0072677 | 0.0018215
33 | 0.98148 | -0.12998 | 0.0072356 | 0.0018134
34 | 0.98199 | -0.12637 | 0 | 0
35 | 0.98188 | -0.12716 | 0.0082093 | 0.0020574
36 | 0.98293 | -0.11968 | 0.028234 | 0.0070761
37 | 0.98426 | -0.11019 | 0 | 0
38 | 0.98606 | -0.097435 | 0.0051195 | 0.0012831
39 | 0.98414 | -0.11104 | 0.0032973 | 0.00082638
40 | 0.9841 | -0.11131 | 0.0026172 | 0.00065592
41 | 0.98836 | -0.081171 | 0.012871 | 0.0032257
42 | 0.98921 | -0.075224 | 0.0065947 | 0.0016528
43 | 0.98269 | -0.1214 | 0.0049407 | 0.0012383
44 | 0.98261 | -0.12203 | 0.001691 | 0.0004238
45 | 0.983 | -0.11924 | 0 | 0
46 | 0.98248 | -0.12295 | 0.0028746 | 0.00072045
47 | 0.98339 | -0.11645 | 0.0026224 | 0.00065724
48 | 0.98265 | -0.1217 | 0.0020818 | 0.00052175
49 | 0.98227 | -0.12441 | 0.0012502 | 0.00031333
50 | 0.98383 | -0.11332 | 0.016174 | 0.0040535
51 | 0.981 | -0.13346 | 0.0012582 | 0.00031533
52 | 0.98201 | -0.12631 | 0 | 0
53 | 0.98426 | -0.11026 | 0 | 0
54 | 0.98192 | -0.12695 | 0.002539 | 0.00063634
55 | 0.98346 | -0.11594 | 0.0079916 | 0.0020029
56 | 0.98708 | -0.090284 | 0.0052865 | 0.0013249
57 | 0.98331 | -0.11698 | 0.0027854 | 0.00069808
58 | 0.97656 | -0.16536 | 0.0011304 | 0.00028331
59 | 0.979 | -0.14779 | 0.0056656 | 0.0014199
60 | 0.99669 | -0.023256 | 0.0011537 | 0.00028914
61 | 0.99695 | -0.021432 | 0.0015648 | 0.00039217
62 | 0.99667 | -0.023418 | 0.0020194 | 0.00050612
63 | 0.99814 | -0.01308 | 0.0025356 | 0.00063548
64 | 0.99845 | -0.010895 | 0.0021128 | 0.00052952
65 | 0.99944 | -0.0039225 | 0.0027481 | 0.00068875
66 | 0.98969 | -0.071866 | 0.0032352 | 0.00081083
67 | 0.99183 | -0.056787 | 0.0045027 | 0.0011285
68 | 0.98815 | -0.082715 | 0.002472 | 0.00061955
69 | 0.99896 | -0.0071714 | 0.0010384 | 0.00026025
70 | 1 | 0 | -0.21612 | -0.054356
71 | 0.99529 | -0.032612 | 0.0016426 | 0.00041169
72 | 0.98328 | -0.11719 | 0.0025156 | 0.00063047
73 | 0.99269 | -0.050786 | 0.0010392 | 0.00026046
74 | 0.99191 | -0.056201 | 0.0016956 | 0.00042497
75 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0082628 | -0.0020667 | 0.008265 | 0.0020672 | 2.1831e-06 | 5.6823e-07 | 0.012645 | 0.012645 | 0.012645 | 0.97225 | -0.19641 | 0.97251 | -0.1945 | 4.6832
1 | 0.0068699 | 0.0017176 | -0.0068668 | -0.0017169 | 3.1183e-06 | 6.3888e-07 | 0.010513 | 0.010513 | 0.010513 | 0.97225 | -0.19641 | 0.97179 | -0.19971 | 3.8937
2 | -0.0088206 | -0.0022065 | 0.0088227 | 0.0022071 | 2.0915e-06 | 5.7599e-07 | 0.013495 | 0.013495 | 0.013495 | 0.97251 | -0.1945 | 0.97275 | -0.19278 | 4.9981
3 | 0.0053601 | 0.0013393 | -0.0053591 | -0.0013392 | 9.5602e-07 | 8.5861e-08 | 0.0082059 | 0.008206 | 0.008206 | 0.97179 | -0.19971 | 0.97161 | -0.201 | 3.0393
4 | -0.0093517 | -0.0023396 | 0.0093645 | 0.0023433 | 1.2801e-05 | 3.6769e-06 | 0.014304 | 0.014303 | 0.014304 | 0.97275 | -0.19278 | 0.97412 | -0.18286 | 5.2977
5 | 0.0053591 | 0.0013392 | -0.0053588 | -0.0013392 | 3.1878e-07 | 2.8655e-08 | 0.008206 | 0.008206 | 0.008206 | 0.97161 | -0.201 | 0.97155 | -0.20144 | 3.0393
6 | -0.00075978 | -0.00019042 | 0.00075982 | 0.00018989 | 3.5968e-08 | -5.2602e-07 | 0.0011568 | 0.0011566 | 0.0011568 | 0.97731 | -0.15991 | 0.97736 | -0.15957 | 0.42845
7 | 0.0021911 | 0.00054874 | -0.0021909 | -0.00054904 | 2.1052e-07 | -2.9893e-07 | 0.0033358 | 0.0033359 | 0.0033359 | 0.97736 | -0.15957 | 0.97726 | -0.16026 | 1.2355
8 | -0.0029509 | -0.00073863 | 0.0029516 | 0.0007382 | 7.0687e-07 | -4.3176e-07 | 0.0044924 | 0.0044922 | 0.0044924 | 0.97736 | -0.15957 | 0.9776 | -0.15783 | 1.6639
9 | -0.0097122 | -0.0024305 | 0.0097172 | 0.0024319 | 4.9757e-06 | 1.4624e-06 | 0.014835 | 0.014834 | 0.014835 | 0.97412 | -0.18286 | 0.97464 | -0.17915 | 5.4943
10 | 0.0049388 | 0.0012339 | -0.0049361 | -0.0012338 | 2.7075e-06 | 1.025e-07 | 0.0075628 | 0.0075632 | 0.0075632 | 0.97155 | -0.20144 | 0.971 | -0.20542 | 2.8012
11 | -0.010177 | -0.0025471 | 0.010177 | 0.0025472 | 4.8431e-07 | 1.462e-07 | 0.015536 | 0.015536 | 0.015536 | 0.97464 | -0.17915 | 0.97469 | -0.17881 | 5.754
12 | 0.0042383 | 0.0010598 | -0.0042367 | -0.00106 | 1.6075e-06 | -1.3698e-07 | 0.0064941 | 0.0064944 | 0.0064944 | 0.971 | -0.20542 | 0.97062 | -0.20817 | 2.4053
13 | 0.00069782 | 0.00017398 | -0.00069777 | -0.00017488 | 5.2842e-08 | -8.9586e-07 | 0.001069 | 0.0010694 | 0.0010694 | 0.971 | -0.20542 | 0.97093 | -0.20597 | 0.39607
14 | -0.011618 | -0.0029084 | 0.011622 | 0.0029089 | 3.5632e-06 | 4.6518e-07 | 0.017736 | 0.017736 | 0.017736 | 0.97469 | -0.17881 | 0.97499 | -0.17659 | 3.2845
15 | -0.018907 | -0.0047316 | 0.018954 | 0.0047451 | 4.707e-05 | 1.3523e-05 | 0.028776 | 0.028775 | 0.028776 | 0.9776 | -0.15783 | 0.98011 | -0.13982 | 5.3289
16 | 0.015956 | 0.0039934 | -0.015941 | -0.0039896 | 1.5095e-05 | 3.7505e-06 | 0.024284 | 0.024285 | 0.024285 | 0.9776 | -0.15783 | 0.97665 | -0.16469 | 4.4972
17 | 0.0056719 | 0.0014206 | -0.0056656 | -0.0014199 | 6.249e-06 | 7.0334e-07 | 0.0086108 | 0.0086114 | 0.0086114 | 0.98011 | -0.13982 | 0.979 | -0.14779 | 3.1894
18 | -0.024626 | -0.0061658 | 0.024648 | 0.0061728 | 2.1683e-05 | 7.0853e-06 | 0.037385 | 0.037385 | 0.037385 | 0.98011 | -0.13982 | 0.981 | -0.13346 | 6.9232
19 | 0.0017477 | 0.00043744 | -0.0017476 | -0.00043763 | 7.8457e-08 | -1.9175e-07 | 0.0026625 | 0.0026626 | 0.0026626 | 0.97665 | -0.16469 | 0.9766 | -0.16501 | 0.98615
20 | 0.013909 | 0.0034811 | -0.013886 | -0.0034764 | 2.284e-05 | 4.7115e-06 | 0.02119 | 0.021192 | 0.021192 | 0.97665 | -0.16469 | 0.97499 | -0.17659 | 3.9244
21 | 0.0011305 | 0.00028297 | -0.0011304 | -0.00028331 | 5.3674e-08 | -3.4213e-07 | 0.0017223 | 0.0017225 | 0.0017225 | 0.9766 | -0.16501 | 0.97656 | -0.16536 | 0.63795
22 | 0.0038438 | 0.00096153 | -0.0038435 | -0.0009616 | 3.7266e-07 | -6.926e-08 | 0.0058921 | 0.0058922 | 0.0058922 | 0.97062 | -0.20817 | 0.97053 | -0.20887 | 2.1823
23 | 0.0019813 | 0.00049497 | -0.0019806 | -0.00049614 | 6.6308e-07 | -1.1678e-06 | 0.0030371 | 0.0030376 | 0.0030376 | 0.97053 | -0.20887 | 0.97019 | -0.2113 | 1.125
24 | 0.0018622 | 0.00046663 | -0.0018622 | -0.0004667 | 3.7721e-08 | -7.7128e-08 | 0.0028551 | 0.0028551 | 0.0028551 | 0.97053 | -0.20887 | 0.97051 | -0.20902 | 1.0575
25 | 0.0016007 | 0.00040092 | -0.0016006 | -0.00040115 | 7.7519e-08 | -2.2472e-07 | 0.0024549 | 0.002455 | 0.002455 | 0.97019 | -0.2113 | 0.97014 | -0.21165 | 0.90926
26 | 0.00062485 | 0.00015655 | -0.00062485 | -0.0001566 | 2.4049e-09 | -5.2423e-08 | 0.0009514 | 0.00095142 | 0.00095142 | 0.97726 | -0.16026 | 0.97726 | -0.16029 | 0.35238
27 | -0.0095516 | -0.0023933 | 0.0095533 | 0.0023938 | 1.7116e-06 | 4.907e-07 | 0.014432 | 0.014432 | 0.014432 | 0.98483 | -0.10619 | 0.98501 | -0.1049 | 5.345
28 | 0.0042686 | 0.0010693 | -0.0042681 | -0.0010693 | 5.1727e-07 | -5.46e-08 | 0.0064494 | 0.0064495 | 0.0064495 | 0.98483 | -0.10619 | 0.98471 | -0.10707 | 2.3887
29 | -0.0095533 | -0.0023938 | 0.009556 | 0.0023946 | 2.6785e-06 | 7.6777e-07 | 0.014432 | 0.014431 | 0.014432 | 0.98501 | -0.1049 | 0.9853 | -0.10287 | 5.345
30 | 0.0042681 | 0.0010693 | -0.0042671 | -0.0010694 | 1.0363e-06 | -1.0918e-07 | 0.0064495 | 0.0064497 | 0.0064497 | 0.98471 | -0.10707 | 0.98446 | -0.10882 | 2.3888
31 | -0.017307 | -0.0043371 | 0.017308 | 0.0043376 | 1.6402e-06 | 5.8183e-07 | 0.026137 | 0.026137 | 0.026137 | 0.9853 | -0.10287 | 0.9854 | -0.10219 | 9.6802
32 | -0.024353 | -0.0061032 | 0.024356 | 0.0061043 | 2.806e-06 | 1.0369e-06 | 0.036775 | 0.036775 | 0.036775 | 0.9854 | -0.10219 | 0.98551 | -0.10136 | 13.6203
33 | -0.09795 | -0.024567 | 0.0981 | 0.024624 | 0.0001506 | 5.736e-05 | 0.1479 | 0.1479 | 0.1479 | 0.98551 | -0.10136 | 0.98708 | -0.090284 | 27.3888
34 | 0.073594 | 0.018462 | -0.073503 | -0.018428 | 9.0765e-05 | 3.431e-05 | 0.11113 | 0.11113 | 0.11113 | 0.98551 | -0.10136 | 0.98426 | -0.11026 | 20.5787
35 | 0.0072363 | 0.0018136 | -0.0072356 | -0.0018134 | 6.8186e-07 | 1.4749e-07 | 0.01097 | 0.01097 | 0.01097 | 0.98158 | -0.1293 | 0.98148 | -0.12998 | 4.0629
36 | -0.014504 | -0.003635 | 0.01451 | 0.003637 | 5.8895e-06 | 2.0183e-06 | 0.021987 | 0.021987 | 0.021987 | 0.98158 | -0.1293 | 0.98199 | -0.12637 | 8.1434
37 | 0.0082102 | 0.0020577 | -0.0082093 | -0.0020574 | 8.9948e-07 | 2.2815e-07 | 0.012441 | 0.012441 | 0.012441 | 0.98199 | -0.12637 | 0.98188 | -0.12716 | 4.6078
38 | -0.02272 | -0.0056947 | 0.022741 | 0.0057025 | 2.1058e-05 | 7.7389e-06 | 0.034428 | 0.034428 | 0.034428 | 0.98199 | -0.12637 | 0.98293 | -0.11968 | 12.7512
39 | -0.050975 | -0.012779 | 0.051042 | 0.012804 | 6.7085e-05 | 2.5573e-05 | 0.07717 | 0.07717 | 0.07717 | 0.98293 | -0.11968 | 0.98426 | -0.11019 | 28.5817
40 | -0.056957 | -0.014286 | 0.057058 | 0.014325 | 0.00010092 | 3.8538e-05 | 0.086113 | 0.086113 | 0.086113 | 0.98426 | -0.11019 | 0.98606 | -0.097435 | 31.8937
41 | 0.0059153 | 0.0014823 | -0.0059146 | -0.0014822 | 6.9643e-07 | 9.0508e-08 | 0.0089427 | 0.0089428 | 0.0089428 | 0.98426 | -0.11019 | 0.98414 | -0.11104 | 3.3121
42 | -0.062178 | -0.015608 | 0.062319 | 0.015662 | 0.00014077 | 5.3816e-05 | 0.093839 | 0.093839 | 0.093839 | 0.98606 | -0.097435 | 0.98836 | -0.081171 | 34.755
43 | 0.0026173 | 0.00065584 | -0.0026172 | -0.00065592 | 9.6497e-08 | -8.8357e-08 | 0.0039573 | 0.0039573 | 0.0039573 | 0.98414 | -0.11104 | 0.9841 | -0.11131 | 1.4657
44 | -0.075189 | -0.018888 | 0.075251 | 0.018911 | 6.2236e-05 | 2.3837e-05 | 0.11322 | 0.11322 | 0.11322 | 0.98836 | -0.081171 | 0.98921 | -0.075224 | 41.9317
45 | -0.081846 | -0.020564 | 0.082063 | 0.020647 | 0.00021722 | 8.325e-05 | 0.12314 | 0.12314 | 0.12314 | 0.98921 | -0.075224 | 0.99191 | -0.056201 | 45.6058
46 | 0.008358 | 0.0020932 | -0.0083573 | -0.002093 | 7.1953e-07 | 1.8554e-07 | 0.012655 | 0.012655 | 0.012655 | 0.98269 | -0.1214 | 0.98261 | -0.12203 | 4.6872
47 | -0.013299 | -0.0033315 | 0.013303 | 0.0033328 | 3.9724e-06 | 1.3289e-06 | 0.020137 | 0.020137 | 0.020137 | 0.98269 | -0.1214 | 0.983 | -0.11924 | 7.4581
48 | 0.0066664 | 0.0016692 | -0.0066655 | -0.0016691 | 8.4739e-07 | 1.5714e-07 | 0.010095 | 0.010095 | 0.010095 | 0.98261 | -0.12203 | 0.98248 | -0.12295 | 3.7388
49 | -0.041342 | -0.01036 | 0.041358 | 0.010366 | 1.6021e-05 | 5.8294e-06 | 0.062582 | 0.062582 | 0.062582 | 0.983 | -0.11924 | 0.98339 | -0.11645 | 11.5892
50 | 0.02804 | 0.0070272 | -0.02803 | -0.0070239 | 9.5444e-06 | 3.2406e-06 | 0.042445 | 0.042445 | 0.042445 | 0.983 | -0.11924 | 0.98265 | -0.1217 | 7.8602
51 | 0.0037909 | 0.00094861 | -0.0037901 | -0.00094879 | 7.669e-07 | -1.7714e-07 | 0.005741 | 0.0057411 | 0.0057411 | 0.98248 | -0.12295 | 0.98227 | -0.12441 | 2.1263
52 | -0.043981 | -0.011023 | 0.044 | 0.01103 | 1.9009e-05 | 6.9619e-06 | 0.06655 | 0.06655 | 0.06655 | 0.98339 | -0.11645 | 0.98383 | -0.11332 | 12.324
53 | 0.025948 | 0.0065022 | -0.025906 | -0.0064882 | 4.2149e-05 | 1.3998e-05 | 0.039293 | 0.039293 | 0.039293 | 0.98265 | -0.1217 | 0.981 | -0.13346 | 7.2766
54 | 0.0025399 | 0.00063546 | -0.0025392 | -0.00063611 | 6.6685e-07 | -6.5714e-07 | 0.0038472 | 0.0038476 | 0.0038476 | 0.98227 | -0.12441 | 0.98201 | -0.12631 | 1.425
55 | -0.060174 | -0.015084 | 0.060199 | 0.015093 | 2.5556e-05 | 9.5779e-06 | 0.091012 | 0.091012 | 0.091012 | 0.98383 | -0.11332 | 0.98426 | -0.11026 | 16.8541
56 | 0.0025392 | 0.00063611 | -0.002539 | -0.00063634 | 2.2556e-07 | -2.2213e-07 | 0.0038476 | 0.0038477 | 0.0038477 | 0.98201 | -0.12631 | 0.98192 | -0.12695 | 1.4251
57 | 0.013304 | 0.0033349 | -0.013293 | -0.0033314 | 1.0461e-05 | 3.4974e-06 | 0.020113 | 0.020113 | 0.020113 | 0.98426 | -0.11026 | 0.98346 | -0.11594 | 7.4494
58 | 0.0053018 | 0.0013285 | -0.005301 | -0.0013285 | 7.598e-07 | 5.2164e-08 | 0.0080218 | 0.0080218 | 0.0080218 | 0.98346 | -0.11594 | 0.98331 | -0.11698 | 2.9711
59 | -0.10339 | -0.025949 | 0.1035 | 0.02599 | 0.00010876 | 4.1465e-05 | 0.15587 | 0.15587 | 0.15587 | 0.98708 | -0.090284 | 0.98815 | -0.082715 | 28.8646
60 | 0.0025157 | 0.00063039 | -0.0025156 | -0.00063047 | 7.5029e-08 | -7.6385e-08 | 0.0038069 | 0.0038069 | 0.0038069 | 0.98331 | -0.11698 | 0.98328 | -0.11719 | 1.41
61 | -0.0031732 | -0.00079518 | 0.003174 | 0.00079474 | 8.0047e-07 | -4.3729e-07 | 0.0047374 | 0.0047371 | 0.0047374 | 0.99669 | -0.023256 | 0.99695 | -0.021432 | 1.7546
62 | 0.0020195 | 0.00050603 | -0.0020194 | -0.00050612 | 4.5199e-08 | -8.6462e-08 | 0.003015 | 0.003015 | 0.003015 | 0.99669 | -0.023256 | 0.99667 | -0.023418 | 1.1167
63 | -0.0047388 | -0.0011869 | 0.0047442 | 0.0011867 | 5.469e-06 | -1.8414e-07 | 0.0070727 | 0.0070719 | 0.0070727 | 0.99695 | -0.021432 | 0.99814 | -0.01308 | 2.6195
64 | -0.0072798 | -0.0018222 | 0.007282 | 0.0018227 | 2.1966e-06 | 4.5402e-07 | 0.010852 | 0.010852 | 0.010852 | 0.99814 | -0.01308 | 0.99845 | -0.010895 | 4.0192
65 | -0.0093948 | -0.0023522 | 0.0094039 | 0.0023547 | 9.0552e-06 | 2.5135e-06 | 0.014001 | 0.014 | 0.014001 | 0.99845 | -0.010895 | 0.99944 | -0.0039225 | 5.1854
66 | -0.012152 | -0.0030434 | 0.012159 | 0.0030456 | 6.5923e-06 | 2.1123e-06 | 0.018092 | 0.018092 | 0.018092 | 0.99944 | -0.0039225 | 1 | 0 | 6.7007
67 | -0.10936 | -0.027482 | 0.10959 | 0.027569 | 0.00023 | 8.776e-05 | 0.16446 | 0.16446 | 0.16446 | 0.98969 | -0.071866 | 0.99183 | -0.056787 | 30.4547
68 | 0.10613 | 0.026671 | -0.10597 | -0.02661 | 0.00016002 | 6.1028e-05 | 0.15959 | 0.15959 | 0.15959 | 0.98969 | -0.071866 | 0.98815 | -0.082715 | 29.5539
69 | -0.1141 | -0.028698 | 0.11489 | 0.029001 | 0.00079495 | 0.00030349 | 0.17121 | 0.17121 | 0.17121 | 0.99183 | -0.056787 | 0.99896 | -0.0071714 | 31.7056
70 | -0.11593 | -0.029262 | 0.11605 | 0.029306 | 0.00011687 | 4.462e-05 | 0.17276 | 0.17276 | 0.17276 | 0.99896 | -0.0071714 | 1 | 0 | 31.9919
71 | 0.087118 | 0.022004 | -0.08672 | -0.021852 | 0.00039763 | 0.00015244 | 0.12969 | 0.12969 | 0.12969 | 1 | 0 | 0.99529 | -0.032612 | 48.0344
72 | 0.085077 | 0.02144 | -0.084862 | -0.021357 | 0.00021586 | 8.2747e-05 | 0.12724 | 0.12724 | 0.12724 | 0.99529 | -0.032612 | 0.99269 | -0.050786 | 47.1248
73 | 0.083822 | 0.021097 | -0.083759 | -0.021072 | 6.3312e-05 | 2.4268e-05 | 0.12568 | 0.12568 | 0.12568 | 0.99269 | -0.050786 | 0.99191 | -0.056201 | 46.5479

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21612 | 0.054356

## res_load
| p_mw | q_mvar
0 | 0.0013929 | 0.00034909
1 | 0.00055565 | 0.00013926
2 | 0.0015067 | 0.00037762
3 | 0.00052895 | 0.00013257
4 | 0.00075978 | 0.00019042
5 | 0.00034775 | 8.7153e-05
6 | 0.00041996 | 0.00010525
7 | 0.00045942 | 0.00011514
8 | 0.0014413 | 0.00036122
9 | 0.00028364 | 7.1087e-05
10 | 0.0022644 | 0.00056751
11 | 0.00061711 | 0.00015466
12 | 0.00039284 | 9.8455e-05
13 | 0.00069777 | 0.00017488
14 | 0.00037994 | 9.5222e-05
15 | 0.0018622 | 0.0004667
16 | 0.0016006 | 0.00040115
17 | 0.0015661 | 0.00039249
18 | 0.00062485 | 0.0001566
19 | 0.0052829 | 0.001324
20 | 0.0077506 | 0.0019425
21 | 0.0042671 | 0.0010694
22 | 0.0070448 | 0.0017656
23 | 0.0072677 | 0.0018215
24 | 0.0072356 | 0.0018134
25 | 0.0082093 | 0.0020574
26 | 0.028234 | 0.0070761
27 | 0.0051195 | 0.0012831
28 | 0.0032973 | 0.00082638
29 | 0.0026172 | 0.00065592
30 | 0.012871 | 0.0032257
31 | 0.0065947 | 0.0016528
32 | 0.0049407 | 0.0012383
33 | 0.001691 | 0.0004238
34 | 0.0028746 | 0.00072045
35 | 0.0026224 | 0.00065724
36 | 0.0020818 | 0.00052175
37 | 0.0012502 | 0.00031333
38 | 0.016174 | 0.0040535
39 | 0.0012582 | 0.00031533
40 | 0.002539 | 0.00063634
41 | 0.0079916 | 0.0020029
42 | 0.0052865 | 0.0013249
43 | 0.0027854 | 0.00069808
44 | 0.0011304 | 0.00028331
45 | 0.0056656 | 0.0014199
46 | 0.0011537 | 0.00028914
47 | 0.0015648 | 0.00039217
48 | 0.0020194 | 0.00050612
49 | 0.0025356 | 0.00063548
50 | 0.0021128 | 0.00052952
51 | 0.0027481 | 0.00068875
52 | 0.0032352 | 0.00081083
53 | 0.0045027 | 0.0011285
54 | 0.002472 | 0.00061955
55 | 0.0010384 | 0.00026025
56 | 0.0016426 | 0.00041169
57 | 0.0025156 | 0.00063047
58 | 0.0010392 | 0.00026046
59 | 0.0016956 | 0.00042497

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1