## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1107-18_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1107-18_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1107-18_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1107-18_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1107-18_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1107-18_0_2_node_37 | 0.4 | n |  | TRUE
6 | bus_LV_1107-18_0_2_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1107-18_0_2_node_35 | 0.4 | n |  | TRUE
8 | bus_LV_1107-18_0_2_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_1107-18_0_2_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_1107-18_0_2_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1107-18_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1107-18_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1107-18_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1107-18_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1107-18_0_2_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1107-18_0_2_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_1107-18_0_2_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1107-18_0_2_node_21 | 0.4 | n |  | TRUE
19 | bus_LV_1107-18_0_2_node_38 | 0.4 | n |  | TRUE
20 | bus_LV_1107-18_0_2_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1107-18_0_2_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1107-18_0_2_node_27 | 0.4 | n |  | TRUE
23 | bus_LV_1107-18_0_2_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1107-18_0_2_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_1107-18_0_2_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1107-18_0_2_node_12 | 0.4 | n |  | TRUE
27 | bus_LV_1107-18_0_2_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1107-18_0_2_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1107-18_0_2_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1107-18_0_2_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_1107-18_0_2_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_1107-18_0_2_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1107-18_0_2_node_34 | 0.4 | n |  | TRUE
34 | bus_LV_1107-18_0_2_node_45 | 0.4 | n |  | TRUE
35 | bus_LV_1107-18_0_2_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_1107-18_0_2_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_1107-18_0_2_node_43 | 0.4 | n |  | TRUE
38 | bus_LV_1107-18_0_2_node_41 | 0.4 | n |  | TRUE
39 | bus_LV_1107-18_0_2_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_1107-18_0_2_node_44 | 0.4 | n |  | TRUE
41 | bus_LV_1107-18_0_2_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1107-18_0_2_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1107-18_0_2_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_1107-18_0_2_node_42 | 0.4 | n |  | TRUE
45 | bus_MV_124_0_node_34 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1107-18_0_2_load_0 | 0 | 0.0021858 | 0.00054782 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1107-18_0_2_load_1 | 1 | 0.0021858 | 0.00054782 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1107-18_0_2_load_2 | 2 | 0.010167 | 0.002548 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1107-18_0_2_load_3 | 3 | 0.0021858 | 0.00054782 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1107-18_0_2_load_37 | 5 | 0.0021858 | 0.00054782 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1107-18_0_2_load_17 | 6 | 0.011364 | 0.002848 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1107-18_0_2_load_25 | 8 | 0.011451 | 0.0028698 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1107-18_0_2_load_5 | 10 | 0.0031341 | 0.00078548 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1107-18_0_2_load_6 | 11 | 0.0018883 | 0.00047326 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1107-18_0_2_load_10 | 14 | 0.0029678 | 0.0007438 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1107-18_0_2_load_26 | 16 | 0.00097049 | 0.00024323 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1107-18_0_2_load_21 | 18 | 0.0028273 | 0.00070859 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1107-18_0_2_load_38 | 19 | 0.0031369 | 0.00078619 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1107-18_0_2_load_23 | 20 | 0.007825 | 0.0019611 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1107-18_0_2_load_11 | 21 | 0.0075562 | 0.0018938 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1107-18_0_2_load_20 | 23 | 0.012558 | 0.0031474 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1107-18_0_2_load_29 | 24 | 0.0035813 | 0.00089757 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1107-18_0_2_load_24 | 25 | 0.0037894 | 0.00094972 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1107-18_0_2_load_12 | 26 | 0.012716 | 0.0031868 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1107-18_0_2_load_15 | 31 | 0.004676 | 0.0011719 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1107-18_0_2_load_34 | 33 | 0.010698 | 0.0026811 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1107-18_0_2_load_45 | 34 | 0.0061132 | 0.0015321 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1107-18_0_2_load_30 | 36 | 0.0068363 | 0.0017133 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1107-18_0_2_load_43 | 37 | 0.014649 | 0.0036715 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1107-18_0_2_load_41 | 38 | 0.0007838 | 0.00019644 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1107-18_0_2_load_22 | 39 | 0.00324 | 0.00081201 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1107-18_0_2_load_36 | 41 | 0.0031786 | 0.00079664 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1107-18_0_2_load_39 | 42 | 0.0031809 | 0.0007972 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1107-18_0_2_load_40 | 43 | 0.0031809 | 0.0007972 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1107-18_0_2_load_42 | 44 | 0.00024161 | 6.0554e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1107-18_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 2.5704e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
1 | LV_1107-18_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.024143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_1107-18_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 2.5697e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1107-18_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.00028949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1107-18_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 2.5691e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1107-18_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.017141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1107-18_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0059746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1107-18_0_2_line_7 | NAYY 4x150 SE | 7 | 41 | 0.019343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1107-18_0_2_line_8 | NAYY 4x150 SE | 7 | 33 | 0.01914 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1107-18_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.027852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1107-18_0_2_line_10 | NAYY 4x150 SE | 9 | 22 | 0.025962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1107-18_0_2_line_11 | NAYY 4x150 SE | 9 | 28 | 0.030901 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1107-18_0_2_line_12 | NAYY 4x150 SE | 10 | 11 | 0.0084309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1107-18_0_2_line_13 | NAYY 4x150 SE | 10 | 12 | 0.0148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1107-18_0_2_line_14 | NAYY 4x150 SE | 11 | 13 | 0.015731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1107-18_0_2_line_15 | NAYY 4x150 SE | 12 | 14 | 0.014935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1107-18_0_2_line_16 | NAYY 4x150 SE | 13 | 15 | 0.035761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1107-18_0_2_line_17 | NAYY 4x150 SE | 13 | 16 | 0.017248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1107-18_0_2_line_18 | NAYY 4x150 SE | 14 | 20 | 0.0019956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1107-18_0_2_line_19 | NAYY 4x150 SE | 15 | 21 | 0.019499 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1107-18_0_2_line_20 | NAYY 4x150 SE | 16 | 22 | 0.015506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1107-18_0_2_line_21 | NAYY 4x150 SE | 17 | 18 | 0.0037678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1107-18_0_2_line_22 | NAYY 4x150 SE | 17 | 19 | 0.017657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1107-18_0_2_line_23 | NAYY 4x150 SE | 18 | 23 | 0.038187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1107-18_0_2_line_24 | NAYY 4x150 SE | 19 | 24 | 0.011345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1107-18_0_2_line_25 | NAYY 4x150 SE | 20 | 25 | 0.010148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1107-18_0_2_line_26 | NAYY 4x150 SE | 22 | 24 | 0.015967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1107-18_0_2_line_27 | NAYY 4x150 SE | 23 | 39 | 0.002039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1107-18_0_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.010357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1107-18_0_2_line_29 | NAYY 4x150 SE | 26 | 28 | 0.017821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1107-18_0_2_line_30 | NAYY 4x150 SE | 27 | 29 | 0.013944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1107-18_0_2_line_31 | NAYY 4x150 SE | 28 | 30 | 0.04274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1107-18_0_2_line_32 | NAYY 4x150 SE | 29 | 33 | 0.018684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1107-18_0_2_line_33 | NAYY 4x150 SE | 30 | 34 | 0.014636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1107-18_0_2_line_34 | NAYY 4x150 SE | 31 | 32 | 0.0066789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1107-18_0_2_line_35 | NAYY 4x150 SE | 32 | 35 | 0.008468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1107-18_0_2_line_36 | NAYY 4x150 SE | 32 | 36 | 0.014319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1107-18_0_2_line_37 | NAYY 4x150 SE | 34 | 38 | 0.1271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1107-18_0_2_line_38 | NAYY 4x150 SE | 35 | 37 | 0.019082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1107-18_0_2_line_39 | NAYY 4x150 SE | 37 | 40 | 0.018453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1107-18_0_2_line_40 | NAYY 4x150 SE | 38 | 44 | 0.016192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1107-18_0_2_line_41 | NAYY 4x150 SE | 40 | 43 | 0.013213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1107-18_0_2_line_42 | NAYY 4x150 SE | 41 | 42 | 6.9998e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1107-18_0_2_line_43 | NAYY 4x150 SE | 42 | 43 | 6.7131e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1107-18_0_2_trafo_17 | 0.25 MVA 20/0.4 kV | 45 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2647826.4757 | 1211621.1174 | 2647826.4679 | 1211621.0929
1 | 2647826.4757 | 1211621.1174 | 2647833.747 | 1211644.1391
2 | 2647826.4679 | 1211621.0929 | 2647826.4602 | 1211621.0684
3 | 2647833.8342 | 1211644.4152 | 2647833.747 | 1211644.1391
4 | 2647826.4602 | 1211621.0684 | 2647826.4525 | 1211621.0439
5 | 2647833.8342 | 1211644.4152 | 2647817.6245 | 1211649.9887
6 | 2647824.653 | 1211615.3467 | 2647826.4525 | 1211621.0439
7 | 2647824.653 | 1211615.3467 | 2647818.8263 | 1211596.9021
8 | 2647824.653 | 1211615.3467 | 2647810.9736 | 1211619.4618 | 2647806.1186 | 1211619.4229
9 | 2647798.9882 | 1211689.0512 | 2647825.5695 | 1211680.7328
10 | 2647807.2021 | 1211713.6759 | 2647805.0831 | 1211707.8777 | 2647800.3362 | 1211693.409 | 2647798.9882 | 1211689.0512
11 | 2647790.0085 | 1211659.4841 | 2647791.4447 | 1211664.2095 | 2647798.9882 | 1211689.0512
12 | 2647841.5274 | 1211740.6652 | 2647833.215 | 1211742.0732
13 | 2647856.1198 | 1211738.1934 | 2647841.5274 | 1211740.6652
14 | 2647817.7048 | 1211744.7005 | 2647833.215 | 1211742.0732
15 | 2647856.1198 | 1211738.1934 | 2647870.7688 | 1211735.2842
16 | 2647817.7048 | 1211744.7005 | 2647829.3932 | 1211778.5029
17 | 2647817.7048 | 1211744.7005 | 2647812.1743 | 1211728.3636
18 | 2647872.7261 | 1211734.8955 | 2647870.7688 | 1211735.2842
19 | 2647829.3932 | 1211778.5029 | 2647847.857 | 1211772.2337
20 | 2647807.2021 | 1211713.6759 | 2647812.1743 | 1211728.3636
21 | 2647851.4787 | 1211705.8149 | 2647850.9432 | 1211702.0853
22 | 2647851.4787 | 1211705.8149 | 2647834.094 | 1211708.9014
23 | 2647850.9432 | 1211702.0853 | 2647848.3844 | 1211684.2663 | 2647848.4326 | 1211682.9882 | 2647848.8201 | 1211682.0463 | 2647849.7521 | 1211681.4201 | 2647851.1315 | 1211680.8975 | 2647866.0674 | 1211677.629
24 | 2647822.9237 | 1211710.8846 | 2647834.094 | 1211708.9014
25 | 2647872.7261 | 1211734.8955 | 2647882.6794 | 1211732.9188
26 | 2647807.2021 | 1211713.6759 | 2647822.9237 | 1211710.8846
27 | 2647868.0593 | 1211677.1931 | 2647866.0674 | 1211677.629
28 | 2647781.8132 | 1211632.5249 | 2647784.8254 | 1211642.4337
29 | 2647790.0085 | 1211659.4841 | 2647784.8254 | 1211642.4337
30 | 2647781.8132 | 1211632.5249 | 2647789.7807 | 1211630.0539 | 2647788.1901 | 1211624.6824
31 | 2647756.9352 | 1211679.1977 | 2647760.3276 | 1211676.8568 | 2647768.6767 | 1211672.2653 | 2647791.4447 | 1211664.2095 | 2647790.0085 | 1211659.4841
32 | 2647788.1901 | 1211624.6824 | 2647806.1186 | 1211619.4229
33 | 2647756.9352 | 1211679.1977 | 2647756.3637 | 1211678.4593 | 2647749.7929 | 1211666.4358
34 | 2647772.7056 | 1211602.7678 | 2647774.6603 | 1211609.1543
35 | 2647772.7056 | 1211602.7678 | 2647780.4756 | 1211599.3502
36 | 2647772.7056 | 1211602.7678 | 2647765.9397 | 1211590.1478
37 | 2647749.7929 | 1211666.4358 | 2647622.9928 | 1211675.1804
38 | 2647780.4756 | 1211599.3502 | 2647795.3065 | 1211592.8318 | 2647797.9404 | 1211591.662
39 | 2647814.8048 | 1211584.1717 | 2647797.9404 | 1211591.662
40 | 2647610.2093 | 1211665.5287 | 2647618.6572 | 1211670.4546 | 2647622.9928 | 1211675.1804
41 | 2647814.8048 | 1211584.1717 | 2647818.785 | 1211596.7714
42 | 2647818.8263 | 1211596.9021 | 2647818.8053 | 1211596.8354
43 | 2647818.8053 | 1211596.8354 | 2647818.785 | 1211596.7714

## bus_geodata
| x | y | coords
0 | 2647826.4757 | 1211621.1174
1 | 2647826.4679 | 1211621.0929
2 | 2647833.747 | 1211644.1391
3 | 2647826.4602 | 1211621.0684
4 | 2647833.8342 | 1211644.4152
5 | 2647826.4525 | 1211621.0439
6 | 2647817.6245 | 1211649.9887
7 | 2647824.653 | 1211615.3467
8 | 2647825.5695 | 1211680.7328
9 | 2647798.9882 | 1211689.0512
10 | 2647841.5274 | 1211740.6652
11 | 2647833.215 | 1211742.0732
12 | 2647856.1198 | 1211738.1934
13 | 2647817.7048 | 1211744.7005
14 | 2647870.7688 | 1211735.2842
15 | 2647829.3932 | 1211778.5029
16 | 2647812.1743 | 1211728.3636
17 | 2647851.4787 | 1211705.8149
18 | 2647850.9432 | 1211702.0853
19 | 2647834.094 | 1211708.9014
20 | 2647872.7261 | 1211734.8955
21 | 2647847.857 | 1211772.2337
22 | 2647807.2021 | 1211713.6759
23 | 2647866.0674 | 1211677.629
24 | 2647822.9237 | 1211710.8846
25 | 2647882.6794 | 1211732.9188
26 | 2647784.8254 | 1211642.4337
27 | 2647781.8132 | 1211632.5249
28 | 2647790.0085 | 1211659.4841
29 | 2647788.1901 | 1211624.6824
30 | 2647756.9352 | 1211679.1977
31 | 2647774.6603 | 1211609.1543
32 | 2647772.7056 | 1211602.7678
33 | 2647806.1186 | 1211619.4229
34 | 2647749.7929 | 1211666.4358
35 | 2647780.4756 | 1211599.3502
36 | 2647765.9397 | 1211590.1478
37 | 2647797.9404 | 1211591.662
38 | 2647622.9928 | 1211675.1804
39 | 2647868.0593 | 1211677.1931
40 | 2647814.8048 | 1211584.1717
41 | 2647818.8263 | 1211596.9021
42 | 2647818.8053 | 1211596.8354
43 | 2647818.785 | 1211596.7714
44 | 2647610.2093 | 1211665.5287
45 | 2647833.8342 | 1211644.4152

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99567 | -0.030058 | 0.0021858 | 0.00054782
1 | 0.99566 | -0.030076 | 0.0021858 | 0.00054782
2 | 0.99811 | -0.013086 | 0.010167 | 0.002548
3 | 0.99566 | -0.030093 | 0.0021858 | 0.00054782
4 | 0.99814 | -0.012869 | 0 | 0
5 | 0.99566 | -0.03011 | 0.0021858 | 0.00054782
6 | 1 | 0 | -0.15289 | -0.038376
7 | 0.99509 | -0.03406 | 0 | 0
8 | 0.98189 | -0.12687 | 0.011451 | 0.0028698
9 | 0.98235 | -0.12357 | 0 | 0
10 | 0.97834 | -0.15215 | 0.0031341 | 0.00078548
11 | 0.97856 | -0.15059 | 0.0018883 | 0.00047326
12 | 0.97803 | -0.1544 | 0 | 0
13 | 0.97901 | -0.14738 | 0 | 0
14 | 0.97771 | -0.15667 | 0.0029678 | 0.0007438
15 | 0.97862 | -0.15019 | 0 | 0
16 | 0.97969 | -0.1425 | 0.00097049 | 0.00024323
17 | 0.9789 | -0.14817 | 0 | 0
18 | 0.9788 | -0.1489 | 0.0028273 | 0.00070859
19 | 0.97938 | -0.14474 | 0.0031369 | 0.00078619
20 | 0.97768 | -0.15692 | 0.007825 | 0.0019611
21 | 0.9784 | -0.15173 | 0.0075562 | 0.0018938
22 | 0.98033 | -0.13797 | 0 | 0
23 | 0.97792 | -0.15519 | 0.012558 | 0.0031474
24 | 0.97974 | -0.14217 | 0.0035813 | 0.00089757
25 | 0.97762 | -0.15732 | 0.0037894 | 0.00094972
26 | 0.98714 | -0.089687 | 0.012716 | 0.0031868
27 | 0.98842 | -0.080701 | 0 | 0
28 | 0.98527 | -0.10287 | 0 | 0
29 | 0.99014 | -0.068638 | 0 | 0
30 | 0.98483 | -0.10602 | 0 | 0
31 | 0.9924 | -0.05298 | 0.004676 | 0.0011719
32 | 0.99245 | -0.052664 | 0 | 0
33 | 0.99244 | -0.052539 | 0.010698 | 0.0026811
34 | 0.98468 | -0.1071 | 0.0061132 | 0.0015321
35 | 0.99259 | -0.051676 | 0 | 0
36 | 0.99231 | -0.053656 | 0.0068363 | 0.0017133
37 | 0.99291 | -0.049451 | 0.014649 | 0.0036715
38 | 0.98449 | -0.10845 | 0.0007838 | 0.00019644
39 | 0.97791 | -0.15526 | 0.00324 | 0.00081201
40 | 0.9936 | -0.044566 | 0 | 0
41 | 0.9941 | -0.041029 | 0.0031786 | 0.00079664
42 | 0.9941 | -0.041052 | 0.0031809 | 0.0007972
43 | 0.99409 | -0.041072 | 0.0031809 | 0.0007972
44 | 0.98449 | -0.10849 | 0.00024161 | 6.0554e-05
45 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.13912 | 0.035045 | -0.13912 | -0.035045 | 3.469e-07 | 1.3275e-07 | 0.20798 | 0.20798 | 0.20798 | 0.99567 | -0.030058 | 0.99566 | -0.030076 | 38.5154
1 | -0.14131 | -0.035593 | 0.14165 | 0.035721 | 0.00033615 | 0.00012866 | 0.21125 | 0.21125 | 0.21125 | 0.99567 | -0.030058 | 0.99811 | -0.013086 | 39.1204
2 | 0.13694 | 0.034497 | -0.13694 | -0.034497 | 3.3601e-07 | 1.2856e-07 | 0.20472 | 0.20472 | 0.20472 | 0.99566 | -0.030076 | 0.99566 | -0.030093 | 37.9105
3 | -0.15181 | -0.038269 | 0.15182 | 0.038271 | 4.6298e-06 | 1.7731e-06 | 0.22641 | 0.22641 | 0.22641 | 0.99811 | -0.013086 | 0.99814 | -0.012869 | 41.9272
4 | 0.13475 | 0.033949 | -0.13475 | -0.033949 | 3.2529e-07 | 1.2444e-07 | 0.20145 | 0.20145 | 0.20145 | 0.99566 | -0.030093 | 0.99566 | -0.03011 | 37.3055
5 | -0.15182 | -0.038271 | 0.15209 | 0.038376 | 0.00027414 | 0.00010499 | 0.22641 | 0.22641 | 0.22641 | 0.99814 | -0.012869 | 1 | 0 | 41.9272
6 | 0.13257 | 0.033401 | -0.13249 | -0.033373 | 7.3214e-05 | 2.8004e-05 | 0.19818 | 0.19818 | 0.19818 | 0.99566 | -0.03011 | 0.99509 | -0.03406 | 36.7006
7 | 0.035774 | 0.008974 | -0.035739 | -0.0089609 | 3.4544e-05 | 1.3035e-05 | 0.053497 | 0.053497 | 0.053497 | 0.99509 | -0.03406 | 0.9941 | -0.041029 | 19.8138
8 | 0.09672 | 0.024399 | -0.096469 | -0.024303 | 0.00025003 | 9.5916e-05 | 0.14469 | 0.14469 | 0.14469 | 0.99509 | -0.03406 | 0.99244 | -0.052539 | 53.5875
9 | -0.011451 | -0.0028698 | 0.011456 | 0.0028715 | 5.2336e-06 | 1.6605e-06 | 0.017353 | 0.017353 | 0.017353 | 0.98189 | -0.12687 | 0.98235 | -0.12357 | 6.4271
10 | 0.053692 | 0.013482 | -0.053585 | -0.013441 | 0.00010718 | 4.0897e-05 | 0.08134 | 0.08134 | 0.08134 | 0.98235 | -0.12357 | 0.98033 | -0.13797 | 30.1258
11 | -0.065148 | -0.016354 | 0.065336 | 0.016426 | 0.00018781 | 7.1843e-05 | 0.098693 | 0.098693 | 0.098693 | 0.98235 | -0.12357 | 0.98527 | -0.10287 | 36.5529
12 | -0.017726 | -0.0044433 | 0.01773 | 0.0044447 | 3.824e-06 | 1.3649e-06 | 0.026961 | 0.026961 | 0.026961 | 0.97834 | -0.15215 | 0.97856 | -0.15059 | 9.9855
13 | 0.014592 | 0.0036579 | -0.014587 | -0.0036563 | 4.5491e-06 | 1.5639e-06 | 0.022194 | 0.022194 | 0.022194 | 0.97834 | -0.15215 | 0.97803 | -0.1544 | 8.22
14 | -0.019618 | -0.004918 | 0.019627 | 0.0049211 | 8.736e-06 | 3.1623e-06 | 0.029832 | 0.029832 | 0.029832 | 0.97856 | -0.15059 | 0.97901 | -0.14738 | 11.049
15 | 0.014587 | 0.0036563 | -0.014583 | -0.0036547 | 4.5905e-06 | 1.5782e-06 | 0.022194 | 0.022194 | 0.022194 | 0.97803 | -0.1544 | 0.97771 | -0.15667 | 8.22
16 | 0.0075608 | 0.0018948 | -0.0075578 | -0.0018941 | 2.9469e-06 | 6.8395e-07 | 0.011492 | 0.011492 | 0.011492 | 0.97901 | -0.14738 | 0.97862 | -0.15019 | 4.2563
17 | -0.027188 | -0.0068159 | 0.027206 | 0.0068228 | 1.8379e-05 | 6.8517e-06 | 0.041324 | 0.041324 | 0.041324 | 0.97901 | -0.14738 | 0.97969 | -0.1425 | 15.3051
18 | 0.011615 | 0.0029109 | -0.011615 | -0.0029108 | 3.8912e-07 | 1.2464e-07 | 0.017677 | 0.017677 | 0.017677 | 0.97771 | -0.15667 | 0.97768 | -0.15692 | 6.5471
19 | 0.0075578 | 0.0018941 | -0.0075562 | -0.0018938 | 1.6069e-06 | 3.731e-07 | 0.011492 | 0.011492 | 0.011492 | 0.97862 | -0.15019 | 0.9784 | -0.15173 | 4.2563
20 | -0.028177 | -0.007066 | 0.028194 | 0.0070727 | 1.7723e-05 | 6.6212e-06 | 0.042798 | 0.042798 | 0.042798 | 0.97969 | -0.1425 | 0.98033 | -0.13797 | 15.851
21 | 0.018641 | 0.0046735 | -0.018639 | -0.0046728 | 1.8879e-06 | 6.7875e-07 | 0.028337 | 0.028337 | 0.028337 | 0.9789 | -0.14817 | 0.9788 | -0.1489 | 10.4951
22 | -0.018641 | -0.0046735 | 0.01865 | 0.0046766 | 8.847e-06 | 3.1806e-06 | 0.028337 | 0.028337 | 0.028337 | 0.9789 | -0.14817 | 0.97938 | -0.14474 | 10.4951
23 | 0.015812 | 0.0039642 | -0.015798 | -0.0039594 | 1.377e-05 | 4.8164e-06 | 0.024039 | 0.024039 | 0.024039 | 0.9788 | -0.1489 | 0.97792 | -0.15519 | 8.9033
24 | -0.021787 | -0.0054628 | 0.021795 | 0.0054657 | 7.7574e-06 | 2.8408e-06 | 0.033103 | 0.033103 | 0.033103 | 0.97938 | -0.14474 | 0.97974 | -0.14217 | 12.2603
25 | 0.0037896 | 0.00094967 | -0.0037894 | -0.00094972 | 2.1065e-07 | -4.6225e-08 | 0.0057677 | 0.0057678 | 0.0057678 | 0.97768 | -0.15692 | 0.97762 | -0.15732 | 2.1362
26 | 0.025391 | 0.0063687 | -0.025376 | -0.0063632 | 1.4801e-05 | 5.4915e-06 | 0.038542 | 0.038542 | 0.038542 | 0.98033 | -0.13797 | 0.97974 | -0.14217 | 14.2749
27 | 0.00324 | 0.000812 | -0.00324 | -0.00081201 | 3.0925e-08 | -1.3688e-08 | 0.00493 | 0.00493 | 0.00493 | 0.97792 | -0.15519 | 0.97791 | -0.15526 | 1.8259
28 | -0.085328 | -0.021452 | 0.085435 | 0.021493 | 0.00010695 | 4.1004e-05 | 0.12865 | 0.12865 | 0.12865 | 0.98714 | -0.089687 | 0.98842 | -0.080701 | 47.647
29 | 0.072612 | 0.018265 | -0.072479 | -0.018214 | 0.00013328 | 5.1036e-05 | 0.10948 | 0.10948 | 0.10948 | 0.98714 | -0.089687 | 0.98527 | -0.10287 | 40.548
30 | -0.085435 | -0.021493 | 0.085579 | 0.021548 | 0.000144 | 5.5206e-05 | 0.12865 | 0.12865 | 0.12865 | 0.98842 | -0.080701 | 0.99014 | -0.068638 | 47.647
31 | 0.0071429 | 0.0017882 | -0.0071398 | -0.0017876 | 3.1033e-06 | 6.495e-07 | 0.010787 | 0.010787 | 0.010787 | 0.98527 | -0.10287 | 0.98483 | -0.10602 | 3.9952
32 | -0.085579 | -0.021548 | 0.085772 | 0.021622 | 0.00019295 | 7.3972e-05 | 0.12865 | 0.12865 | 0.12865 | 0.99014 | -0.068638 | 0.99244 | -0.052539 | 47.6469
33 | 0.0071398 | 0.0017876 | -0.0071388 | -0.0017873 | 1.0627e-06 | 2.2253e-07 | 0.010787 | 0.010787 | 0.010787 | 0.98483 | -0.10602 | 0.98468 | -0.1071 | 3.9953
34 | -0.004676 | -0.0011719 | 0.0046762 | 0.0011719 | 2.0487e-07 | -7.504e-09 | 0.0070113 | 0.0070112 | 0.0070113 | 0.9924 | -0.05298 | 0.99245 | -0.052664 | 2.5968
35 | -0.011513 | -0.0028854 | 0.011515 | 0.0028859 | 1.5746e-06 | 4.9618e-07 | 0.017263 | 0.017263 | 0.017263 | 0.99245 | -0.052664 | 0.99259 | -0.051676 | 6.3935
36 | 0.0068373 | 0.0017135 | -0.0068363 | -0.0017133 | 9.3901e-07 | 1.7615e-07 | 0.010251 | 0.010251 | 0.010251 | 0.99245 | -0.052664 | 0.99231 | -0.053656 | 3.7968
37 | 0.0010256 | 0.00025525 | -0.0010254 | -0.00025679 | 1.9043e-07 | -1.5432e-06 | 0.0015492 | 0.0015498 | 0.0015498 | 0.98468 | -0.1071 | 0.98449 | -0.10845 | 0.574
38 | -0.011515 | -0.0028859 | 0.011519 | 0.002887 | 3.5483e-06 | 1.118e-06 | 0.017263 | 0.017262 | 0.017263 | 0.99259 | -0.051676 | 0.99291 | -0.049451 | 6.3935
39 | -0.026168 | -0.0065586 | 0.026186 | 0.0065651 | 1.7709e-05 | 6.5723e-06 | 0.039217 | 0.039217 | 0.039217 | 0.99291 | -0.049451 | 0.9936 | -0.044566 | 14.5248
40 | 0.00024161 | 6.0349e-05 | -0.00024161 | -6.0554e-05 | 1.3472e-09 | -2.0538e-07 | 0.00036512 | 0.00036519 | 0.00036519 | 0.98449 | -0.10845 | 0.98449 | -0.10849 | 0.13526
41 | -0.026186 | -0.0065651 | 0.026198 | 0.0065698 | 1.2681e-05 | 4.706e-06 | 0.039217 | 0.039217 | 0.039217 | 0.9936 | -0.044566 | 0.99409 | -0.041072 | 14.5247
42 | 0.03256 | 0.0081643 | -0.03256 | -0.0081643 | 1.0376e-07 | 3.8999e-08 | 0.048739 | 0.048739 | 0.048739 | 0.9941 | -0.041029 | 0.9941 | -0.041052 | 18.0516
43 | 0.029379 | 0.0073671 | -0.029379 | -0.007367 | 8.1018e-08 | 3.0291e-08 | 0.043978 | 0.043978 | 0.043978 | 0.9941 | -0.041052 | 0.99409 | -0.041072 | 16.2882

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16426 | 0.041224

## res_load
| p_mw | q_mvar
0 | 0.0021858 | 0.00054782
1 | 0.0021858 | 0.00054782
2 | 0.010167 | 0.002548
3 | 0.0021858 | 0.00054782
4 | 0.0021858 | 0.00054782
5 | 0.011364 | 0.002848
6 | 0.011451 | 0.0028698
7 | 0.0031341 | 0.00078548
8 | 0.0018883 | 0.00047326
9 | 0.0029678 | 0.0007438
10 | 0.00097049 | 0.00024323
11 | 0.0028273 | 0.00070859
12 | 0.0031369 | 0.00078619
13 | 0.007825 | 0.0019611
14 | 0.0075562 | 0.0018938
15 | 0.012558 | 0.0031474
16 | 0.0035813 | 0.00089757
17 | 0.0037894 | 0.00094972
18 | 0.012716 | 0.0031868
19 | 0.004676 | 0.0011719
20 | 0.010698 | 0.0026811
21 | 0.0061132 | 0.0015321
22 | 0.0068363 | 0.0017133
23 | 0.014649 | 0.0036715
24 | 0.0007838 | 0.00019644
25 | 0.00324 | 0.00081201
26 | 0.0031786 | 0.00079664
27 | 0.0031809 | 0.0007972
28 | 0.0031809 | 0.0007972
29 | 0.00024161 | 6.0554e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1