## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1107-20_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1107-20_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1107-20_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1107-20_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1107-20_0_2_node_41 | 0.4 | n |  | TRUE
5 | bus_LV_1107-20_0_2_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1107-20_0_2_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1107-20_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1107-20_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1107-20_0_2_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1107-20_0_2_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_1107-20_0_2_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1107-20_0_2_node_27 | 0.4 | n |  | TRUE
13 | bus_LV_1107-20_0_2_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1107-20_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1107-20_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1107-20_0_2_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1107-20_0_2_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1107-20_0_2_node_31 | 0.4 | n |  | TRUE
19 | bus_LV_1107-20_0_2_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_1107-20_0_2_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1107-20_0_2_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1107-20_0_2_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1107-20_0_2_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1107-20_0_2_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1107-20_0_2_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1107-20_0_2_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1107-20_0_2_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_1107-20_0_2_node_35 | 0.4 | n |  | TRUE
29 | bus_LV_1107-20_0_2_node_36 | 0.4 | n |  | TRUE
30 | bus_LV_1107-20_0_2_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_1107-20_0_2_node_34 | 0.4 | n |  | TRUE
32 | bus_LV_1107-20_0_2_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_1107-20_0_2_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_1107-20_0_2_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1107-20_0_2_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_1107-20_0_2_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_1107-20_0_2_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_1107-20_0_2_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_1107-20_0_2_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_1107-20_0_2_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_1107-20_0_2_node_33 | 0.4 | n |  | TRUE
42 | bus_MV_124_0_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1107-20_0_2_load_0 | 0 | 0.00562 | 0.0014085 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1107-20_0_2_load_1 | 1 | 0.0062666 | 0.0015706 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1107-20_0_2_load_2 | 2 | 0.005114 | 0.0012817 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1107-20_0_2_load_3 | 3 | 0.0021228 | 0.00053202 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1107-20_0_2_load_4 | 6 | 0.0032612 | 0.00081733 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1107-20_0_2_load_5 | 7 | 0.0035215 | 0.00088257 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1107-20_0_2_load_6 | 8 | 0.002928 | 0.00073382 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1107-20_0_2_load_8 | 9 | 0.0049078 | 0.00123 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1107-20_0_2_load_42 | 10 | 0.0038516 | 0.00096529 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1107-20_0_2_load_13 | 11 | 0.0024767 | 0.00062072 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1107-20_0_2_load_27 | 12 | 0.0035 | 0.00087718 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1107-20_0_2_load_14 | 13 | 0.0058092 | 0.0014559 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1107-20_0_2_load_9 | 14 | 0.0015797 | 0.00039591 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1107-20_0_2_load_10 | 15 | 0.00085909 | 0.00021531 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1107-20_0_2_load_11 | 16 | 0.0027901 | 0.00069926 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1107-20_0_2_load_12 | 17 | 0.0019199 | 0.00048116 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1107-20_0_2_load_31 | 18 | 0.0037331 | 0.0009356 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1107-20_0_2_load_32 | 19 | 0.0041866 | 0.0010493 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1107-20_0_2_load_15 | 20 | 0.0043046 | 0.0010788 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1107-20_0_2_load_16 | 21 | 0.0030512 | 0.00076471 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1107-20_0_2_load_17 | 22 | 0.0026267 | 0.00065831 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1107-20_0_2_load_18 | 23 | 0.0026134 | 0.00065498 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1107-20_0_2_load_20 | 25 | 0.004977 | 0.0012474 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1107-20_0_2_load_21 | 26 | 0.0019548 | 0.00048992 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1107-20_0_2_load_22 | 27 | 0.0045834 | 0.0011487 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1107-20_0_2_load_35 | 28 | 0.0013427 | 0.00033652 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1107-20_0_2_load_39 | 30 | 0.0066833 | 0.001675 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1107-20_0_2_load_34 | 31 | 0.0018933 | 0.00047451 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1107-20_0_2_load_37 | 32 | 0.0038832 | 0.00097321 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1107-20_0_2_load_26 | 33 | 0.0043124 | 0.0010808 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1107-20_0_2_load_38 | 34 | 0.0052603 | 0.0013184 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1107-20_0_2_load_23 | 35 | 0.0028544 | 0.00071538 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1107-20_0_2_load_24 | 36 | 0.0033025 | 0.00082769 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1107-20_0_2_load_28 | 38 | 0.001128 | 0.00028271 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1107-20_0_2_load_30 | 40 | 0.0015111 | 0.00037872 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1107-20_0_2_load_33 | 41 | 0.0017606 | 0.00044126 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1107-20_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.024308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1107-20_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.020345 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1107-20_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.020251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1107-20_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.016787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1107-20_0_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.093828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1107-20_0_2_line_5 | NAYY 4x150 SE | 5 | 10 | 0.040728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1107-20_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.020774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1107-20_0_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.023627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1107-20_0_2_line_8 | NAYY 4x150 SE | 6 | 8 | 0.014993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1107-20_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.006128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1107-20_0_2_line_10 | NAYY 4x150 SE | 9 | 11 | 0.023335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1107-20_0_2_line_11 | NAYY 4x150 SE | 10 | 12 | 0.0071127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1107-20_0_2_line_12 | NAYY 4x150 SE | 11 | 13 | 0.010745 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1107-20_0_2_line_13 | NAYY 4x150 SE | 12 | 37 | 0.011734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1107-20_0_2_line_14 | NAYY 4x150 SE | 13 | 20 | 0.011786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1107-20_0_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.005606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1107-20_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.0034352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1107-20_0_2_line_17 | NAYY 4x150 SE | 15 | 17 | 0.038328 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1107-20_0_2_line_18 | NAYY 4x150 SE | 17 | 18 | 0.039549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1107-20_0_2_line_19 | NAYY 4x150 SE | 18 | 19 | 0.032892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1107-20_0_2_line_20 | NAYY 4x150 SE | 19 | 32 | 0.0030294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1107-20_0_2_line_21 | NAYY 4x150 SE | 20 | 21 | 0.015996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1107-20_0_2_line_22 | NAYY 4x150 SE | 22 | 23 | 0.005968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1107-20_0_2_line_23 | NAYY 4x150 SE | 22 | 24 | 0.021374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1107-20_0_2_line_24 | NAYY 4x150 SE | 23 | 25 | 0.033701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1107-20_0_2_line_25 | NAYY 4x150 SE | 24 | 26 | 0.037504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1107-20_0_2_line_26 | NAYY 4x150 SE | 24 | 27 | 0.014967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1107-20_0_2_line_27 | NAYY 4x150 SE | 25 | 28 | 0.037606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1107-20_0_2_line_28 | NAYY 4x150 SE | 26 | 29 | 0.013996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1107-20_0_2_line_29 | NAYY 4x150 SE | 27 | 30 | 0.0025555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1107-20_0_2_line_30 | NAYY 4x150 SE | 28 | 31 | 0.022616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1107-20_0_2_line_31 | NAYY 4x150 SE | 29 | 32 | 0.018544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1107-20_0_2_line_32 | NAYY 4x150 SE | 29 | 33 | 0.011624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1107-20_0_2_line_33 | NAYY 4x150 SE | 30 | 34 | 0.029734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1107-20_0_2_line_34 | NAYY 4x150 SE | 31 | 41 | 0.10387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1107-20_0_2_line_35 | NAYY 4x150 SE | 33 | 36 | 0.015323 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1107-20_0_2_line_36 | NAYY 4x150 SE | 35 | 36 | 0.01889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1107-20_0_2_line_37 | NAYY 4x150 SE | 35 | 37 | 0.027037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1107-20_0_2_line_38 | NAYY 4x150 SE | 38 | 39 | 0.00839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1107-20_0_2_line_39 | NAYY 4x150 SE | 39 | 40 | 0.027677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1107-20_0_2_line_40 | NAYY 4x150 SE | 40 | 41 | 0.014626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1107-20_0_2_trafo_37 | 0.25 MVA 20/0.4 kV | 42 | 32 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2647896.97 | 1213086.1493 | 2647892.7718 | 1213084.8815 | 2647888.0706 | 1213082.8648 | 2647884.0229 | 1213080.8312 | 2647880.2378 | 1213078.2548 | 2647875.8514 | 1213074.6167
1 | 2647896.97 | 1213086.1493 | 2647896.97 | 1213086.1493 | 2647901.9457 | 1213087.0898 | 2647905.9087 | 1213087.3773 | 2647910.1845 | 1213087.5006 | 2647915.012 | 1213087.028 | 2647917.1485 | 1213086.5985
2 | 2647935.7372 | 1213078.9363 | 2647934.2805 | 1213079.9118 | 2647930.3882 | 1213082.1597 | 2647924.3976 | 1213084.6353 | 2647920.0109 | 1213086.0231 | 2647917.1485 | 1213086.5985
3 | 2647949.6178 | 1213069.4956 | 2647939.9399 | 1213076.1217 | 2647935.7372 | 1213078.9363
4 | 2647949.6178 | 1213069.4956 | 2647953.9896 | 1213067.1293 | 2647957.3057 | 1213065.6773 | 2647963.5815 | 1213063.6376 | 2647970.8997 | 1213062.3401 | 2647971.135 | 1213069.9243 | 2647970.5038 | 1213072.8432 | 2647969.2457 | 1213076.2573 | 2647959.3555 | 1213092.2873 | 2647948.6035 | 1213112.5128 | 2647940.1682 | 1213125.2193
5 | 2647940.1682 | 1213125.2193 | 2647941.4478 | 1213129.5098 | 2647941.9606 | 1213135.6509 | 2647937.8568 | 1213145.3237 | 2647944.2972 | 1213163.8151
6 | 2647940.1682 | 1213125.2193 | 2647937.8766 | 1213128.6807 | 2647929.9602 | 1213135.4322 | 2647924.2487 | 1213137.8911
7 | 2647901.0555 | 1213141.1813 | 2647901.0555 | 1213141.1813 | 2647919.9973 | 1213139.7214 | 2647924.2487 | 1213137.8911
8 | 2647901.0555 | 1213141.1813 | 2647886.0679 | 1213140.7991
9 | 2647879.9419 | 1213140.6429 | 2647886.0679 | 1213140.7991
10 | 2647856.8298 | 1213137.6735 | 2647874.9675 | 1213140.516 | 2647879.9419 | 1213140.6429
11 | 2647946.6366 | 1213170.532 | 2647944.2972 | 1213163.8151
12 | 2647856.8298 | 1213137.6735 | 2647853.2844 | 1213137.1179 | 2647846.3468 | 1213135.3635
13 | 2647950.494 | 1213181.6133 | 2647949.6031 | 1213179.0491 | 2647946.6366 | 1213170.532
14 | 2647834.9204 | 1213132.474 | 2647846.3468 | 1213135.3635
15 | 2647764.1832 | 1213146.8102 | 2647767.4407 | 1213151.3726
16 | 2647762.1872 | 1213144.0144 | 2647764.1832 | 1213146.8102
17 | 2647791.3495 | 1213181.1515 | 2647790.6157 | 1213180.6081 | 2647786.2572 | 1213176.593 | 2647781.403 | 1213170.9286 | 2647767.4407 | 1213151.3726
18 | 2647791.3495 | 1213181.1515 | 2647793.7571 | 1213182.9346 | 2647797.87 | 1213185.3579 | 2647803.8216 | 1213187.7403 | 2647814.0979 | 1213190.7577 | 2647828.2226 | 1213194.6788
19 | 2647828.2226 | 1213194.6788 | 2647840.3681 | 1213198.0503 | 2647847.5673 | 1213199.2532 | 2647855.1723 | 1213200.0591 | 2647860.4939 | 1213200.5055
20 | 2647860.4939 | 1213200.5055 | 2647863.5127 | 1213200.7588
21 | 2647819.4127 | 1213128.5524 | 2647834.9204 | 1213132.474
22 | 2647846.4249 | 1213247.3432 | 2647851.452 | 1213249.0583 | 2647852.098 | 1213249.1751
23 | 2647873.1304 | 1213252.9789 | 2647852.098 | 1213249.1751
24 | 2647846.4249 | 1213247.3432 | 2647839.104 | 1213244.8457 | 2647815.7532 | 1213233.4904
25 | 2647873.1304 | 1213252.9789 | 2647878.6504 | 1213228.6866 | 2647880.2329 | 1213216.1937
26 | 2647873.1304 | 1213252.9789 | 2647887.8586 | 1213255.642
27 | 2647781.9338 | 1213217.0443 | 2647815.7532 | 1213233.4904
28 | 2647881.9918 | 1213202.3089 | 2647880.2329 | 1213216.1937
29 | 2647890.3733 | 1213256.0967 | 2647887.8586 | 1213255.642
30 | 2647759.8902 | 1213212.6103 | 2647769.7137 | 1213213.4268 | 2647781.037 | 1213216.6082 | 2647781.9338 | 1213217.0443
31 | 2647881.9918 | 1213202.3089 | 2647863.5127 | 1213200.7588
32 | 2647881.9918 | 1213202.3089 | 2647892.2573 | 1213202.8805 | 2647893.5961 | 1213202.7738
33 | 2647919.634 | 1213261.378 | 2647893.6559 | 1213256.6902 | 2647890.3733 | 1213256.0967
34 | 2647759.8902 | 1213212.6103 | 2647682.1056 | 1213281.4508
35 | 2647893.5961 | 1213202.7738 | 2647899.2275 | 1213202.325 | 2647904.5755 | 1213201.3451 | 2647908.658 | 1213200.2119
36 | 2647908.658 | 1213200.2119 | 2647912.1659 | 1213199.2381 | 2647920.7923 | 1213195.8276 | 2647926.3598 | 1213193.6623
37 | 2647950.494 | 1213181.6133 | 2647942.6704 | 1213186.2643 | 2647934.516 | 1213190.4902 | 2647926.3598 | 1213193.6623
38 | 2647672.0566 | 1213319.8644 | 2647663.7191 | 1213318.9277
39 | 2647672.0566 | 1213319.8644 | 2647671.0119 | 1213312.7741 | 2647672.2033 | 1213301.5103 | 2647673.5521 | 1213292.4268
40 | 2647682.1056 | 1213281.4508 | 2647677.8162 | 1213283.5445 | 2647673.5521 | 1213292.4268

## bus_geodata
| x | y | coords
0 | 2647896.97 | 1213086.1493
1 | 2647875.8514 | 1213074.6167
2 | 2647917.1485 | 1213086.5985
3 | 2647935.7372 | 1213078.9363
4 | 2647949.6178 | 1213069.4956
5 | 2647940.1682 | 1213125.2193
6 | 2647901.0555 | 1213141.1813
7 | 2647924.2487 | 1213137.8911
8 | 2647886.0679 | 1213140.7991
9 | 2647879.9419 | 1213140.6429
10 | 2647944.2972 | 1213163.8151
11 | 2647856.8298 | 1213137.6735
12 | 2647946.6366 | 1213170.532
13 | 2647846.3468 | 1213135.3635
14 | 2647764.1832 | 1213146.8102
15 | 2647767.4407 | 1213151.3726
16 | 2647762.1872 | 1213144.0144
17 | 2647791.3495 | 1213181.1515
18 | 2647828.2226 | 1213194.6788
19 | 2647860.4939 | 1213200.5055
20 | 2647834.9204 | 1213132.474
21 | 2647819.4127 | 1213128.5524
22 | 2647852.098 | 1213249.1751
23 | 2647846.4249 | 1213247.3432
24 | 2647873.1304 | 1213252.9789
25 | 2647815.7532 | 1213233.4904
26 | 2647880.2329 | 1213216.1937
27 | 2647887.8586 | 1213255.642
28 | 2647781.9338 | 1213217.0443
29 | 2647881.9918 | 1213202.3089
30 | 2647890.3733 | 1213256.0967
31 | 2647759.8902 | 1213212.6103
32 | 2647863.5127 | 1213200.7588
33 | 2647893.5961 | 1213202.7738
34 | 2647919.634 | 1213261.378
35 | 2647926.3598 | 1213193.6623
36 | 2647908.658 | 1213200.2119
37 | 2647950.494 | 1213181.6133
38 | 2647663.7191 | 1213318.9277
39 | 2647672.0566 | 1213319.8644
40 | 2647673.5521 | 1213292.4268
41 | 2647682.1056 | 1213281.4508
42 | 2647881.9918 | 1213202.3089

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98251 | -0.1228 | 0.00562 | 0.0014085
1 | 0.98229 | -0.12437 | 0.0062666 | 0.0015706
2 | 0.98286 | -0.1203 | 0.005114 | 0.0012817
3 | 0.98336 | -0.11674 | 0.0021228 | 0.00053202
4 | 0.98382 | -0.11343 | 0 | 0
5 | 0.98643 | -0.094966 | 0 | 0
6 | 0.9846 | -0.10792 | 0.0032612 | 0.00081733
7 | 0.98552 | -0.10142 | 0.0035215 | 0.00088257
8 | 0.98409 | -0.11155 | 0.002928 | 0.00073382
9 | 0.98391 | -0.11285 | 0.0049078 | 0.00123
10 | 0.98934 | -0.074385 | 0.0038516 | 0.00096529
11 | 0.98338 | -0.11661 | 0.0024767 | 0.00062072
12 | 0.98989 | -0.070523 | 0.0035 | 0.00087718
13 | 0.98317 | -0.11807 | 0.0058092 | 0.0014559
14 | 0.9987 | -0.0091133 | 0.0015797 | 0.00039591
15 | 0.99873 | -0.0088681 | 0.00085909 | 0.00021531
16 | 0.99869 | -0.0092092 | 0.0027901 | 0.00069926
17 | 0.99902 | -0.0068624 | 0.0019199 | 0.00048116
18 | 0.99942 | -0.0040337 | 0.0037331 | 0.0009356
19 | 0.99993 | -0.00045598 | 0.0041866 | 0.0010493
20 | 0.98305 | -0.11897 | 0.0043046 | 0.0010788
21 | 0.98298 | -0.11947 | 0.0030512 | 0.00076471
22 | 0.99411 | -0.041195 | 0.0026267 | 0.00065831
23 | 0.99397 | -0.042114 | 0.0026134 | 0.00065498
24 | 0.99465 | -0.037338 | 0 | 0
25 | 0.99336 | -0.046418 | 0.004977 | 0.0012474
26 | 0.9965 | -0.024342 | 0.0019548 | 0.00048992
27 | 0.9943 | -0.039835 | 0.0045834 | 0.0011487
28 | 0.99295 | -0.049331 | 0.0013427 | 0.00033652
29 | 0.99723 | -0.01923 | 0 | 0
30 | 0.99425 | -0.040143 | 0.0066833 | 0.001675
31 | 0.99275 | -0.050776 | 0.0018933 | 0.00047451
32 | 1 | 0 | -0.12058 | -0.030163
33 | 0.9961 | -0.027084 | 0.0043124 | 0.0010808
34 | 0.99403 | -0.041723 | 0.0052603 | 0.0013184
35 | 0.99308 | -0.048177 | 0.0028544 | 0.00071538
36 | 0.99471 | -0.036797 | 0.0033025 | 0.00082769
37 | 0.99086 | -0.063746 | 0 | 0
38 | 0.99198 | -0.056223 | 0.001128 | 0.00028271
39 | 0.99199 | -0.056127 | 0 | 0
40 | 0.99204 | -0.055809 | 0.0015111 | 0.00037872
41 | 0.99209 | -0.055417 | 0.0017606 | 0.00044126
42 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.006268 | 0.0015708 | -0.0062666 | -0.0015706 | 1.3669e-06 | 2.1796e-07 | 0.0094929 | 0.009493 | 0.009493 | 0.98251 | -0.1228 | 0.98229 | -0.12437 | 3.5159
1 | -0.011888 | -0.0029793 | 0.011892 | 0.0029806 | 4.1152e-06 | 1.325e-06 | 0.018004 | 0.018004 | 0.018004 | 0.98251 | -0.1228 | 0.98286 | -0.1203 | 6.6683
2 | -0.017006 | -0.0042623 | 0.017014 | 0.0042653 | 8.3765e-06 | 2.9649e-06 | 0.025747 | 0.025747 | 0.025747 | 0.98286 | -0.1203 | 0.98336 | -0.11674 | 9.5358
3 | -0.019137 | -0.0047973 | 0.019146 | 0.0048004 | 8.7845e-06 | 3.1656e-06 | 0.028959 | 0.028959 | 0.028959 | 0.98336 | -0.11674 | 0.98382 | -0.11343 | 10.7255
4 | -0.019146 | -0.0048004 | 0.019195 | 0.0048181 | 4.9099e-05 | 1.7689e-05 | 0.028959 | 0.028958 | 0.028959 | 0.98382 | -0.11343 | 0.98643 | -0.094966 | 10.7254
5 | -0.049534 | -0.012431 | 0.049676 | 0.012485 | 0.00014192 | 5.4062e-05 | 0.074727 | 0.074727 | 0.074727 | 0.98643 | -0.094966 | 0.98934 | -0.074385 | 27.6768
6 | 0.030339 | 0.0076126 | -0.030312 | -0.0076024 | 2.7155e-05 | 1.0179e-05 | 0.045769 | 0.045769 | 0.045769 | 0.98643 | -0.094966 | 0.98552 | -0.10142 | 16.9515
7 | -0.026766 | -0.0067108 | 0.02679 | 0.0067198 | 2.4125e-05 | 8.9781e-06 | 0.040452 | 0.040452 | 0.040452 | 0.9846 | -0.10792 | 0.98552 | -0.10142 | 14.9823
8 | 0.023505 | 0.0058935 | -0.023493 | -0.0058892 | 1.1806e-05 | 4.3501e-06 | 0.035524 | 0.035524 | 0.035524 | 0.9846 | -0.10792 | 0.98409 | -0.11155 | 13.1569
9 | 0.020565 | 0.0051553 | -0.020561 | -0.005154 | 3.6976e-06 | 1.3443e-06 | 0.031096 | 0.031096 | 0.031096 | 0.98409 | -0.11155 | 0.98391 | -0.11285 | 11.5172
10 | 0.015654 | 0.003924 | -0.015645 | -0.0039211 | 8.161e-06 | 2.8426e-06 | 0.023674 | 0.023674 | 0.023674 | 0.98391 | -0.11285 | 0.98338 | -0.11661 | 8.7682
11 | -0.053527 | -0.01345 | 0.053556 | 0.013461 | 2.8776e-05 | 1.0976e-05 | 0.08052 | 0.08052 | 0.08052 | 0.98934 | -0.074385 | 0.98989 | -0.070523 | 29.8222
12 | 0.013169 | 0.0033004 | -0.013166 | -0.0032995 | 2.6622e-06 | 8.8764e-07 | 0.019927 | 0.019927 | 0.019927 | 0.98338 | -0.11661 | 0.98317 | -0.11807 | 7.3802
13 | -0.057056 | -0.014338 | 0.05711 | 0.014359 | 5.3876e-05 | 2.0571e-05 | 0.085781 | 0.085781 | 0.085781 | 0.98989 | -0.070523 | 0.99086 | -0.063746 | 31.7708
14 | 0.007357 | 0.0018436 | -0.0073561 | -0.0018434 | 9.1181e-07 | 2.0125e-07 | 0.011135 | 0.011135 | 0.011135 | 0.98317 | -0.11807 | 0.98305 | -0.11897 | 4.1239
15 | -0.0043698 | -0.0010951 | 0.0043699 | 0.0010951 | 1.4829e-07 | -1.6325e-08 | 0.0065108 | 0.0065107 | 0.0065108 | 0.9987 | -0.0091133 | 0.99873 | -0.0088681 | 2.4114
16 | 0.0027901 | 0.00069923 | -0.0027901 | -0.00069926 | 3.7044e-08 | -3.0702e-08 | 0.0041571 | 0.0041571 | 0.0041571 | 0.9987 | -0.0091133 | 0.99869 | -0.0092092 | 1.5397
17 | -0.005229 | -0.0013104 | 0.0052305 | 0.0013105 | 1.4516e-06 | 5.6595e-08 | 0.0077907 | 0.0077905 | 0.0077907 | 0.99873 | -0.0088681 | 0.99902 | -0.0068624 | 2.8854
18 | -0.0071503 | -0.0017916 | 0.0071531 | 0.0017922 | 2.7992e-06 | 5.5854e-07 | 0.01065 | 0.01065 | 0.01065 | 0.99902 | -0.0068624 | 0.99942 | -0.0040337 | 3.9445
19 | -0.010886 | -0.0027278 | 0.010892 | 0.0027294 | 5.3917e-06 | 1.6425e-06 | 0.016208 | 0.016208 | 0.016208 | 0.99942 | -0.0040337 | 0.99993 | -0.00045598 | 6.003
20 | -0.015078 | -0.0037787 | 0.015079 | 0.003779 | 9.5173e-07 | 3.2631e-07 | 0.022438 | 0.022438 | 0.022438 | 0.99993 | -0.00045598 | 1 | 0 | 8.3104
21 | 0.0030515 | 0.00076459 | -0.0030512 | -0.00076471 | 2.1294e-07 | -1.2088e-07 | 0.0046189 | 0.0046189 | 0.0046189 | 0.98305 | -0.11897 | 0.98298 | -0.11947 | 1.7107
22 | 0.015243 | 0.0038192 | -0.015241 | -0.0038186 | 1.9386e-06 | 6.6826e-07 | 0.022816 | 0.022816 | 0.022816 | 0.99411 | -0.041195 | 0.99397 | -0.042114 | 8.4504
23 | -0.01787 | -0.0044775 | 0.017879 | 0.0044809 | 9.5419e-06 | 3.3927e-06 | 0.026748 | 0.026748 | 0.026748 | 0.99411 | -0.041195 | 0.99465 | -0.037338 | 9.9066
24 | 0.012628 | 0.0031636 | -0.01262 | -0.0031611 | 7.5148e-06 | 2.4538e-06 | 0.018904 | 0.018904 | 0.018904 | 0.99397 | -0.042114 | 0.99336 | -0.046418 | 7.0014
25 | -0.034414 | -0.0086252 | 0.034476 | 0.0086486 | 6.203e-05 | 2.337e-05 | 0.051483 | 0.051483 | 0.051483 | 0.99465 | -0.037338 | 0.9965 | -0.024342 | 19.068
26 | 0.016534 | 0.0041443 | -0.016529 | -0.0041423 | 5.7144e-06 | 2.0037e-06 | 0.024736 | 0.024736 | 0.024736 | 0.99465 | -0.037338 | 0.9943 | -0.039835 | 9.1614
27 | 0.0076432 | 0.0019138 | -0.0076401 | -0.0019131 | 3.0757e-06 | 6.9634e-07 | 0.011449 | 0.011449 | 0.011449 | 0.99336 | -0.046418 | 0.99295 | -0.049331 | 4.2403
28 | -0.03643 | -0.0091385 | 0.036456 | 0.0091483 | 2.5847e-05 | 9.7588e-06 | 0.054402 | 0.054402 | 0.054402 | 0.9965 | -0.024342 | 0.99723 | -0.01923 | 20.149
29 | 0.011945 | 0.0029936 | -0.011945 | -0.0029934 | 5.096e-07 | 1.6286e-07 | 0.017877 | 0.017877 | 0.017877 | 0.9943 | -0.039835 | 0.99425 | -0.040143 | 6.621
30 | 0.0062974 | 0.0015766 | -0.0062961 | -0.0015764 | 1.2567e-06 | 1.9086e-07 | 0.0094365 | 0.0094366 | 0.0094366 | 0.99295 | -0.049331 | 0.99275 | -0.050776 | 3.495
31 | -0.10442 | -0.026276 | 0.1047 | 0.026384 | 0.00028103 | 0.00010785 | 0.15584 | 0.15584 | 0.15584 | 0.99723 | -0.01923 | 1 | 0 | 57.7194
32 | 0.06796 | 0.017128 | -0.067885 | -0.0171 | 7.4641e-05 | 2.8557e-05 | 0.10144 | 0.10144 | 0.10144 | 0.99723 | -0.01923 | 0.9961 | -0.027084 | 37.5705
33 | 0.0052615 | 0.0013184 | -0.0052603 | -0.0013184 | 1.1504e-06 | 5.695e-08 | 0.0078743 | 0.0078744 | 0.0078744 | 0.99425 | -0.040143 | 0.99403 | -0.041723 | 2.9165
34 | 0.0044028 | 0.0011019 | -0.0044 | -0.0011021 | 2.8225e-06 | -2.5656e-07 | 0.0065987 | 0.0065992 | 0.0065992 | 0.99275 | -0.050776 | 0.99209 | -0.055417 | 2.4442
35 | 0.063573 | 0.016019 | -0.063487 | -0.015986 | 8.6291e-05 | 3.299e-05 | 0.094998 | 0.094998 | 0.094998 | 0.9961 | -0.027084 | 0.99471 | -0.036797 | 35.1846
36 | -0.060089 | -0.015122 | 0.060184 | 0.015158 | 9.5603e-05 | 3.6526e-05 | 0.090058 | 0.090058 | 0.090058 | 0.99308 | -0.048177 | 0.99471 | -0.036797 | 33.3548
37 | 0.057234 | 0.014406 | -0.05711 | -0.014359 | 0.00012415 | 4.7399e-05 | 0.085781 | 0.085781 | 0.085781 | 0.99308 | -0.048177 | 0.99086 | -0.063746 | 31.7708
38 | -0.001128 | -0.00028271 | 0.001128 | 0.00028261 | 1.499e-08 | -1.0255e-07 | 0.0016921 | 0.0016921 | 0.0016921 | 0.99198 | -0.056223 | 0.99199 | -0.056127 | 0.62671
39 | -0.001128 | -0.00028261 | 0.0011281 | 0.00028227 | 4.9442e-08 | -3.383e-07 | 0.0016921 | 0.0016919 | 0.0016921 | 0.99199 | -0.056127 | 0.99204 | -0.055809 | 0.62669
40 | -0.0026392 | -0.00066099 | 0.0026393 | 0.00066085 | 1.4301e-07 | -1.3384e-07 | 0.0039585 | 0.0039585 | 0.0039585 | 0.99204 | -0.055809 | 0.99209 | -0.055417 | 1.4661

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.12446 | 0.031137

## res_load
| p_mw | q_mvar
0 | 0.00562 | 0.0014085
1 | 0.0062666 | 0.0015706
2 | 0.005114 | 0.0012817
3 | 0.0021228 | 0.00053202
4 | 0.0032612 | 0.00081733
5 | 0.0035215 | 0.00088257
6 | 0.002928 | 0.00073382
7 | 0.0049078 | 0.00123
8 | 0.0038516 | 0.00096529
9 | 0.0024767 | 0.00062072
10 | 0.0035 | 0.00087718
11 | 0.0058092 | 0.0014559
12 | 0.0015797 | 0.00039591
13 | 0.00085909 | 0.00021531
14 | 0.0027901 | 0.00069926
15 | 0.0019199 | 0.00048116
16 | 0.0037331 | 0.0009356
17 | 0.0041866 | 0.0010493
18 | 0.0043046 | 0.0010788
19 | 0.0030512 | 0.00076471
20 | 0.0026267 | 0.00065831
21 | 0.0026134 | 0.00065498
22 | 0.004977 | 0.0012474
23 | 0.0019548 | 0.00048992
24 | 0.0045834 | 0.0011487
25 | 0.0013427 | 0.00033652
26 | 0.0066833 | 0.001675
27 | 0.0018933 | 0.00047451
28 | 0.0038832 | 0.00097321
29 | 0.0043124 | 0.0010808
30 | 0.0052603 | 0.0013184
31 | 0.0028544 | 0.00071538
32 | 0.0033025 | 0.00082769
33 | 0.001128 | 0.00028271
34 | 0.0015111 | 0.00037872
35 | 0.0017606 | 0.00044126

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1