## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1121-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1121-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1121-1_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1121-1_0_3_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1121-1_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1121-1_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1121-1_0_3_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_1121-1_0_3_node_26 | 0.4 | n |  | TRUE
8 | bus_LV_1121-1_0_3_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1121-1_0_3_node_48 | 0.4 | n |  | TRUE
10 | bus_LV_1121-1_0_3_node_42 | 0.4 | n |  | TRUE
11 | bus_LV_1121-1_0_3_node_103 | 0.4 | n |  | TRUE
12 | bus_LV_1121-1_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1121-1_0_3_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1121-1_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1121-1_0_3_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_1121-1_0_3_node_40 | 0.4 | n |  | TRUE
17 | bus_LV_1121-1_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1121-1_0_3_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1121-1_0_3_node_20 | 0.4 | n |  | TRUE
20 | bus_LV_1121-1_0_3_node_44 | 0.4 | n |  | TRUE
21 | bus_LV_1121-1_0_3_node_22 | 0.4 | n |  | TRUE
22 | bus_LV_1121-1_0_3_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1121-1_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1121-1_0_3_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_1121-1_0_3_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_1121-1_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1121-1_0_3_node_31 | 0.4 | n |  | TRUE
28 | bus_LV_1121-1_0_3_node_32 | 0.4 | n |  | TRUE
29 | bus_LV_1121-1_0_3_node_46 | 0.4 | n |  | TRUE
30 | bus_LV_1121-1_0_3_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_1121-1_0_3_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_1121-1_0_3_node_104 | 0.4 | n |  | TRUE
33 | bus_LV_1121-1_0_3_node_41 | 0.4 | n |  | TRUE
34 | bus_LV_1121-1_0_3_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_1121-1_0_3_node_45 | 0.4 | n |  | TRUE
36 | bus_LV_1121-1_0_3_node_47 | 0.4 | n |  | TRUE
37 | bus_LV_1121-1_0_3_node_49 | 0.4 | n |  | TRUE
38 | bus_MV_128_0_node_273 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1121-1_0_3_load_0 | 0 | 0.0013481 | 0.00033787 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1121-1_0_3_load_1 | 1 | 0.0029355 | 0.0007357 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1121-1_0_3_load_28 | 6 | 0.0050691 | 0.0012704 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1121-1_0_3_load_26 | 7 | 0.0011615 | 0.00029111 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1121-1_0_3_load_48 | 9 | 0.00027171 | 6.8097e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1121-1_0_3_load_42 | 10 | 0.00095713 | 0.00023988 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1121-1_0_3_load_103 | 11 | 0.012045 | 0.0030189 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1121-1_0_3_load_38 | 15 | 0.0022084 | 0.00055349 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1121-1_0_3_load_40 | 16 | 0.0034087 | 0.0008543 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1121-1_0_3_load_29 | 18 | 0.0012061 | 0.00030228 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1121-1_0_3_load_44 | 20 | 0.0005928 | 0.00014857 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1121-1_0_3_load_22 | 21 | 0.0010257 | 0.00025706 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1121-1_0_3_load_30 | 24 | 0.00038002 | 9.5242e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1121-1_0_3_load_27 | 26 | 0.012287 | 0.0030795 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1121-1_0_3_load_31 | 27 | 0.00042122 | 0.00010557 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1121-1_0_3_load_46 | 29 | 0.011166 | 0.0027984 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1121-1_0_3_load_37 | 30 | 0.0014888 | 0.00037314 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1121-1_0_3_load_39 | 31 | 0.0053111 | 0.0013311 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1121-1_0_3_load_104 | 32 | 0.0065878 | 0.0016511 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1121-1_0_3_load_41 | 33 | 0.0011847 | 0.00029692 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1121-1_0_3_load_43 | 34 | 0.00068528 | 0.00017175 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1121-1_0_3_load_47 | 36 | 0.0015863 | 0.00039755 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1121-1_0_3_load_49 | 37 | 0.0014013 | 0.0003512 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1121-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0038822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1121-1_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.053277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1121-1_0_3_line_2 | NAYY 4x150 SE | 2 | 5 | 0.047698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1121-1_0_3_line_3 | NAYY 4x150 SE | 2 | 3 | 0.036037 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1121-1_0_3_line_4 | NAYY 4x150 SE | 3 | 4 | 0.20451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1121-1_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.065262 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1121-1_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0030428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1121-1_0_3_line_7 | NAYY 4x150 SE | 5 | 11 | 0.0064075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1121-1_0_3_line_8 | NAYY 4x150 SE | 6 | 17 | 0.032392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1121-1_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.028256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1121-1_0_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.038823 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1121-1_0_3_line_11 | NAYY 4x150 SE | 10 | 14 | 0.033332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1121-1_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.058488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1121-1_0_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.16458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1121-1_0_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.12417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1121-1_0_3_line_15 | NAYY 4x150 SE | 12 | 15 | 0.4042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1121-1_0_3_line_16 | NAYY 4x150 SE | 13 | 19 | 0.63055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1121-1_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.099767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1121-1_0_3_line_18 | NAYY 4x150 SE | 15 | 30 | 0.001349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1121-1_0_3_line_19 | NAYY 4x150 SE | 16 | 33 | 0.02394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1121-1_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.069736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1121-1_0_3_line_21 | NAYY 4x150 SE | 18 | 23 | 0.056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1121-1_0_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.056666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1121-1_0_3_line_23 | NAYY 4x150 SE | 20 | 34 | 0.028082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1121-1_0_3_line_24 | NAYY 4x150 SE | 21 | 22 | 0.051514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1121-1_0_3_line_25 | NAYY 4x150 SE | 22 | 23 | 0.015312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1121-1_0_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.038964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1121-1_0_3_line_27 | NAYY 4x150 SE | 24 | 25 | 0.031701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1121-1_0_3_line_28 | NAYY 4x150 SE | 25 | 26 | 0.04549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1121-1_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.057322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1121-1_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.2747 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1121-1_0_3_line_31 | NAYY 4x150 SE | 29 | 35 | 0.097512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1121-1_0_3_line_32 | NAYY 4x150 SE | 30 | 31 | 0.0056559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1121-1_0_3_line_33 | NAYY 4x150 SE | 31 | 32 | 0.25604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1121-1_0_3_line_34 | NAYY 4x150 SE | 34 | 35 | 0.056198 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1121-1_0_3_line_35 | NAYY 4x150 SE | 35 | 36 | 0.028865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1121-1_0_3_line_36 | NAYY 4x150 SE | 36 | 37 | 0.040637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1121-1_0_3_trafo_21 | 0.25 MVA 20/0.4 kV | 38 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23
0 | 2642317.0097 | 1221539.8412 | 2642313.2311 | 1221540.7321
1 | 2642291.4882 | 1221502.572 | 2642296.5718 | 1221516.283 | 2642302.4941 | 1221543.2634 | 2642313.2311 | 1221540.7321
2 | 2642244.7351 | 1221512.6687 | 2642291.4882 | 1221502.572
3 | 2642326.6459 | 1221494.2165 | 2642291.4882 | 1221502.572
4 | 2642326.6459 | 1221494.2165 | 2642424.1449 | 1221472.6745 | 2642459.1698 | 1221467.0427 | 2642470.8037 | 1221465.2578 | 2642481.1807 | 1221464.2089 | 2642487.2839 | 1221463.5965 | 2642494.9793 | 1221463.0844 | 2642497.2847 | 1221496.1429
5 | 2642497.2847 | 1221496.1429 | 2642506.179 | 1221496.6399 | 2642512.709 | 1221495.7415 | 2642553.6049 | 1221493.3208 | 2642562.3837 | 1221493.858
6 | 2642497.2847 | 1221496.1429 | 2642497.8789 | 1221499.1272
7 | 2642244.7351 | 1221512.6687 | 2642238.4797 | 1221514.0564
8 | 2642594.6503 | 1221496.527 | 2642584.0477 | 1221495.1838 | 2642562.3837 | 1221493.858
9 | 2641976.5083 | 1221364.4182 | 2641971.3529 | 1221343.5471 | 2641970.1797 | 1221336.8917
10 | 2641976.5083 | 1221364.4182 | 2641977.8033 | 1221369.0189 | 2641979.0472 | 1221373.3525 | 2641987.8792 | 1221401.5363
11 | 2641997.8465 | 1221433.3432 | 2641987.8792 | 1221401.5363
12 | 2642181.2038 | 1221525.8712 | 2642202.0897 | 1221521.1607 | 2642237.3048 | 1221514.3171 | 2642238.4797 | 1221514.0564
13 | 2642019.3402 | 1221554.3562 | 2642038.607 | 1221553.3359 | 2642074.7742 | 1221548.0101 | 2642117.4064 | 1221540.2621 | 2642181.2038 | 1221525.8712
14 | 2641997.8465 | 1221433.3432 | 2642018.9011 | 1221504.7678 | 2642020.8402 | 1221529.8965 | 2642019.7776 | 1221546.121 | 2642019.7008 | 1221547.3212 | 2642019.3402 | 1221554.3562
15 | 2642019.3402 | 1221554.3562 | 2641990.9428 | 1221553.9781 | 2641952.4078 | 1221546.5467 | 2641624.395 | 1221471.2212
16 | 2642181.2038 | 1221525.8712 | 2642185.2728 | 1221544.7002 | 2642174.2185 | 1221549.3025 | 2642144.953 | 1221576.2006 | 2642141.6012 | 1221582.4918 | 2642140.8477 | 1221590.3579 | 2642144.754 | 1221596.8227 | 2642167.5403 | 1221610.8033 | 2642196.267 | 1221626.7607 | 2642225.37 | 1221648.4687 | 2642249.4511 | 1221671.2753 | 2642276.3093 | 1221703.5407 | 2642293.1726 | 1221737.5696 | 2642312.0441 | 1221768.6223 | 2642341.482 | 1221810.2897 | 2642363.725 | 1221837.553 | 2642398.6295 | 1221870.9102 | 2642430.3806 | 1221898.6083 | 2642453.8074 | 1221920.366 | 2642470.0202 | 1221940.0823 | 2642479.1626 | 1221957.8137 | 2642481.0716 | 1221966.6548 | 2642481.5025 | 1221976.4304 | 2642479.3523 | 1221995.0263
17 | 2641997.8465 | 1221433.3432 | 2641953.6432 | 1221447.596 | 2641958.7376 | 1221464.1974 | 2641924.2267 | 1221474.2928
18 | 2641623.0802 | 1221470.9193 | 2641624.395 | 1221471.2212
19 | 2641901.2495 | 1221481.0142 | 2641924.2267 | 1221474.2928
20 | 2642594.6503 | 1221496.527 | 2642593.0835 | 1221515.1492 | 2642591.0467 | 1221530.5439 | 2642588.0979 | 1221537.6938 | 2642587.4716 | 1221565.4721
21 | 2642589.8129 | 1221621.412 | 2642587.3648 | 1221570.2081 | 2642587.4716 | 1221565.4721
22 | 2642479.3523 | 1221995.0263 | 2642471.9991 | 1221997.631 | 2642432.6362 | 1222004.6883 | 2642424.4623 | 1222008.1452
23 | 2642398.5986 | 1222019.0838 | 2642424.4623 | 1222008.1452
24 | 2642590.5456 | 1221636.7042 | 2642591.6675 | 1221662.272 | 2642592.9265 | 1221688.1633
25 | 2642590.5456 | 1221636.7042 | 2642589.8129 | 1221621.412
26 | 2642589.8129 | 1221621.412 | 2642550.8924 | 1221623.2582
27 | 2642519.5273 | 1221627.6806 | 2642522.8677 | 1221627.282 | 2642533.3613 | 1221625.8115 | 2642546.8346 | 1221623.4507 | 2642550.8924 | 1221623.2582
28 | 2642519.5273 | 1221627.6806 | 2642517.0402 | 1221607.3618 | 2642513.0481 | 1221582.6628
29 | 2642073.2177 | 1221910.1612 | 2642067.9287 | 1221930.8808 | 2642052.2612 | 1221954.0731 | 2642044.7208 | 1221951.555
30 | 2642342.7701 | 1221963.0686 | 2642073.2177 | 1221910.1612
31 | 2642342.7701 | 1221963.0686 | 2642328.5347 | 1221967.1254 | 2642323.8005 | 1221969.4154 | 2642321.5715 | 1221973.5576 | 2642321.4925 | 1221979.3383 | 2642342.31 | 1222033.1297 | 2642346.9701 | 1222041.2455
32 | 2641617.5677 | 1221469.6534 | 2641623.0802 | 1221470.9193
33 | 2641617.5677 | 1221469.6534 | 2641405.5393 | 1221613.1852
34 | 2642346.9701 | 1222041.2455 | 2642356.8723 | 1222037.4913 | 2642385.8177 | 1222024.4893 | 2642398.5986 | 1222019.0838
35 | 2642327.1276 | 1222060.5272 | 2642338.0044 | 1222044.5059 | 2642346.9701 | 1222041.2455
36 | 2642327.1276 | 1222060.5272 | 2642310.6026 | 1222097.6525

## bus_geodata
| x | y | coords
0 | 2642317.0097 | 1221539.8412
1 | 2642313.2311 | 1221540.7321
2 | 2642291.4882 | 1221502.572
3 | 2642326.6459 | 1221494.2165
4 | 2642497.2847 | 1221496.1429
5 | 2642244.7351 | 1221512.6687
6 | 2642562.3837 | 1221493.858
7 | 2642497.8789 | 1221499.1272
8 | 2641976.5083 | 1221364.4182
9 | 2641970.1797 | 1221336.8917
10 | 2641987.8792 | 1221401.5363
11 | 2642238.4797 | 1221514.0564
12 | 2642019.3402 | 1221554.3562
13 | 2642181.2038 | 1221525.8712
14 | 2641997.8465 | 1221433.3432
15 | 2641624.395 | 1221471.2212
16 | 2641924.2267 | 1221474.2928
17 | 2642594.6503 | 1221496.527
18 | 2642587.4716 | 1221565.4721
19 | 2642479.3523 | 1221995.0263
20 | 2642424.4623 | 1222008.1452
21 | 2642592.9265 | 1221688.1633
22 | 2642590.5456 | 1221636.7042
23 | 2642589.8129 | 1221621.412
24 | 2642550.8924 | 1221623.2582
25 | 2642519.5273 | 1221627.6806
26 | 2642513.0481 | 1221582.6628
27 | 2642044.7208 | 1221951.555
28 | 2642073.2177 | 1221910.1612
29 | 2642342.7701 | 1221963.0686
30 | 2641623.0802 | 1221470.9193
31 | 2641617.5677 | 1221469.6534
32 | 2641405.5393 | 1221613.1852
33 | 2641901.2495 | 1221481.0142
34 | 2642398.5986 | 1222019.0838
35 | 2642346.9701 | 1222041.2455
36 | 2642327.1276 | 1222060.5272
37 | 2642310.6026 | 1222097.6525
38 | 2642244.7351 | 1221512.6687

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99451 | -0.038212 | 0.0013481 | 0.00033787
1 | 0.99452 | -0.038159 | 0.0029355 | 0.0007357
2 | 0.99485 | -0.035855 | 0 | 0
3 | 0.99374 | -0.043564 | 0 | 0
4 | 0.98747 | -0.087615 | 0 | 0
5 | 0.9966 | -0.02362 | 0 | 0
6 | 0.98558 | -0.101 | 0.0050691 | 0.0012704
7 | 0.98747 | -0.087651 | 0.0011615 | 0.00029111
8 | 0.9938 | -0.043392 | 0 | 0
9 | 0.99379 | -0.04347 | 0.00027171 | 6.8097e-05
10 | 0.99381 | -0.043284 | 0.00095713 | 0.00023988
11 | 0.99684 | -0.021979 | 0.012045 | 0.0030189
12 | 0.99491 | -0.035536 | 0 | 0
13 | 1 | 0 | -0.076529 | -0.019072
14 | 0.99387 | -0.042867 | 0 | 0
15 | 0.98579 | -0.099866 | 0.0022084 | 0.00055349
16 | 0.99322 | -0.047508 | 0.0034087 | 0.0008543
17 | 0.98488 | -0.10598 | 0 | 0
18 | 0.98337 | -0.1167 | 0.0012061 | 0.00030228
19 | 0.98548 | -0.10181 | 0 | 0
20 | 0.98418 | -0.11109 | 0.0005928 | 0.00014857
21 | 0.98215 | -0.12535 | 0.0010257 | 0.00025706
22 | 0.98223 | -0.1248 | 0 | 0
23 | 0.98225 | -0.12464 | 0 | 0
24 | 0.98154 | -0.12975 | 0.00038002 | 9.5242e-05
25 | 0.98097 | -0.13379 | 0 | 0
26 | 0.98016 | -0.13959 | 0.012287 | 0.0030795
27 | 0.98052 | -0.13726 | 0.00042122 | 0.00010557
28 | 0.98055 | -0.137 | 0 | 0
29 | 0.98072 | -0.13575 | 0.011166 | 0.0027984
30 | 0.98576 | -0.10005 | 0.0014888 | 0.00037314
31 | 0.98566 | -0.10074 | 0.0053111 | 0.0013311
32 | 0.98322 | -0.11815 | 0.0065878 | 0.0016511
33 | 0.99317 | -0.047795 | 0.0011847 | 0.00029692
34 | 0.98355 | -0.11552 | 0.00068528 | 0.00017175
35 | 0.98236 | -0.12401 | 0 | 0
36 | 0.98224 | -0.1249 | 0.0015863 | 0.00039755
37 | 0.98216 | -0.12549 | 0.0014013 | 0.0003512
38 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0013481 | -0.00033787 | 0.0013481 | 0.00033782 | 9.8562e-09 | -4.6584e-08 | 0.0020171 | 0.0020171 | 0.0020171 | 0.99451 | -0.038212 | 0.99452 | -0.038159 | 0.74707
1 | -0.0042836 | -0.0010735 | 0.004285 | 0.0010734 | 1.3656e-06 | -1.6633e-07 | 0.0064092 | 0.0064089 | 0.0064092 | 0.99452 | -0.038159 | 0.99485 | -0.035855 | 2.3738
2 | -0.02568 | -0.0064625 | 0.025723 | 0.0064788 | 4.3931e-05 | 1.6276e-05 | 0.038419 | 0.038419 | 0.038419 | 0.99485 | -0.035855 | 0.9966 | -0.02362 | 14.2292
3 | 0.021395 | 0.0053891 | -0.021372 | -0.0053807 | 2.3041e-05 | 8.3946e-06 | 0.03201 | 0.03201 | 0.03201 | 0.99485 | -0.035855 | 0.99374 | -0.043564 | 11.8556
4 | 0.021372 | 0.0053807 | -0.021241 | -0.0053331 | 0.00013076 | 4.7661e-05 | 0.03201 | 0.032011 | 0.032011 | 0.99374 | -0.043564 | 0.98747 | -0.087615 | 11.8559
5 | 0.020079 | 0.005042 | -0.020042 | -0.0050285 | 3.7291e-05 | 1.351e-05 | 0.030261 | 0.030261 | 0.030261 | 0.98747 | -0.087615 | 0.98558 | -0.101 | 11.2078
6 | 0.0011615 | 0.00029107 | -0.0011615 | -0.00029111 | 5.817e-09 | -3.6688e-08 | 0.0017503 | 0.0017503 | 0.0017503 | 0.98747 | -0.087615 | 0.98747 | -0.087651 | 0.64827
7 | -0.025723 | -0.0064788 | 0.025729 | 0.006481 | 5.9014e-06 | 2.1862e-06 | 0.038419 | 0.038419 | 0.038419 | 0.9966 | -0.02362 | 0.99684 | -0.021979 | 14.2291
8 | 0.014973 | 0.0037581 | -0.014962 | -0.0037545 | 1.0331e-05 | 3.5609e-06 | 0.022608 | 0.022608 | 0.022608 | 0.98558 | -0.101 | 0.98488 | -0.10598 | 8.3733
9 | 0.00027171 | 6.7732e-05 | -0.00027171 | -6.8097e-05 | 2.9175e-09 | -3.6499e-07 | 0.00040671 | 0.00040684 | 0.00040684 | 0.9938 | -0.043392 | 0.99379 | -0.04347 | 0.15068
10 | -0.00027171 | -6.7732e-05 | 0.00027172 | 6.7231e-05 | 4.0055e-09 | -5.015e-07 | 0.00040671 | 0.00040653 | 0.00040671 | 0.9938 | -0.043392 | 0.99381 | -0.043284 | 0.15063
11 | -0.0012288 | -0.00030711 | 0.0012289 | 0.00030671 | 7.0383e-08 | -4.0485e-07 | 0.0018396 | 0.0018395 | 0.0018396 | 0.99381 | -0.043284 | 0.99387 | -0.042867 | 0.68134
12 | -0.037775 | -0.0094998 | 0.037891 | 0.0095437 | 0.00011609 | 4.3885e-05 | 0.056399 | 0.056399 | 0.056399 | 0.99684 | -0.021979 | 1 | 0 | 20.8886
13 | -0.021585 | -0.0054189 | 0.021692 | 0.0054579 | 0.00010705 | 3.9025e-05 | 0.032286 | 0.032285 | 0.032286 | 0.99491 | -0.035536 | 1 | 0 | 11.9579
14 | 0.0058312 | 0.0014581 | -0.0058253 | -0.0014575 | 5.8924e-06 | 6.5547e-07 | 0.0087202 | 0.0087208 | 0.0087208 | 0.99491 | -0.035536 | 0.99387 | -0.042867 | 3.2299
15 | 0.015754 | 0.0039608 | -0.015614 | -0.0039121 | 0.00014008 | 4.8677e-05 | 0.023566 | 0.023568 | 0.023568 | 0.99491 | -0.035536 | 0.98579 | -0.099866 | 8.7288
16 | 0.016146 | 0.0040698 | -0.015919 | -0.0039905 | 0.00022731 | 7.9274e-05 | 0.024034 | 0.024037 | 0.024037 | 1 | 0 | 0.98548 | -0.10181 | 8.9026
17 | 0.0045964 | 0.0011508 | -0.0045935 | -0.0011509 | 2.9481e-06 | -1.5815e-07 | 0.0068813 | 0.0068818 | 0.0068818 | 0.99387 | -0.042867 | 0.99322 | -0.047508 | 2.5488
18 | 0.013405 | 0.0033586 | -0.013405 | -0.0033585 | 3.4465e-07 | 1.1536e-07 | 0.020234 | 0.020234 | 0.020234 | 0.98579 | -0.099866 | 0.98576 | -0.10005 | 7.4942
19 | 0.0011848 | 0.00029663 | -0.0011847 | -0.00029692 | 4.7065e-08 | -2.9172e-07 | 0.0017749 | 0.001775 | 0.001775 | 0.99322 | -0.047508 | 0.99317 | -0.047795 | 0.65742
20 | 0.014962 | 0.0037545 | -0.01494 | -0.0037468 | 2.2242e-05 | 7.6684e-06 | 0.022608 | 0.022608 | 0.022608 | 0.98488 | -0.10598 | 0.98337 | -0.1167 | 8.3734
21 | 0.013734 | 0.0034446 | -0.013719 | -0.0034395 | 1.5094e-05 | 5.0956e-06 | 0.020783 | 0.020783 | 0.020783 | 0.98337 | -0.1167 | 0.98225 | -0.12464 | 7.6975
22 | 0.015919 | 0.0039905 | -0.015899 | -0.0039834 | 2.0431e-05 | 7.1369e-06 | 0.024037 | 0.024037 | 0.024037 | 0.98548 | -0.10181 | 0.98418 | -0.11109 | 8.9027
23 | 0.015306 | 0.0038348 | -0.015296 | -0.0038315 | 9.3838e-06 | 3.2525e-06 | 0.023141 | 0.023141 | 0.023141 | 0.98418 | -0.11109 | 0.98355 | -0.11552 | 8.5708
24 | -0.0010257 | -0.00025706 | 0.0010257 | 0.00025643 | 7.761e-08 | -6.2213e-07 | 0.0015539 | 0.0015537 | 0.0015539 | 0.98215 | -0.12535 | 0.98223 | -0.1248 | 0.57553
25 | -0.0010257 | -0.00025643 | 0.0010258 | 0.00025625 | 2.3064e-08 | -1.8494e-07 | 0.0015537 | 0.0015536 | 0.0015537 | 0.98223 | -0.1248 | 0.98225 | -0.12464 | 0.57545
26 | 0.012693 | 0.0031832 | -0.012684 | -0.0031802 | 8.9908e-06 | 2.9652e-06 | 0.01923 | 0.01923 | 0.01923 | 0.98225 | -0.12464 | 0.98154 | -0.12975 | 7.1222
27 | 0.012304 | 0.003085 | -0.012297 | -0.0030828 | 6.8833e-06 | 2.247e-06 | 0.018654 | 0.018654 | 0.018654 | 0.98154 | -0.12975 | 0.98097 | -0.13379 | 6.9088
28 | 0.012297 | 0.0030828 | -0.012287 | -0.0030795 | 9.8774e-06 | 3.2252e-06 | 0.018654 | 0.018654 | 0.018654 | 0.98097 | -0.13379 | 0.98016 | -0.13959 | 6.9089
29 | -0.00042122 | -0.00010557 | 0.00042124 | 0.00010485 | 1.461e-08 | -7.1742e-07 | 0.00063924 | 0.00063898 | 0.00063924 | 0.98052 | -0.13726 | 0.98055 | -0.137 | 0.23676
30 | -0.00042124 | -0.00010485 | 0.00042131 | 0.00010141 | 6.9852e-08 | -3.4387e-06 | 0.00063898 | 0.00063777 | 0.00063898 | 0.98055 | -0.137 | 0.98072 | -0.13575 | 0.23666
31 | -0.011587 | -0.0028999 | 0.011606 | 0.0029059 | 1.8804e-05 | 5.9996e-06 | 0.017579 | 0.017579 | 0.017579 | 0.98072 | -0.13575 | 0.98236 | -0.12401 | 6.5109
32 | 0.011916 | 0.0029854 | -0.011915 | -0.002985 | 1.1418e-06 | 3.6707e-07 | 0.017987 | 0.017987 | 0.017987 | 0.98576 | -0.10005 | 0.98566 | -0.10074 | 6.6618
33 | 0.0066037 | 0.0016539 | -0.0065878 | -0.0016511 | 1.588e-05 | 2.8522e-06 | 0.0099689 | 0.0099701 | 0.0099701 | 0.98566 | -0.10074 | 0.98322 | -0.11815 | 3.6926
34 | 0.014611 | 0.0036598 | -0.014594 | -0.0036539 | 1.7135e-05 | 5.8779e-06 | 0.022104 | 0.022105 | 0.022105 | 0.98355 | -0.11552 | 0.98236 | -0.12401 | 8.1869
35 | 0.002988 | 0.00074806 | -0.0029877 | -0.00074828 | 3.6894e-07 | -2.235e-07 | 0.0045258 | 0.0045259 | 0.0045259 | 0.98236 | -0.12401 | 0.98224 | -0.1249 | 1.6763
36 | 0.0014014 | 0.00035073 | -0.0014013 | -0.0003512 | 1.1428e-07 | -4.7036e-07 | 0.0021229 | 0.002123 | 0.002123 | 0.98224 | -0.1249 | 0.98216 | -0.12549 | 0.78631

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.076529 | 0.019072

## res_load
| p_mw | q_mvar
0 | 0.0013481 | 0.00033787
1 | 0.0029355 | 0.0007357
2 | 0.0050691 | 0.0012704
3 | 0.0011615 | 0.00029111
4 | 0.00027171 | 6.8097e-05
5 | 0.00095713 | 0.00023988
6 | 0.012045 | 0.0030189
7 | 0.0022084 | 0.00055349
8 | 0.0034087 | 0.0008543
9 | 0.0012061 | 0.00030228
10 | 0.0005928 | 0.00014857
11 | 0.0010257 | 0.00025706
12 | 0.00038002 | 9.5242e-05
13 | 0.012287 | 0.0030795
14 | 0.00042122 | 0.00010557
15 | 0.011166 | 0.0027984
16 | 0.0014888 | 0.00037314
17 | 0.0053111 | 0.0013311
18 | 0.0065878 | 0.0016511
19 | 0.0011847 | 0.00029692
20 | 0.00068528 | 0.00017175
21 | 0.0015863 | 0.00039755
22 | 0.0014013 | 0.0003512

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1