## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1122-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1122-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1122-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1122-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1122-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1122-1_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1122-1_0_4_node_38 | 0.4 | n |  | TRUE
7 | bus_LV_1122-1_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1122-1_0_4_node_39 | 0.4 | n |  | TRUE
9 | bus_LV_1122-1_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1122-1_0_4_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1122-1_0_4_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1122-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1122-1_0_4_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_1122-1_0_4_node_44 | 0.4 | n |  | TRUE
15 | bus_LV_1122-1_0_4_node_71 | 0.4 | n |  | TRUE
16 | bus_LV_1122-1_0_4_node_70 | 0.4 | n |  | TRUE
17 | bus_LV_1122-1_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1122-1_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1122-1_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1122-1_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1122-1_0_4_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_1122-1_0_4_node_42 | 0.4 | n |  | TRUE
23 | bus_LV_1122-1_0_4_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_1122-1_0_4_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_1122-1_0_4_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1122-1_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_1122-1_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1122-1_0_4_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1122-1_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1122-1_0_4_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1122-1_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_1122-1_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1122-1_0_4_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1122-1_0_4_node_59 | 0.4 | n |  | TRUE
35 | bus_LV_1122-1_0_4_node_29 | 0.4 | n |  | TRUE
36 | bus_LV_1122-1_0_4_node_66 | 0.4 | n |  | TRUE
37 | bus_LV_1122-1_0_4_node_60 | 0.4 | n |  | TRUE
38 | bus_LV_1122-1_0_4_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_1122-1_0_4_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1122-1_0_4_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_1122-1_0_4_node_27 | 0.4 | n |  | TRUE
42 | bus_LV_1122-1_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_1122-1_0_4_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_1122-1_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_1122-1_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_1122-1_0_4_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_1122-1_0_4_node_45 | 0.4 | n |  | TRUE
48 | bus_LV_1122-1_0_4_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_1122-1_0_4_node_35 | 0.4 | n |  | TRUE
50 | bus_LV_1122-1_0_4_node_36 | 0.4 | n |  | TRUE
51 | bus_LV_1122-1_0_4_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_1122-1_0_4_node_41 | 0.4 | n |  | TRUE
53 | bus_LV_1122-1_0_4_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_1122-1_0_4_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_1122-1_0_4_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_1122-1_0_4_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_1122-1_0_4_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_1122-1_0_4_node_48 | 0.4 | n |  | TRUE
59 | bus_LV_1122-1_0_4_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_1122-1_0_4_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_1122-1_0_4_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_1122-1_0_4_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_1122-1_0_4_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_1122-1_0_4_node_88 | 0.4 | n |  | TRUE
65 | bus_LV_1122-1_0_4_node_67 | 0.4 | n |  | TRUE
66 | bus_LV_1122-1_0_4_node_61 | 0.4 | n |  | TRUE
67 | bus_LV_1122-1_0_4_node_87 | 0.4 | n |  | TRUE
68 | bus_LV_1122-1_0_4_node_68 | 0.4 | n |  | TRUE
69 | bus_LV_1122-1_0_4_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_1122-1_0_4_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_1122-1_0_4_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_1122-1_0_4_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_1122-1_0_4_node_74 | 0.4 | n |  | TRUE
74 | bus_LV_1122-1_0_4_node_75 | 0.4 | n |  | TRUE
75 | bus_LV_1122-1_0_4_node_77 | 0.4 | n |  | TRUE
76 | bus_LV_1122-1_0_4_node_73 | 0.4 | n |  | TRUE
77 | bus_LV_1122-1_0_4_node_84 | 0.4 | n |  | TRUE
78 | bus_LV_1122-1_0_4_node_72 | 0.4 | n |  | TRUE
79 | bus_LV_1122-1_0_4_node_79 | 0.4 | n |  | TRUE
80 | bus_LV_1122-1_0_4_node_76 | 0.4 | n |  | TRUE
81 | bus_LV_1122-1_0_4_node_83 | 0.4 | n |  | TRUE
82 | bus_LV_1122-1_0_4_node_80 | 0.4 | n |  | TRUE
83 | bus_LV_1122-1_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_1122-1_0_4_node_82 | 0.4 | n |  | TRUE
85 | bus_LV_1122-1_0_4_node_89 | 0.4 | n |  | TRUE
86 | bus_MV_129_0_node_267 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1122-1_0_4_load_0 | 0 | 0.00058319 | 0.00014616 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1122-1_0_4_load_1 | 1 | 0.0016318 | 0.00040897 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1122-1_0_4_load_3 | 3 | 0.00894 | 0.0022406 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1122-1_0_4_load_4 | 4 | 0.0026129 | 0.00065485 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1122-1_0_4_load_5 | 5 | 0.01503 | 0.0037668 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1122-1_0_4_load_38 | 6 | 0.0015493 | 0.0003883 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1122-1_0_4_load_11 | 10 | 0.0031338 | 0.00078539 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1122-1_0_4_load_9 | 11 | 0.0062515 | 0.0015668 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1122-1_0_4_load_10 | 13 | 0.00070005 | 0.00017545 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1122-1_0_4_load_44 | 14 | 0.00096042 | 0.0002407 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1122-1_0_4_load_71 | 15 | 0.00053106 | 0.0001331 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1122-1_0_4_load_70 | 16 | 0.00030068 | 7.5359e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1122-1_0_4_load_12 | 17 | 0.0032287 | 0.0008092 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1122-1_0_4_load_14 | 19 | 0.0081917 | 0.002053 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1122-1_0_4_load_15 | 20 | 0.0044972 | 0.0011271 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1122-1_0_4_load_23 | 21 | 0.0035279 | 0.00088418 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1122-1_0_4_load_42 | 22 | 0.0092326 | 0.0023139 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1122-1_0_4_load_43 | 23 | 0.010326 | 0.0025878 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1122-1_0_4_load_40 | 24 | 0.015894 | 0.0039834 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1122-1_0_4_load_24 | 25 | 0.0008654 | 0.00021689 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1122-1_0_4_load_16 | 26 | 0.0013954 | 0.00034972 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1122-1_0_4_load_17 | 27 | 0.0029873 | 0.00074869 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1122-1_0_4_load_19 | 29 | 0.00097382 | 0.00024406 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1122-1_0_4_load_21 | 31 | 0.0010789 | 0.00027041 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1122-1_0_4_load_59 | 34 | 0.001902 | 0.00047668 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1122-1_0_4_load_29 | 35 | 0.005488 | 0.0013754 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1122-1_0_4_load_66 | 36 | 0.00070997 | 0.00017793 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1122-1_0_4_load_25 | 39 | 0.0017053 | 0.00042739 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1122-1_0_4_load_26 | 40 | 0.0022886 | 0.00057357 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1122-1_0_4_load_30 | 42 | 0.0012251 | 0.00030704 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1122-1_0_4_load_31 | 43 | 0.0021514 | 0.00053918 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1122-1_0_4_load_32 | 44 | 0.00041108 | 0.00010303 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1122-1_0_4_load_34 | 45 | 0.0014488 | 0.00036311 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1122-1_0_4_load_64 | 46 | 0.00048869 | 0.00012248 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1122-1_0_4_load_45 | 47 | 0.0025798 | 0.00064657 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1122-1_0_4_load_33 | 48 | 0.0033056 | 0.00082846 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1122-1_0_4_load_35 | 49 | 0.0055073 | 0.0013802 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1122-1_0_4_load_36 | 50 | 0.00084514 | 0.00021181 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1122-1_0_4_load_41 | 52 | 0.0048239 | 0.001209 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1122-1_0_4_load_51 | 53 | 0.002737 | 0.00068595 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1122-1_0_4_load_52 | 54 | 0.0015655 | 0.00039236 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1122-1_0_4_load_50 | 56 | 0.0027881 | 0.00069876 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1122-1_0_4_load_47 | 57 | 0.0015713 | 0.00039381 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1122-1_0_4_load_48 | 58 | 0.0014625 | 0.00036653 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1122-1_0_4_load_54 | 59 | 0.0011322 | 0.00028375 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1122-1_0_4_load_55 | 60 | 0.00044184 | 0.00011074 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1122-1_0_4_load_56 | 61 | 0.0007376 | 0.00018486 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1122-1_0_4_load_58 | 63 | 0.001112 | 0.0002787 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1122-1_0_4_load_88 | 64 | 0.0037038 | 0.00092825 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1122-1_0_4_load_67 | 65 | 0.00061943 | 0.00015524 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1122-1_0_4_load_61 | 66 | 0.0024558 | 0.00061549 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1122-1_0_4_load_87 | 67 | 0.0012042 | 0.00030181 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1122-1_0_4_load_62 | 69 | 0.00084151 | 0.0002109 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1122-1_0_4_load_63 | 70 | 0.00077651 | 0.00019461 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1122-1_0_4_load_65 | 71 | 0.0013337 | 0.00033425 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1122-1_0_4_load_69 | 72 | 0.0010286 | 0.0002578 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1122-1_0_4_load_75 | 74 | 0.00092111 | 0.00023085 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1122-1_0_4_load_73 | 76 | 0.0002779 | 6.9649e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1122-1_0_4_load_84 | 77 | 0.0010284 | 0.00025773 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1122-1_0_4_load_72 | 78 | 0.00036331 | 9.1055e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1122-1_0_4_load_79 | 79 | 0.00078937 | 0.00019784 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1122-1_0_4_load_76 | 80 | 0.00068918 | 0.00017272 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1122-1_0_4_load_83 | 81 | 0.001011 | 0.00025338 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1122-1_0_4_load_80 | 82 | 0.0040704 | 0.0010201 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1122-1_0_4_load_82 | 84 | 0.0057281 | 0.0014356 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1122-1_0_4_load_89 | 85 | 0.0023711 | 0.00059426 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1122-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0025142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1122-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.015917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1122-1_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.032739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1122-1_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.025504 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
4 | LV_1122-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.01144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1122-1_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0097316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
6 | LV_1122-1_0_4_line_6 | NAYY 4x150 SE | 5 | 7 | 0.042813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1122-1_0_4_line_7 | NAYY 4x150 SE | 6 | 8 | 0.02422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1122-1_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.031956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1122-1_0_4_line_9 | NAYY 4x150 SE | 8 | 55 | 0.046566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1122-1_0_4_line_10 | NAYY 4x150 SE | 8 | 51 | 0.018666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1122-1_0_4_line_11 | NAYY 4x150 SE | 9 | 10 | 0.032667 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1122-1_0_4_line_12 | NAYY 4x150 SE | 9 | 11 | 0.019009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1122-1_0_4_line_13 | NAYY 4x150 SE | 10 | 14 | 0.029545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1122-1_0_4_line_14 | NAYY 4x150 SE | 11 | 12 | 0.014829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1122-1_0_4_line_15 | NAYY 4x150 SE | 12 | 13 | 0.034896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1122-1_0_4_line_16 | NAYY 4x150 SE | 13 | 15 | 0.029678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1122-1_0_4_line_17 | NAYY 4x150 SE | 15 | 16 | 0.010802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1122-1_0_4_line_18 | NAYY 4x150 SE | 16 | 78 | 0.016329 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1122-1_0_4_line_19 | NAYY 4x150 SE | 17 | 18 | 0.032657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1122-1_0_4_line_20 | NAYY 4x150 SE | 17 | 19 | 0.054085 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1122-1_0_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.013874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1122-1_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.042109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1122-1_0_4_line_23 | NAYY 4x150 SE | 21 | 25 | 0.0035233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1122-1_0_4_line_24 | NAYY 4x150 SE | 22 | 23 | 0.026273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1122-1_0_4_line_25 | NAYY 4x150 SE | 22 | 24 | 0.022971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1122-1_0_4_line_26 | NAYY 4x150 SE | 24 | 52 | 0.00069858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1122-1_0_4_line_27 | NAYY 4x150 SE | 25 | 39 | 0.0003267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1122-1_0_4_line_28 | NAYY 4x150 SE | 26 | 27 | 0.0040486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1122-1_0_4_line_29 | NAYY 4x150 SE | 26 | 28 | 0.022269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1122-1_0_4_line_30 | NAYY 4x150 SE | 27 | 29 | 0.020545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1122-1_0_4_line_31 | NAYY 4x150 SE | 28 | 30 | 0.036609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1122-1_0_4_line_32 | NAYY 4x150 SE | 28 | 31 | 0.029521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1122-1_0_4_line_33 | NAYY 4x150 SE | 29 | 32 | 0.030116 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1122-1_0_4_line_34 | NAYY 4x150 SE | 30 | 33 | 0.023213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1122-1_0_4_line_35 | NAYY 4x150 SE | 30 | 34 | 0.0020378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1122-1_0_4_line_36 | NAYY 4x150 SE | 32 | 35 | 0.0071706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1122-1_0_4_line_37 | NAYY 4x150 SE | 33 | 36 | 0.023715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1122-1_0_4_line_38 | NAYY 4x150 SE | 34 | 37 | 0.013872 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1122-1_0_4_line_39 | NAYY 4x150 SE | 35 | 38 | 0.024291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1122-1_0_4_line_40 | NAYY 4x150 SE | 36 | 46 | 0.023177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1122-1_0_4_line_41 | NAYY 4x150 SE | 37 | 66 | 0.032694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1122-1_0_4_line_42 | NAYY 4x150 SE | 37 | 62 | 0.059156 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1122-1_0_4_line_43 | NAYY 4x150 SE | 38 | 47 | 0.037073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1122-1_0_4_line_44 | NAYY 4x150 SE | 39 | 40 | 0.0092055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1122-1_0_4_line_45 | NAYY 4x150 SE | 40 | 41 | 0.021132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1122-1_0_4_line_46 | NAYY 4x150 SE | 41 | 42 | 0.018852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1122-1_0_4_line_47 | NAYY 4x150 SE | 41 | 43 | 0.031044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1122-1_0_4_line_48 | NAYY 4x150 SE | 42 | 44 | 0.0058212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1122-1_0_4_line_49 | NAYY 4x150 SE | 43 | 45 | 0.016509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1122-1_0_4_line_50 | NAYY 4x150 SE | 44 | 48 | 0.0052787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1122-1_0_4_line_51 | NAYY 4x150 SE | 45 | 49 | 0.028582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1122-1_0_4_line_52 | NAYY 4x150 SE | 46 | 69 | 0.025811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1122-1_0_4_line_53 | NAYY 4x150 SE | 48 | 50 | 0.010592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1122-1_0_4_line_54 | NAYY 4x150 SE | 49 | 52 | 0.045809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1122-1_0_4_line_55 | NAYY 4x150 SE | 50 | 51 | 0.028343 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_1122-1_0_4_line_56 | NAYY 4x150 SE | 51 | 53 | 0.018674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1122-1_0_4_line_57 | NAYY 4x150 SE | 53 | 54 | 0.038007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1122-1_0_4_line_58 | NAYY 4x150 SE | 55 | 56 | 0.048264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1122-1_0_4_line_59 | NAYY 4x150 SE | 55 | 57 | 0.025273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1122-1_0_4_line_60 | NAYY 4x150 SE | 57 | 58 | 0.022423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1122-1_0_4_line_61 | NAYY 4x150 SE | 59 | 60 | 0.026976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1122-1_0_4_line_62 | NAYY 4x150 SE | 59 | 61 | 0.0041839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1122-1_0_4_line_63 | NAYY 4x150 SE | 60 | 62 | 0.014654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1122-1_0_4_line_64 | NAYY 4x150 SE | 61 | 63 | 0.03702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1122-1_0_4_line_65 | NAYY 4x150 SE | 62 | 64 | 0.033247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1122-1_0_4_line_66 | NAYY 4x150 SE | 63 | 65 | 0.0029373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1122-1_0_4_line_67 | NAYY 4x150 SE | 64 | 67 | 0.0046558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1122-1_0_4_line_68 | NAYY 4x150 SE | 65 | 68 | 0.051723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1122-1_0_4_line_69 | NAYY 4x150 SE | 67 | 85 | 0.021841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1122-1_0_4_line_70 | NAYY 4x150 SE | 68 | 73 | 0.034033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1122-1_0_4_line_71 | NAYY 4x150 SE | 68 | 74 | 0.015459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1122-1_0_4_line_72 | NAYY 4x150 SE | 69 | 70 | 0.017023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1122-1_0_4_line_73 | NAYY 4x150 SE | 70 | 71 | 0.018904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1122-1_0_4_line_74 | NAYY 4x150 SE | 71 | 72 | 0.0008618 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1122-1_0_4_line_75 | NAYY 4x150 SE | 73 | 75 | 0.01839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1122-1_0_4_line_76 | NAYY 4x150 SE | 73 | 76 | 0.040127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1122-1_0_4_line_77 | NAYY 4x150 SE | 74 | 77 | 0.044477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1122-1_0_4_line_78 | NAYY 4x150 SE | 75 | 79 | 0.033561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1122-1_0_4_line_79 | NAYY 4x150 SE | 75 | 80 | 0.016281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1122-1_0_4_line_80 | NAYY 4x150 SE | 76 | 78 | 0.014209 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1122-1_0_4_line_81 | NAYY 4x150 SE | 77 | 81 | 0.0027668 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1122-1_0_4_line_82 | NAYY 4x150 SE | 81 | 83 | 0.0078434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1122-1_0_4_line_83 | NAYY 4x150 SE | 82 | 83 | 0.027069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1122-1_0_4_line_84 | NAYY 4x150 SE | 82 | 84 | 0.01783 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1122-1_0_4_trafo_7 | 0.25 MVA 20/0.4 kV | 86 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2633730.4282 | 1225496.8487 | 2633730.584 | 1225499.3581
1 | 2633731.5748 | 1225515.244 | 2633731.4774 | 1225513.7092 | 2633730.8798 | 1225504.1223 | 2633730.584 | 1225499.3581
2 | 2633731.5748 | 1225515.244 | 2633723.839 | 1225515.934 | 2633698.927 | 1225517.6714
3 | 2633731.5748 | 1225515.244 | 2633756.9753 | 1225512.9507
4 | 2633687.5148 | 1225518.4674 | 2633698.927 | 1225517.6714
5 | 2633756.9753 | 1225512.9507 | 2633766.6674 | 1225512.0756
6 | 2633644.806 | 1225521.4461 | 2633687.5148 | 1225518.4674
7 | 2633790.1512 | 1225513.2969 | 2633786.8279 | 1225511.1879 | 2633783.3672 | 1225510.5679 | 2633766.6674 | 1225512.0756
8 | 2633644.806 | 1225521.4461 | 2633645.3706 | 1225531.5331 | 2633644.9426 | 1225536.1891 | 2633642.6847 | 1225540.0342 | 2633639.8197 | 1225542.6529 | 2633634.3157 | 1225545.4569 | 2633631.7045 | 1225546.0981
9 | 2633790.1512 | 1225513.2969 | 2633785.322 | 1225497.3599 | 2633772.4826 | 1225470.3265
10 | 2633790.1512 | 1225513.2969 | 2633790.8959 | 1225516.9922 | 2633793.2305 | 1225531.7032
11 | 2633631.7045 | 1225546.0981 | 2633627.4337 | 1225554.7125 | 2633618.1752 | 1225574.0385 | 2633616.6509 | 1225574.5948
12 | 2633631.7045 | 1225546.0981 | 2633626.5103 | 1225545.0681 | 2633619.6189 | 1225539.8595 | 2633617.7097 | 1225535.1575
13 | 2633590.0175 | 1225587.1017 | 2633600.8784 | 1225580.5449 | 2633609.2349 | 1225577.3011 | 2633616.6509 | 1225574.5948
14 | 2633614.701 | 1225520.7647 | 2633615.791 | 1225530.4322 | 2633617.7097 | 1225535.1575
15 | 2633614.701 | 1225520.7647 | 2633610.161 | 1225519.316 | 2633602.8917 | 1225515.2392 | 2633597.7575 | 1225511.6303 | 2633591.5439 | 1225505.8474 | 2633589.9376 | 1225499.0009
16 | 2633589.9376 | 1225499.0009 | 2633592.1296 | 1225492.0535 | 2633600.6337 | 1225481.484 | 2633607.0046 | 1225475.3748
17 | 2633613.6555 | 1225466.9265 | 2633613.6555 | 1225466.9265 | 2633609.5205 | 1225472.9623 | 2633607.0046 | 1225475.3748
18 | 2633613.6555 | 1225466.9265 | 2633613.6426 | 1225459.811 | 2633609.8988 | 1225451.3922
19 | 2633784.0669 | 1225685.2101 | 2633758.7589 | 1225686.2117 | 2633753.2986 | 1225681.3223
20 | 2633699.2142 | 1225681.4163 | 2633753.2986 | 1225681.3223
21 | 2633784.0669 | 1225685.2101 | 2633779.1289 | 1225672.2444
22 | 2633770.6033 | 1225631.3942 | 2633770.3571 | 1225636.6254 | 2633771.4639 | 1225647.3159 | 2633775.037 | 1225661.5002 | 2633779.1289 | 1225672.2444
23 | 2633770.769 | 1225627.8748 | 2633770.6033 | 1225631.3942
24 | 2633661.4221 | 1225642.5832 | 2633658.9702 | 1225644.0997 | 2633640.016 | 1225651.4972 | 2633637.4097 | 1225653.0687
25 | 2633681.6808 | 1225631.7863 | 2633666.1129 | 1225639.6819 | 2633661.4221 | 1225642.5832
26 | 2633682.3038 | 1225631.4703 | 2633681.6808 | 1225631.7863
27 | 2633770.769 | 1225627.8748 | 2633770.7843 | 1225627.5484
28 | 2633470.0183 | 1225649.0478 | 2633470.6643 | 1225649.5535 | 2633472.9707 | 1225651.8123
29 | 2633452.4837 | 1225635.3207 | 2633470.0183 | 1225649.0478
30 | 2633477.9553 | 1225667.1197 | 2633473.2975 | 1225663.8769 | 2633477.3209 | 1225656.0726 | 2633472.9707 | 1225651.8123
31 | 2633473.1955 | 1225605.1411 | 2633457.1469 | 1225629.6657 | 2633452.4837 | 1225635.3207
32 | 2633452.4837 | 1225635.3207 | 2633448.3014 | 1225640.378 | 2633439.6085 | 1225650.9133 | 2633437.8542 | 1225652.8491 | 2633433.3551 | 1225657.7965
33 | 2633504.488 | 1225658.7602 | 2633498.8447 | 1225662.1194 | 2633488.5924 | 1225668.221 | 2633481.7012 | 1225669.7276 | 2633477.9553 | 1225667.1197
34 | 2633487.3976 | 1225623.2206 | 2633480.2627 | 1225611.4512 | 2633473.1955 | 1225605.1411
35 | 2633473.1955 | 1225605.1411 | 2633474.0196 | 1225603.2773
36 | 2633504.488 | 1225658.7602 | 2633507.9631 | 1225665.0325
37 | 2633487.3976 | 1225623.2206 | 2633500.5983 | 1225619.8817 | 2633505.3688 | 1225616.7288 | 2633507.2706 | 1225612.7826
38 | 2633479.6295 | 1225590.5907 | 2633474.0196 | 1225603.2773
39 | 2633520.6333 | 1225685.7561 | 2633508.4426 | 1225665.8979 | 2633507.9631 | 1225665.0325
40 | 2633510.5981 | 1225589.9644 | 2633510.5981 | 1225589.9644 | 2633508.2756 | 1225610.6971 | 2633507.2706 | 1225612.7826
41 | 2633479.6295 | 1225590.5907 | 2633466.1146 | 1225560.808
42 | 2633496.7899 | 1225534.1866 | 2633493.912 | 1225549.9021 | 2633485.2497 | 1225577.8702 | 2633479.6295 | 1225590.5907
43 | 2633520.6333 | 1225685.7561 | 2633526.403 | 1225681.5083 | 2633531.3148 | 1225676.1327 | 2633543.2736 | 1225656.9243
44 | 2633771.6439 | 1225618.4052 | 2633771.0811 | 1225621.2425 | 2633770.7843 | 1225627.5484
45 | 2633775.7553 | 1225597.6771 | 2633771.6439 | 1225618.4052
46 | 2633775.7553 | 1225597.6771 | 2633780.315 | 1225584.9397 | 2633782.2359 | 1225579.9749
47 | 2633775.7553 | 1225597.6771 | 2633756.6176 | 1225595.9342 | 2633744.8651 | 1225594.6065
48 | 2633782.2359 | 1225579.9749 | 2633784.3365 | 1225574.5459
49 | 2633744.8651 | 1225594.6065 | 2633728.4603 | 1225592.7532
50 | 2633786.2413 | 1225569.6228 | 2633784.3365 | 1225574.5459
51 | 2633700.1095 | 1225589.263 | 2633702.2266 | 1225589.7894 | 2633728.4603 | 1225592.7532
52 | 2633518.9921 | 1225565.5964 | 2633514.4017 | 1225576.789 | 2633510.5981 | 1225589.9644
53 | 2633786.2413 | 1225569.6228 | 2633790.0634 | 1225559.7443
54 | 2633700.1095 | 1225589.263 | 2633682.3038 | 1225631.4703
55 | 2633793.2305 | 1225531.7032 | 2633792.7303 | 1225545.0528 | 2633790.9467 | 1225557.4613 | 2633790.0634 | 1225559.7443
56 | 2633793.2305 | 1225531.7032 | 2633811.86 | 1225532.9982
57 | 2633849.8029 | 1225534.6317 | 2633837.9895 | 1225534.8146 | 2633811.86 | 1225532.9982
58 | 2633772.4826 | 1225470.3265 | 2633763.8249 | 1225455.7909 | 2633747.0258 | 1225429.3279
59 | 2633772.4826 | 1225470.3265 | 2633796.9687 | 1225464.0681
60 | 2633796.9687 | 1225464.0681 | 2633818.693 | 1225458.5156
61 | 2633505.1682 | 1225493.4533 | 2633502.9677 | 1225500.5233 | 2633499.435 | 1225519.7733
62 | 2633505.1682 | 1225493.4533 | 2633506.4116 | 1225489.4584
63 | 2633496.7899 | 1225534.1866 | 2633499.435 | 1225519.7733
64 | 2633525.0047 | 1225458.1262 | 2633515.8024 | 1225467.976 | 2633509.213 | 1225480.4575 | 2633506.4116 | 1225489.4584
65 | 2633496.7899 | 1225534.1866 | 2633485.5558 | 1225532.8671 | 2633466.0896 | 1225522.7565
66 | 2633525.0047 | 1225458.1262 | 2633525.5564 | 1225457.5357 | 2633527.1861 | 1225456.1655
67 | 2633461.9579 | 1225520.6105 | 2633466.0896 | 1225522.7565
68 | 2633566.7767 | 1225422.8803 | 2633527.1861 | 1225456.1655
69 | 2633442.5798 | 1225510.5346 | 2633459.8049 | 1225519.4922 | 2633461.9579 | 1225520.6105
70 | 2633566.7767 | 1225422.8803 | 2633572.1151 | 1225418.5188 | 2633577.446 | 1225414.1573 | 2633592.6449 | 1225400.6905
71 | 2633566.7767 | 1225422.8803 | 2633557.2363 | 1225410.7163
72 | 2633518.9921 | 1225565.5964 | 2633525.4516 | 1225549.8462
73 | 2633532.7699 | 1225532.4161 | 2633527.5443 | 1225544.7437 | 2633525.4516 | 1225549.8462
74 | 2633533.1063 | 1225531.6226 | 2633532.7699 | 1225532.4161
75 | 2633592.6449 | 1225400.6905 | 2633597.9024 | 1225393.2156 | 2633603.2892 | 1225385.6748
76 | 2633592.6449 | 1225400.6905 | 2633599.3273 | 1225409.3889 | 2633606.0335 | 1225437.7653
77 | 2633557.2363 | 1225410.7163 | 2633551.4229 | 1225403.3043 | 2633537.4063 | 1225391.2515 | 2633525.9133 | 1225379.313
78 | 2633603.2892 | 1225385.6748 | 2633609.5212 | 1225366.7208 | 2633610.8653 | 1225353.1786
79 | 2633603.2892 | 1225385.6748 | 2633608.332 | 1225389.3832 | 2633614.1862 | 1225393.0518 | 2633617.0353 | 1225394.3061
80 | 2633609.8988 | 1225451.3922 | 2633608.5226 | 1225448.2975 | 2633606.0335 | 1225437.7653
81 | 2633525.9133 | 1225379.313 | 2633525.9133 | 1225379.313 | 2633523.5117 | 1225377.9392
82 | 2633516.7407 | 1225373.9804 | 2633522.3015 | 1225377.247 | 2633523.5117 | 1225377.9392
83 | 2633516.7407 | 1225373.9804 | 2633513.4624 | 1225379.9878 | 2633511.6052 | 1225384.0353 | 2633505.2263 | 1225398.4596
84 | 2633498.0149 | 1225414.7663 | 2633505.2263 | 1225398.4596

## bus_geodata
| x | y | coords
0 | 2633730.584 | 1225499.3581
1 | 2633730.4282 | 1225496.8487
2 | 2633731.5748 | 1225515.244
3 | 2633698.927 | 1225517.6714
4 | 2633756.9753 | 1225512.9507
5 | 2633687.5148 | 1225518.4674
6 | 2633766.6674 | 1225512.0756
7 | 2633644.806 | 1225521.4461
8 | 2633790.1512 | 1225513.2969
9 | 2633631.7045 | 1225546.0981
10 | 2633616.6509 | 1225574.5948
11 | 2633617.7097 | 1225535.1575
12 | 2633614.701 | 1225520.7647
13 | 2633589.9376 | 1225499.0009
14 | 2633590.0175 | 1225587.1017
15 | 2633607.0046 | 1225475.3748
16 | 2633613.6555 | 1225466.9265
17 | 2633753.2986 | 1225681.3223
18 | 2633784.0669 | 1225685.2101
19 | 2633699.2142 | 1225681.4163
20 | 2633779.1289 | 1225672.2444
21 | 2633770.6033 | 1225631.3942
22 | 2633661.4221 | 1225642.5832
23 | 2633637.4097 | 1225653.0687
24 | 2633681.6808 | 1225631.7863
25 | 2633770.769 | 1225627.8748
26 | 2633470.0183 | 1225649.0478
27 | 2633472.9707 | 1225651.8123
28 | 2633452.4837 | 1225635.3207
29 | 2633477.9553 | 1225667.1197
30 | 2633473.1955 | 1225605.1411
31 | 2633433.3551 | 1225657.7965
32 | 2633504.488 | 1225658.7602
33 | 2633487.3976 | 1225623.2206
34 | 2633474.0196 | 1225603.2773
35 | 2633507.9631 | 1225665.0325
36 | 2633507.2706 | 1225612.7826
37 | 2633479.6295 | 1225590.5907
38 | 2633520.6333 | 1225685.7561
39 | 2633770.7843 | 1225627.5484
40 | 2633771.6439 | 1225618.4052
41 | 2633775.7553 | 1225597.6771
42 | 2633782.2359 | 1225579.9749
43 | 2633744.8651 | 1225594.6065
44 | 2633784.3365 | 1225574.5459
45 | 2633728.4603 | 1225592.7532
46 | 2633510.5981 | 1225589.9644
47 | 2633543.2736 | 1225656.9243
48 | 2633786.2413 | 1225569.6228
49 | 2633700.1095 | 1225589.263
50 | 2633790.0634 | 1225559.7443
51 | 2633793.2305 | 1225531.7032
52 | 2633682.3038 | 1225631.4703
53 | 2633811.86 | 1225532.9982
54 | 2633849.8029 | 1225534.6317
55 | 2633772.4826 | 1225470.3265
56 | 2633747.0258 | 1225429.3279
57 | 2633796.9687 | 1225464.0681
58 | 2633818.693 | 1225458.5156
59 | 2633505.1682 | 1225493.4533
60 | 2633499.435 | 1225519.7733
61 | 2633506.4116 | 1225489.4584
62 | 2633496.7899 | 1225534.1866
63 | 2633525.0047 | 1225458.1262
64 | 2633466.0896 | 1225522.7565
65 | 2633527.1861 | 1225456.1655
66 | 2633466.1146 | 1225560.808
67 | 2633461.9579 | 1225520.6105
68 | 2633566.7767 | 1225422.8803
69 | 2633518.9921 | 1225565.5964
70 | 2633525.4516 | 1225549.8462
71 | 2633532.7699 | 1225532.4161
72 | 2633533.1063 | 1225531.6226
73 | 2633592.6449 | 1225400.6905
74 | 2633557.2363 | 1225410.7163
75 | 2633603.2892 | 1225385.6748
76 | 2633606.0335 | 1225437.7653
77 | 2633525.9133 | 1225379.313
78 | 2633609.8988 | 1225451.3922
79 | 2633610.8653 | 1225353.1786
80 | 2633617.0353 | 1225394.3061
81 | 2633523.5117 | 1225377.9392
82 | 2633505.2263 | 1225398.4596
83 | 2633516.7407 | 1225373.9804
84 | 2633498.0149 | 1225414.7663
85 | 2633442.5798 | 1225510.5346
86 | 2633644.806 | 1225521.4461

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99026 | -0.067485 | 0.00058319 | 0.00014616
1 | 0.99025 | -0.067526 | 0.0016318 | 0.00040897
2 | 0.99031 | -0.067126 | 0 | 0
3 | 0.9926 | -0.051161 | 0.00894 | 0.0022406
4 | 0.98856 | -0.079324 | 0.0026129 | 0.00065485
5 | 0.99348 | -0.045082 | 0.01503 | 0.0037668
6 | 0.98791 | -0.08386 | 0.0015493 | 0.0003883
7 | 0.99721 | -0.019197 | 0 | 0
8 | 0.98633 | -0.094982 | 0 | 0
9 | 1 | 0 | -0.18641 | -0.046964
10 | 0.99981 | -0.0013365 | 0.0031338 | 0.00078539
11 | 0.9984 | -0.011044 | 0.0062515 | 0.0015668
12 | 0.99728 | -0.018754 | 0 | 0
13 | 0.99464 | -0.036964 | 0.00070005 | 0.00017545
14 | 0.99977 | -0.0016203 | 0.00096042 | 0.0002407
15 | 0.99243 | -0.052316 | 0.00053106 | 0.0001331
16 | 0.99164 | -0.057863 | 0.00030068 | 7.5359e-05
17 | 0.97677 | -0.16278 | 0.0032287 | 0.0008092
18 | 0.97731 | -0.15887 | 0 | 0
19 | 0.97612 | -0.16742 | 0.0081917 | 0.002053
20 | 0.97754 | -0.15722 | 0.0044972 | 0.0011271
21 | 0.97852 | -0.15022 | 0.0035279 | 0.00088418
22 | 0.97096 | -0.20432 | 0.0092326 | 0.0023139
23 | 0.97056 | -0.20719 | 0.010326 | 0.0025878
24 | 0.97162 | -0.19956 | 0.015894 | 0.0039834
25 | 0.97862 | -0.1495 | 0.0008654 | 0.00021689
26 | 0.97355 | -0.18603 | 0.0013954 | 0.00034972
27 | 0.97348 | -0.18654 | 0.0029873 | 0.00074869
28 | 0.97399 | -0.18288 | 0 | 0
29 | 0.97321 | -0.1885 | 0.00097382 | 0.00024406
30 | 0.97477 | -0.17729 | 0 | 0
31 | 0.97394 | -0.18321 | 0.0010789 | 0.00027041
32 | 0.97285 | -0.19106 | 0 | 0
33 | 0.97459 | -0.17856 | 0 | 0
34 | 0.97483 | -0.17687 | 0.001902 | 0.00047668
35 | 0.97277 | -0.19167 | 0.005488 | 0.0013754
36 | 0.97441 | -0.17985 | 0.00070997 | 0.00017793
37 | 0.97526 | -0.17372 | 0 | 0
38 | 0.97267 | -0.19234 | 0 | 0
39 | 0.97863 | -0.14944 | 0.0017053 | 0.00042739
40 | 0.97892 | -0.14732 | 0.0022886 | 0.00057357
41 | 0.97967 | -0.14197 | 0 | 0
42 | 0.98171 | -0.12755 | 0.0012251 | 0.00030704
43 | 0.97743 | -0.15796 | 0.0021514 | 0.00053918
44 | 0.98235 | -0.12304 | 0.00041108 | 0.00010303
45 | 0.97628 | -0.16612 | 0.0014488 | 0.00036311
46 | 0.97426 | -0.18094 | 0.00048869 | 0.00012248
47 | 0.97253 | -0.19335 | 0.0025798 | 0.00064657
48 | 0.98293 | -0.11893 | 0.0033056 | 0.00082846
49 | 0.97436 | -0.17985 | 0.0055073 | 0.0013802
50 | 0.98354 | -0.11462 | 0.00084514 | 0.00021181
51 | 0.98518 | -0.10302 | 0 | 0
52 | 0.97165 | -0.1993 | 0.0048239 | 0.001209
53 | 0.98507 | -0.10384 | 0.002737 | 0.00068595
54 | 0.98498 | -0.10446 | 0.0015655 | 0.00039236
55 | 0.98594 | -0.09777 | 0 | 0
56 | 0.98574 | -0.099153 | 0.0027881 | 0.00069876
57 | 0.98582 | -0.098558 | 0.0015713 | 0.00039381
58 | 0.98578 | -0.098895 | 0.0014625 | 0.00036653
59 | 0.97927 | -0.14506 | 0.0011322 | 0.00028375
60 | 0.97802 | -0.15401 | 0.00044184 | 0.00011074
61 | 0.97947 | -0.14363 | 0.0007376 | 0.00018486
62 | 0.97735 | -0.15881 | 0 | 0
63 | 0.98129 | -0.13068 | 0.001112 | 0.0002787
64 | 0.97699 | -0.16134 | 0.0037038 | 0.00092825
65 | 0.98144 | -0.12962 | 0.00061943 | 0.00015524
66 | 0.97515 | -0.17456 | 0.0024558 | 0.00061549
67 | 0.97697 | -0.16151 | 0.0012042 | 0.00030181
68 | 0.98411 | -0.11069 | 0 | 0
69 | 0.97411 | -0.18202 | 0.00084151 | 0.0002109
70 | 0.97403 | -0.18258 | 0.00077651 | 0.00019461
71 | 0.97397 | -0.18305 | 0.0013337 | 0.00033425
72 | 0.97396 | -0.18306 | 0.0010286 | 0.0002578
73 | 0.9865 | -0.093829 | 0 | 0
74 | 0.98383 | -0.11273 | 0.00092111 | 0.00023085
75 | 0.98646 | -0.094109 | 0 | 0
76 | 0.98941 | -0.073444 | 0.0002779 | 6.9649e-05
77 | 0.98306 | -0.11816 | 0.0010284 | 0.00025773
78 | 0.99044 | -0.066214 | 0.00036331 | 9.1055e-05
79 | 0.98643 | -0.094382 | 0.00078937 | 0.00019784
80 | 0.98645 | -0.094224 | 0.00068918 | 0.00017272
81 | 0.98302 | -0.11847 | 0.001011 | 0.00025338
82 | 0.98253 | -0.12201 | 0.0040704 | 0.0010201
83 | 0.98291 | -0.11927 | 0 | 0
84 | 0.98238 | -0.12306 | 0.0057281 | 0.0014356
85 | 0.97689 | -0.16205 | 0.0023711 | 0.00059426
86 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0016318 | 0.00040894 | -0.0016318 | -0.00040897 | 9.433e-09 | -2.8717e-08 | 0.0024521 | 0.0024521 | 0.0024521 | 0.99026 | -0.067485 | 0.99025 | -0.067526 | 0.90817
1 | -0.002215 | -0.0005551 | 0.0022151 | 0.00055494 | 1.1003e-07 | -1.6246e-07 | 0.0033284 | 0.0033283 | 0.0033284 | 0.99026 | -0.067485 | 0.99031 | -0.067126 | 1.2327
2 | -0.097292 | -0.024549 | 0.09751 | 0.024633 | 0.00021847 | 8.3184e-05 | 0.14625 | 0.14625 | 0.14625 | 0.99031 | -0.067126 | 0.9926 | -0.051161 | 27.083
3 | 0.095077 | 0.023994 | -0.094914 | -0.023933 | 0.00016253 | 6.1858e-05 | 0.14292 | 0.14292 | 0.14292 | 0.99031 | -0.067126 | 0.98856 | -0.079324 | 26.4667
4 | -0.10645 | -0.026873 | 0.10654 | 0.026908 | 9.0973e-05 | 3.4694e-05 | 0.15965 | 0.15965 | 0.15965 | 0.9926 | -0.051161 | 0.99348 | -0.045082 | 29.5648
5 | 0.092301 | 0.023278 | -0.092243 | -0.023255 | 5.8652e-05 | 2.2309e-05 | 0.13899 | 0.13899 | 0.13899 | 0.98856 | -0.079324 | 0.98791 | -0.08386 | 25.7383
6 | -0.12157 | -0.030675 | 0.12201 | 0.030844 | 0.00044324 | 0.00016936 | 0.18216 | 0.18216 | 0.18216 | 0.99348 | -0.045082 | 0.99721 | -0.019197 | 33.7335
7 | 0.090693 | 0.022867 | -0.090552 | -0.022814 | 0.00014111 | 5.3654e-05 | 0.13665 | 0.13665 | 0.13665 | 0.98791 | -0.08386 | 0.98633 | -0.094982 | 25.3062
8 | -0.12201 | -0.030844 | 0.12235 | 0.03097 | 0.00033084 | 0.00012641 | 0.18216 | 0.18216 | 0.18216 | 0.99721 | -0.019197 | 1 | 0 | 33.7334
9 | 0.005825 | 0.0014585 | -0.0058228 | -0.0014582 | 2.2438e-06 | 2.6891e-07 | 0.0087874 | 0.0087876 | 0.0087876 | 0.98633 | -0.094982 | 0.98594 | -0.09777 | 3.2547
10 | 0.084727 | 0.021355 | -0.084632 | -0.021319 | 9.5218e-05 | 3.6146e-05 | 0.12787 | 0.12787 | 0.12787 | 0.98633 | -0.094982 | 0.98518 | -0.10302 | 23.679
11 | 0.004095 | 0.0010256 | -0.0040942 | -0.0010257 | 7.5681e-07 | -1.3741e-07 | 0.0060931 | 0.0060933 | 0.0060933 | 1 | 0 | 0.99981 | -0.0013365 | 2.2568
12 | 0.059166 | 0.014968 | -0.059074 | -0.014933 | 9.2039e-05 | 3.5151e-05 | 0.088089 | 0.088089 | 0.088089 | 1 | 0 | 0.9984 | -0.011044 | 32.6255
13 | 0.00096046 | 0.00024033 | -0.00096042 | -0.0002407 | 3.7667e-08 | -3.7296e-07 | 0.0014293 | 0.0014294 | 0.0014294 | 0.99981 | -0.0013365 | 0.99977 | -0.0016203 | 0.52942
14 | 0.052822 | 0.013366 | -0.052765 | -0.013344 | 5.7415e-05 | 2.1889e-05 | 0.078771 | 0.078772 | 0.078772 | 0.9984 | -0.011044 | 0.99728 | -0.018754 | 29.1747
15 | 0.052765 | 0.013344 | -0.05263 | -0.013293 | 0.00013512 | 5.1513e-05 | 0.078772 | 0.078772 | 0.078772 | 0.99728 | -0.018754 | 0.99464 | -0.036964 | 29.1747
16 | 0.05193 | 0.013117 | -0.051818 | -0.013075 | 0.00011187 | 4.2644e-05 | 0.077724 | 0.077725 | 0.077725 | 0.99464 | -0.036964 | 0.99243 | -0.052316 | 28.7869
17 | 0.051287 | 0.012942 | -0.051247 | -0.012926 | 3.989e-05 | 1.5203e-05 | 0.076928 | 0.076928 | 0.076928 | 0.99243 | -0.052316 | 0.99164 | -0.057863 | 28.492
18 | 0.050946 | 0.012851 | -0.050886 | -0.012828 | 5.9596e-05 | 2.2711e-05 | 0.076477 | 0.076477 | 0.076477 | 0.99164 | -0.057863 | 0.99044 | -0.066214 | 28.3249
19 | -0.011426 | -0.0028636 | 0.011432 | 0.0028656 | 6.174e-06 | 1.9656e-06 | 0.017406 | 0.017406 | 0.017406 | 0.97677 | -0.16278 | 0.97731 | -0.15887 | 6.4467
20 | 0.008197 | 0.0020544 | -0.0081917 | -0.002053 | 5.2627e-06 | 1.3476e-06 | 0.012487 | 0.012488 | 0.012488 | 0.97677 | -0.16278 | 0.97612 | -0.16742 | 4.625
21 | -0.011432 | -0.0028656 | 0.011435 | 0.0028664 | 2.6229e-06 | 8.3493e-07 | 0.017406 | 0.017406 | 0.017406 | 0.97731 | -0.15887 | 0.97754 | -0.15722 | 6.4466
22 | -0.015932 | -0.0039935 | 0.015947 | 0.0039989 | 1.5454e-05 | 5.4154e-06 | 0.024252 | 0.024251 | 0.024252 | 0.97754 | -0.15722 | 0.97852 | -0.15022 | 8.9821
23 | -0.019475 | -0.0048831 | 0.019477 | 0.0048838 | 1.9284e-06 | 6.9742e-07 | 0.029616 | 0.029616 | 0.029616 | 0.97852 | -0.15022 | 0.97862 | -0.1495 | 10.969
24 | 0.01033 | 0.0025891 | -0.010326 | -0.0025878 | 4.1086e-06 | 1.2554e-06 | 0.015831 | 0.015831 | 0.015831 | 0.97096 | -0.20432 | 0.97056 | -0.20719 | 5.8632
25 | -0.019562 | -0.004903 | 0.019575 | 0.0049077 | 1.2883e-05 | 4.6707e-06 | 0.02998 | 0.02998 | 0.02998 | 0.97096 | -0.20432 | 0.97162 | -0.19956 | 11.1036
26 | -0.035469 | -0.008891 | 0.03547 | 0.0088915 | 1.2863e-06 | 4.8606e-07 | 0.054321 | 0.054321 | 0.054321 | 0.97162 | -0.19956 | 0.97165 | -0.1993 | 20.1188
27 | -0.020342 | -0.0051007 | 0.020343 | 0.0051008 | 1.9505e-07 | 7.0916e-08 | 0.030932 | 0.030932 | 0.030932 | 0.97862 | -0.1495 | 0.97863 | -0.14944 | 11.4563
28 | 0.012036 | 0.0030161 | -0.012036 | -0.0030158 | 8.5501e-07 | 2.7851e-07 | 0.018397 | 0.018397 | 0.018397 | 0.97355 | -0.18603 | 0.97348 | -0.18654 | 6.8136
29 | -0.013432 | -0.0033658 | 0.013438 | 0.0033678 | 5.8564e-06 | 1.9755e-06 | 0.020529 | 0.020529 | 0.020529 | 0.97355 | -0.18603 | 0.97399 | -0.18288 | 7.6035
30 | 0.0090482 | 0.0022671 | -0.0090457 | -0.0022664 | 2.4522e-06 | 6.8781e-07 | 0.01383 | 0.013831 | 0.013831 | 0.97348 | -0.18654 | 0.97321 | -0.1885 | 5.1224
31 | -0.014517 | -0.0036378 | 0.014528 | 0.0036417 | 1.1236e-05 | 3.8654e-06 | 0.022178 | 0.022178 | 0.022178 | 0.97399 | -0.18288 | 0.97477 | -0.17729 | 8.214
32 | 0.001079 | 0.00027006 | -0.0010789 | -0.00027041 | 5.0051e-08 | -3.4814e-07 | 0.0016483 | 0.0016484 | 0.0016484 | 0.97399 | -0.18288 | 0.97394 | -0.18321 | 0.61053
33 | 0.0080719 | 0.0020223 | -0.0080691 | -0.0020216 | 2.8624e-06 | 7.2685e-07 | 0.012342 | 0.012342 | 0.012342 | 0.97321 | -0.1885 | 0.97285 | -0.19106 | 4.571
34 | 0.0051825 | 0.0012977 | -0.0051816 | -0.0012976 | 9.0649e-07 | 5.9341e-08 | 0.0079108 | 0.0079109 | 0.0079109 | 0.97477 | -0.17729 | 0.97459 | -0.17856 | 2.93
35 | -0.01971 | -0.0049394 | 0.019711 | 0.0049398 | 1.1512e-06 | 4.1737e-07 | 0.030088 | 0.030088 | 0.030088 | 0.97477 | -0.17729 | 0.97483 | -0.17687 | 11.1438
36 | 0.0080691 | 0.0020216 | -0.0080684 | -0.0020214 | 6.8154e-07 | 1.731e-07 | 0.012342 | 0.012342 | 0.012342 | 0.97285 | -0.19106 | 0.97277 | -0.19167 | 4.571
37 | 0.0051816 | 0.0012976 | -0.0051807 | -0.0012975 | 9.2613e-07 | 6.0742e-08 | 0.0079109 | 0.007911 | 0.007911 | 0.97459 | -0.17856 | 0.97441 | -0.17985 | 2.93
38 | -0.021613 | -0.0054165 | 0.021623 | 0.0054199 | 9.4214e-06 | 3.4506e-06 | 0.032992 | 0.032992 | 0.032992 | 0.97483 | -0.17687 | 0.97526 | -0.17372 | 12.2191
39 | 0.0025804 | 0.00064603 | -0.0025802 | -0.00064625 | 2.3614e-07 | -2.1071e-07 | 0.003947 | 0.0039471 | 0.0039471 | 0.97277 | -0.19167 | 0.97267 | -0.19234 | 1.4619
40 | 0.0044707 | 0.0011196 | -0.00447 | -0.0011196 | 6.7406e-07 | -2.9411e-08 | 0.0068269 | 0.006827 | 0.006827 | 0.97441 | -0.17985 | 0.97426 | -0.18094 | 2.5285
41 | 0.0024561 | 0.00061519 | -0.0024558 | -0.00061549 | 2.8649e-07 | -2.9773e-07 | 0.0037473 | 0.0037474 | 0.0037474 | 0.97526 | -0.17372 | 0.97515 | -0.17456 | 1.3879
42 | -0.024079 | -0.0060351 | 0.024129 | 0.0060535 | 4.9823e-05 | 1.8423e-05 | 0.036739 | 0.036739 | 0.036739 | 0.97526 | -0.17372 | 0.97735 | -0.15881 | 13.607
43 | 0.0025802 | 0.00064625 | -0.0025798 | -0.00064657 | 3.6043e-07 | -3.2147e-07 | 0.0039471 | 0.0039472 | 0.0039472 | 0.97267 | -0.19234 | 0.97253 | -0.19335 | 1.4619
44 | -0.022048 | -0.0055281 | 0.022054 | 0.0055305 | 6.4561e-06 | 2.3674e-06 | 0.033525 | 0.033525 | 0.033525 | 0.97863 | -0.14944 | 0.97892 | -0.14732 | 12.4167
45 | -0.024343 | -0.0061041 | 0.024361 | 0.0061108 | 1.8056e-05 | 6.6786e-06 | 0.037004 | 0.037004 | 0.037004 | 0.97892 | -0.14732 | 0.97967 | -0.14197 | 13.7051
46 | -0.074124 | -0.018631 | 0.074273 | 0.018688 | 0.00014916 | 5.7133e-05 | 0.11261 | 0.11261 | 0.11261 | 0.97967 | -0.14197 | 0.98171 | -0.12755 | 41.7056
47 | 0.049763 | 0.01252 | -0.049652 | -0.012478 | 0.00011072 | 4.2195e-05 | 0.075602 | 0.075602 | 0.075602 | 0.97967 | -0.14197 | 0.97743 | -0.15796 | 28.0006
48 | -0.075498 | -0.018995 | 0.075546 | 0.019014 | 4.7591e-05 | 1.823e-05 | 0.11446 | 0.11446 | 0.11446 | 0.98171 | -0.12755 | 0.98235 | -0.12304 | 42.3934
49 | 0.047501 | 0.011939 | -0.047447 | -0.011919 | 5.389e-05 | 2.052e-05 | 0.072327 | 0.072327 | 0.072327 | 0.97743 | -0.15796 | 0.97628 | -0.16612 | 26.7876
50 | -0.075957 | -0.019117 | 0.076 | 0.019133 | 4.3627e-05 | 1.6713e-05 | 0.11508 | 0.11508 | 0.11508 | 0.98235 | -0.12304 | 0.98293 | -0.11893 | 42.624
51 | 0.045998 | 0.011555 | -0.04591 | -0.011522 | 8.7689e-05 | 3.337e-05 | 0.070118 | 0.070118 | 0.070118 | 0.97628 | -0.16612 | 0.97436 | -0.17985 | 25.9698
52 | 0.0039813 | 0.00099717 | -0.0039807 | -0.00099726 | 5.955e-07 | -9.2323e-08 | 0.0060806 | 0.0060807 | 0.0060807 | 0.97426 | -0.18094 | 0.97411 | -0.18202 | 2.2521
53 | -0.079306 | -0.019962 | 0.079354 | 0.01998 | 4.7659e-05 | 1.8062e-05 | 0.12009 | 0.12009 | 0.12009 | 0.98293 | -0.11893 | 0.98354 | -0.11462 | 22.2387
54 | 0.040403 | 0.010142 | -0.040294 | -0.0101 | 0.00010885 | 4.1296e-05 | 0.061708 | 0.061708 | 0.061708 | 0.97436 | -0.17985 | 0.97165 | -0.1993 | 22.8549
55 | -0.080199 | -0.020192 | 0.080329 | 0.020241 | 0.00013026 | 4.9379e-05 | 0.12137 | 0.12137 | 0.12137 | 0.98354 | -0.11462 | 0.98518 | -0.10302 | 22.4755
56 | 0.0043031 | 0.0010778 | -0.0043026 | -0.0010779 | 4.9222e-07 | -4.8447e-08 | 0.0064992 | 0.0064993 | 0.0064993 | 0.98518 | -0.10302 | 0.98507 | -0.10384 | 2.4071
57 | 0.0015657 | 0.00039192 | -0.0015655 | -0.00039236 | 1.3265e-07 | -4.3279e-07 | 0.0023649 | 0.002365 | 0.002365 | 0.98507 | -0.10384 | 0.98498 | -0.10446 | 0.87594
58 | 0.0027886 | 0.00069835 | -0.0027881 | -0.00069876 | 5.3343e-07 | -4.1021e-07 | 0.0042085 | 0.0042087 | 0.0042087 | 0.98594 | -0.09777 | 0.98574 | -0.099153 | 1.5588
59 | 0.0030342 | 0.00075988 | -0.0030338 | -0.00076008 | 3.3069e-07 | -1.9508e-07 | 0.0045791 | 0.0045792 | 0.0045792 | 0.98594 | -0.09777 | 0.98582 | -0.098558 | 1.696
60 | 0.0014625 | 0.00036627 | -0.0014625 | -0.00036653 | 6.8183e-08 | -2.5965e-07 | 0.0022074 | 0.0022076 | 0.0022076 | 0.98582 | -0.098558 | 0.98578 | -0.098895 | 0.81761
61 | 0.031913 | 0.0080117 | -0.031874 | -0.0079968 | 3.9591e-05 | 1.4888e-05 | 0.048497 | 0.048497 | 0.048497 | 0.97927 | -0.14506 | 0.97802 | -0.15401 | 17.962
62 | -0.033045 | -0.0082954 | 0.033052 | 0.0082979 | 6.5839e-06 | 2.4796e-06 | 0.050218 | 0.050218 | 0.050218 | 0.97927 | -0.14506 | 0.97947 | -0.14363 | 18.5991
63 | 0.031432 | 0.007886 | -0.031411 | -0.0078782 | 2.0915e-05 | 7.8604e-06 | 0.047825 | 0.047825 | 0.047825 | 0.97802 | -0.15401 | 0.97735 | -0.15881 | 17.713
64 | -0.033789 | -0.0084827 | 0.03385 | 0.0085057 | 6.0885e-05 | 2.295e-05 | 0.051338 | 0.051338 | 0.051338 | 0.97947 | -0.14363 | 0.98129 | -0.13068 | 19.0142
65 | 0.0072819 | 0.0018247 | -0.0072794 | -0.0018241 | 2.55e-06 | 5.6429e-07 | 0.011087 | 0.011087 | 0.011087 | 0.97735 | -0.15881 | 0.97699 | -0.16134 | 4.1062
66 | -0.034962 | -0.0087844 | 0.034968 | 0.0087863 | 5.1533e-06 | 1.9449e-06 | 0.053024 | 0.053024 | 0.053024 | 0.98129 | -0.13068 | 0.98144 | -0.12962 | 19.6386
67 | 0.0035756 | 0.00089584 | -0.0035755 | -0.00089586 | 8.6159e-08 | -2.5163e-08 | 0.0054458 | 0.0054458 | 0.0054458 | 0.97699 | -0.16134 | 0.97697 | -0.16151 | 2.017
68 | -0.035587 | -0.0089416 | 0.035681 | 0.0089771 | 9.3987e-05 | 3.5494e-05 | 0.053963 | 0.053963 | 0.053963 | 0.98144 | -0.12962 | 0.98411 | -0.11069 | 19.9865
69 | 0.0023713 | 0.00059405 | -0.0023711 | -0.00059426 | 1.7778e-07 | -2.051e-07 | 0.0036116 | 0.0036117 | 0.0036117 | 0.97697 | -0.16151 | 0.97689 | -0.16205 | 1.3377
70 | -0.048459 | -0.01218 | 0.048573 | 0.012224 | 0.00011405 | 4.3432e-05 | 0.073284 | 0.073284 | 0.073284 | 0.98411 | -0.11069 | 0.9865 | -0.093829 | 27.1422
71 | 0.012778 | 0.0032034 | -0.012774 | -0.0032022 | 3.6009e-06 | 1.1886e-06 | 0.019321 | 0.019321 | 0.019321 | 0.98411 | -0.11069 | 0.98383 | -0.11273 | 7.1558
72 | 0.0031392 | 0.00078636 | -0.003139 | -0.00078648 | 2.4426e-07 | -1.1796e-07 | 0.0047952 | 0.0047953 | 0.0047953 | 0.97411 | -0.18202 | 0.97403 | -0.18258 | 1.776
73 | 0.0023625 | 0.00059187 | -0.0023623 | -0.00059204 | 1.5365e-07 | -1.7619e-07 | 0.003609 | 0.0036091 | 0.0036091 | 0.97403 | -0.18258 | 0.97397 | -0.18305 | 1.3367
74 | 0.0010286 | 0.00025779 | -0.0010286 | -0.0002578 | 1.3282e-09 | -1.0214e-08 | 0.0015716 | 0.0015716 | 0.0015716 | 0.97397 | -0.18305 | 0.97396 | -0.18306 | 0.58206
75 | 0.0014787 | 0.00036973 | -0.0014786 | -0.00036994 | 5.7071e-08 | -2.1284e-07 | 0.0022301 | 0.0022301 | 0.0022301 | 0.9865 | -0.093829 | 0.98646 | -0.094109 | 0.82598
76 | -0.050051 | -0.012594 | 0.050194 | 0.012648 | 0.00014278 | 5.4402e-05 | 0.075514 | 0.075514 | 0.075514 | 0.9865 | -0.093829 | 0.98941 | -0.073444 | 27.968
77 | 0.011853 | 0.0029714 | -0.011844 | -0.0029685 | 8.9201e-06 | 2.8665e-06 | 0.017928 | 0.017928 | 0.017928 | 0.98383 | -0.11273 | 0.98306 | -0.11816 | 6.6399
78 | 0.0007894 | 0.00019742 | -0.00078937 | -0.00019784 | 2.969e-08 | -4.1702e-07 | 0.0011906 | 0.0011908 | 0.0011908 | 0.98646 | -0.094109 | 0.98643 | -0.094382 | 0.44102
79 | 0.00068919 | 0.00017252 | -0.00068918 | -0.00017272 | 1.0979e-08 | -2.0363e-07 | 0.0010395 | 0.0010396 | 0.0010396 | 0.98646 | -0.094109 | 0.98645 | -0.094224 | 0.38504
80 | -0.050472 | -0.012718 | 0.050523 | 0.012737 | 5.1121e-05 | 1.9479e-05 | 0.075931 | 0.075931 | 0.075931 | 0.98941 | -0.073444 | 0.99044 | -0.066214 | 28.1228
81 | 0.010816 | 0.0027108 | -0.010815 | -0.0027106 | 4.6273e-07 | 1.4289e-07 | 0.016371 | 0.016371 | 0.016371 | 0.98306 | -0.11816 | 0.98302 | -0.11847 | 6.0634
82 | 0.0098042 | 0.0024572 | -0.0098031 | -0.0024569 | 1.078e-06 | 3.1518e-07 | 0.014841 | 0.014841 | 0.014841 | 0.98302 | -0.11847 | 0.98291 | -0.11927 | 5.4966
83 | -0.0097994 | -0.0024558 | 0.0098031 | 0.0024569 | 3.7202e-06 | 1.0879e-06 | 0.014841 | 0.014841 | 0.014841 | 0.98253 | -0.12201 | 0.98291 | -0.11927 | 5.4966
84 | 0.005729 | 0.0014357 | -0.0057281 | -0.0014356 | 8.3757e-07 | 9.6361e-08 | 0.0086764 | 0.0086765 | 0.0086765 | 0.98253 | -0.12201 | 0.98238 | -0.12306 | 3.2135

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.18641 | 0.046964

## res_load
| p_mw | q_mvar
0 | 0.00058319 | 0.00014616
1 | 0.0016318 | 0.00040897
2 | 0.00894 | 0.0022406
3 | 0.0026129 | 0.00065485
4 | 0.01503 | 0.0037668
5 | 0.0015493 | 0.0003883
6 | 0.0031338 | 0.00078539
7 | 0.0062515 | 0.0015668
8 | 0.00070005 | 0.00017545
9 | 0.00096042 | 0.0002407
10 | 0.00053106 | 0.0001331
11 | 0.00030068 | 7.5359e-05
12 | 0.0032287 | 0.0008092
13 | 0.0081917 | 0.002053
14 | 0.0044972 | 0.0011271
15 | 0.0035279 | 0.00088418
16 | 0.0092326 | 0.0023139
17 | 0.010326 | 0.0025878
18 | 0.015894 | 0.0039834
19 | 0.0008654 | 0.00021689
20 | 0.0013954 | 0.00034972
21 | 0.0029873 | 0.00074869
22 | 0.00097382 | 0.00024406
23 | 0.0010789 | 0.00027041
24 | 0.001902 | 0.00047668
25 | 0.005488 | 0.0013754
26 | 0.00070997 | 0.00017793
27 | 0.0017053 | 0.00042739
28 | 0.0022886 | 0.00057357
29 | 0.0012251 | 0.00030704
30 | 0.0021514 | 0.00053918
31 | 0.00041108 | 0.00010303
32 | 0.0014488 | 0.00036311
33 | 0.00048869 | 0.00012248
34 | 0.0025798 | 0.00064657
35 | 0.0033056 | 0.00082846
36 | 0.0055073 | 0.0013802
37 | 0.00084514 | 0.00021181
38 | 0.0048239 | 0.001209
39 | 0.002737 | 0.00068595
40 | 0.0015655 | 0.00039236
41 | 0.0027881 | 0.00069876
42 | 0.0015713 | 0.00039381
43 | 0.0014625 | 0.00036653
44 | 0.0011322 | 0.00028375
45 | 0.00044184 | 0.00011074
46 | 0.0007376 | 0.00018486
47 | 0.001112 | 0.0002787
48 | 0.0037038 | 0.00092825
49 | 0.00061943 | 0.00015524
50 | 0.0024558 | 0.00061549
51 | 0.0012042 | 0.00030181
52 | 0.00084151 | 0.0002109
53 | 0.00077651 | 0.00019461
54 | 0.0013337 | 0.00033425
55 | 0.0010286 | 0.0002578
56 | 0.00092111 | 0.00023085
57 | 0.0002779 | 6.9649e-05
58 | 0.0010284 | 0.00025773
59 | 0.00036331 | 9.1055e-05
60 | 0.00078937 | 0.00019784
61 | 0.00068918 | 0.00017272
62 | 0.001011 | 0.00025338
63 | 0.0040704 | 0.0010201
64 | 0.0057281 | 0.0014356
65 | 0.0023711 | 0.00059426

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1