## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1122-3_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1122-3_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1122-3_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1122-3_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1122-3_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1122-3_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1122-3_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1122-3_0_3_node_45 | 0.4 | n |  | TRUE
8 | bus_LV_1122-3_0_3_node_43 | 0.4 | n |  | TRUE
9 | bus_LV_1122-3_0_3_node_50 | 0.4 | n |  | TRUE
10 | bus_LV_1122-3_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1122-3_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1122-3_0_3_node_47 | 0.4 | n |  | TRUE
13 | bus_LV_1122-3_0_3_node_49 | 0.4 | n |  | TRUE
14 | bus_LV_1122-3_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1122-3_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1122-3_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1122-3_0_3_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_1122-3_0_3_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_1122-3_0_3_node_26 | 0.4 | n |  | TRUE
20 | bus_LV_1122-3_0_3_node_28 | 0.4 | n |  | TRUE
21 | bus_LV_1122-3_0_3_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1122-3_0_3_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1122-3_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1122-3_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1122-3_0_3_node_13 | 0.4 | n |  | TRUE
26 | bus_LV_1122-3_0_3_node_14 | 0.4 | n |  | TRUE
27 | bus_LV_1122-3_0_3_node_15 | 0.4 | n |  | TRUE
28 | bus_LV_1122-3_0_3_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_1122-3_0_3_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1122-3_0_3_node_37 | 0.4 | n |  | TRUE
31 | bus_LV_1122-3_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_1122-3_0_3_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1122-3_0_3_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_1122-3_0_3_node_33 | 0.4 | n |  | TRUE
35 | bus_LV_1122-3_0_3_node_30 | 0.4 | n |  | TRUE
36 | bus_LV_1122-3_0_3_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_1122-3_0_3_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_1122-3_0_3_node_23 | 0.4 | n |  | TRUE
39 | bus_LV_1122-3_0_3_node_72 | 0.4 | n |  | TRUE
40 | bus_LV_1122-3_0_3_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1122-3_0_3_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_1122-3_0_3_node_27 | 0.4 | n |  | TRUE
43 | bus_LV_1122-3_0_3_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1122-3_0_3_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_1122-3_0_3_node_51 | 0.4 | n |  | TRUE
46 | bus_MV_129_0_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1122-3_0_3_load_0 | 0 | 0.0010645 | 0.00026679 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1122-3_0_3_load_1 | 1 | 0.0017175 | 0.00043045 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1122-3_0_3_load_3 | 3 | 0.0020488 | 0.00051347 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1122-3_0_3_load_4 | 4 | 0.0022459 | 0.00056289 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1122-3_0_3_load_5 | 5 | 0.0011838 | 0.0002967 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1122-3_0_3_load_6 | 6 | 0.00017527 | 4.3927e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1122-3_0_3_load_45 | 7 | 0.0026048 | 0.00065282 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1122-3_0_3_load_43 | 8 | 0.0011319 | 0.00028367 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1122-3_0_3_load_50 | 9 | 0.00083696 | 0.00020976 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1122-3_0_3_load_47 | 12 | 0.001805 | 0.00045237 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1122-3_0_3_load_49 | 13 | 0.0015468 | 0.00038765 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1122-3_0_3_load_8 | 14 | 0.0019722 | 0.00049428 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1122-3_0_3_load_9 | 15 | 0.0043992 | 0.0011025 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1122-3_0_3_load_10 | 16 | 0.0053405 | 0.0013385 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1122-3_0_3_load_18 | 17 | 0.0036195 | 0.00090713 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1122-3_0_3_load_29 | 18 | 0.0013134 | 0.00032916 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1122-3_0_3_load_26 | 19 | 0.00052696 | 0.00013207 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1122-3_0_3_load_28 | 20 | 0.0022702 | 0.00056898 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1122-3_0_3_load_19 | 21 | 0.012588 | 0.0031548 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1122-3_0_3_load_20 | 22 | 0.015369 | 0.0038519 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1122-3_0_3_load_12 | 24 | 0.0026575 | 0.00066602 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1122-3_0_3_load_13 | 25 | 0.001573 | 0.00039424 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1122-3_0_3_load_16 | 28 | 0.0058196 | 0.0014585 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1122-3_0_3_load_37 | 30 | 0.0018529 | 0.00046439 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1122-3_0_3_load_32 | 31 | 0.0014051 | 0.00035216 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1122-3_0_3_load_31 | 32 | 0.0014157 | 0.00035482 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1122-3_0_3_load_33 | 34 | 0.015852 | 0.0039729 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1122-3_0_3_load_30 | 35 | 0.0037713 | 0.00094518 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1122-3_0_3_load_39 | 37 | 0.0098317 | 0.0024641 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1122-3_0_3_load_72 | 39 | 0.0058084 | 0.0014557 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1122-3_0_3_load_24 | 40 | 0.00065789 | 0.00016488 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1122-3_0_3_load_25 | 41 | 0.0017126 | 0.00042922 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1122-3_0_3_load_35 | 43 | 0.0050393 | 0.001263 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1122-3_0_3_load_36 | 44 | 0.012349 | 0.003095 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 22 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1122-3_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.032575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1122-3_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.012225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1122-3_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0049294 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1122-3_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.03098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1122-3_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1122-3_0_3_line_5 | NAYY 4x150 SE | 2 | 6 | 0.013466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1122-3_0_3_line_6 | NAYY 4x150 SE | 3 | 9 | 0.015557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1122-3_0_3_line_7 | NAYY 4x150 SE | 4 | 10 | 0.029199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1122-3_0_3_line_8 | NAYY 4x150 SE | 5 | 11 | 0.033675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1122-3_0_3_line_9 | NAYY 4x150 SE | 6 | 12 | 0.016797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1122-3_0_3_line_10 | NAYY 4x150 SE | 7 | 8 | 0.0058925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1122-3_0_3_line_11 | NAYY 4x150 SE | 8 | 33 | 0.02109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1122-3_0_3_line_12 | NAYY 4x150 SE | 9 | 13 | 0.01113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_1122-3_0_3_line_13 | NAYY 4x150 SE | 10 | 14 | 0.013111 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1122-3_0_3_line_14 | NAYY 4x150 SE | 10 | 15 | 0.052713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1122-3_0_3_line_15 | NAYY 4x150 SE | 11 | 16 | 0.051527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1122-3_0_3_line_16 | NAYY 4x150 SE | 13 | 45 | 0.062169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1122-3_0_3_line_17 | NAYY 4x150 SE | 14 | 17 | 0.031815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1122-3_0_3_line_18 | NAYY 4x150 SE | 17 | 21 | 0.021477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1122-3_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.051219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1122-3_0_3_line_20 | NAYY 4x150 SE | 18 | 20 | 0.0035196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1122-3_0_3_line_21 | NAYY 4x150 SE | 19 | 40 | 0.015688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_1122-3_0_3_line_22 | NAYY 4x150 SE | 20 | 35 | 0.027125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1122-3_0_3_line_23 | NAYY 4x150 SE | 21 | 36 | 0.050704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_1122-3_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.049106 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1122-3_0_3_line_25 | NAYY 4x150 SE | 23 | 38 | 0.018326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1122-3_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.02309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1122-3_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.02594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1122-3_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.0088061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1122-3_0_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.03607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1122-3_0_3_line_30 | NAYY 4x150 SE | 26 | 29 | 0.047024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1122-3_0_3_line_31 | NAYY 4x150 SE | 27 | 30 | 0.090577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1122-3_0_3_line_32 | NAYY 4x150 SE | 28 | 31 | 0.032681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1122-3_0_3_line_33 | NAYY 4x150 SE | 29 | 32 | 0.021138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1122-3_0_3_line_34 | NAYY 4x150 SE | 29 | 33 | 0.040273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1122-3_0_3_line_35 | NAYY 4x150 SE | 31 | 34 | 0.0096228 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1122-3_0_3_line_36 | NAYY 4x150 SE | 32 | 35 | 0.0064039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1122-3_0_3_line_37 | NAYY 4x150 SE | 36 | 37 | 0.045054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1122-3_0_3_line_38 | NAYY 4x150 SE | 36 | 38 | 0.046941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1122-3_0_3_line_39 | NAYY 4x150 SE | 38 | 39 | 0.014389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1122-3_0_3_line_40 | NAYY 4x150 SE | 40 | 41 | 0.0051737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1122-3_0_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.026405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1122-3_0_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.012949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_1122-3_0_3_line_43 | NAYY 4x150 SE | 42 | 44 | 0.03378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1122-3_0_3_line_44 | NAYY 4x150 SE | 43 | 45 | 0.069331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1122-3_0_3_trafo_20 | 0.25 MVA 20/0.4 kV | 46 | 22 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2633406.1022 | 1225705.3019 | 2633435.1643 | 1225720.0176
1 | 2633395.2107 | 1225699.7492 | 2633405.7926 | 1225705.1451 | 2633406.1022 | 1225705.3019
2 | 2633435.1643 | 1225720.0176 | 2633435.9437 | 1225720.4123 | 2633439.5767 | 1225722.2152
3 | 2633395.2107 | 1225699.7492 | 2633380.112 | 1225715.841 | 2633374.0112 | 1225722.3401
4 | 2633395.2107 | 1225699.7492 | 2633338.7354 | 1225665.2107
5 | 2633395.2107 | 1225699.7492 | 2633404.2694 | 1225689.7855
6 | 2633453.5121 | 1225729.1309 | 2633439.5767 | 1225722.2152
7 | 2633354.0327 | 1225743.6339 | 2633373.2185 | 1225723.1846 | 2633374.0112 | 1225722.3401
8 | 2633310.0067 | 1225647.6411 | 2633338.7354 | 1225665.2107
9 | 2633404.2694 | 1225689.7855 | 2633415.5685 | 1225677.3573
10 | 2633486.1997 | 1225864.5811 | 2633491.611 | 1225866.9132
11 | 2633510.9788 | 1225875.2601 | 2633491.611 | 1225866.9132
12 | 2633463.4818 | 1225734.0786 | 2633453.5121 | 1225729.1309
13 | 2633354.0327 | 1225743.6339 | 2633345.0341 | 1225753.1689
14 | 2633354.0327 | 1225743.6339 | 2633362.8031 | 1225750.3426 | 2633398.4444 | 1225771.9329 | 2633398.4444 | 1225771.9329
15 | 2633310.0067 | 1225647.6411 | 2633335.5378 | 1225602.8836
16 | 2633517.0862 | 1225765.1617 | 2633512.8254 | 1225761.2798 | 2633509.5491 | 1225758.8822 | 2633484.9332 | 1225744.7242 | 2633463.4818 | 1225734.0786
17 | 2633323.1976 | 1225776.3072 | 2633345.0341 | 1225753.1689
18 | 2633323.1976 | 1225776.3072 | 2633308.4568 | 1225791.9269
19 | 2633440.2773 | 1225893.765 | 2633422.9997 | 1225845.5482
20 | 2633440.2773 | 1225893.765 | 2633443.7293 | 1225894.4513
21 | 2633422.9997 | 1225845.5482 | 2633432.1687 | 1225841.953 | 2633437.2527 | 1225839.0814
22 | 2633469.6276 | 1225902.1664 | 2633456.0929 | 1225896.9092 | 2633443.7293 | 1225894.4513
23 | 2633273.6561 | 1225828.8024 | 2633308.4568 | 1225791.9269
24 | 2633321.3945 | 1225873.4515 | 2633355.2116 | 1225837.8451
25 | 2633321.3945 | 1225873.4515 | 2633307.9191 | 1225860.9909
26 | 2633456.3612 | 1225999.8207 | 2633458.6677 | 1225991.7696 | 2633464.4747 | 1225978.2491
27 | 2633474.7116 | 1225954.415 | 2633464.4747 | 1225978.2491
28 | 2633453.9361 | 1226008.2863 | 2633456.3612 | 1225999.8207
29 | 2633474.7116 | 1225954.415 | 2633454.9395 | 1225952.4472 | 2633438.9089 | 1225950.1099
30 | 2633474.7116 | 1225954.415 | 2633487.8001 | 1225927.7503 | 2633495.3009 | 1225912.1386
31 | 2633453.9361 | 1226008.2863 | 2633446.9078 | 1226011.3375 | 2633431.9039 | 1226013.3545 | 2633415.3815 | 1226009.0815 | 2633398.434 | 1226003.5499 | 2633382.6773 | 1226001.9495 | 2633366.2972 | 1226006.6629
32 | 2633406.5695 | 1225945.3947 | 2633438.9089 | 1225950.1099
33 | 2633495.3009 | 1225912.1386 | 2633475.5971 | 1225904.4851
34 | 2633495.3009 | 1225912.1386 | 2633500.1215 | 1225900.0362 | 2633506.7844 | 1225881.1401 | 2633510.9788 | 1225875.2601
35 | 2633397.0474 | 1225944.0063 | 2633406.5695 | 1225945.3947
36 | 2633475.5971 | 1225904.4851 | 2633469.6276 | 1225902.1664
37 | 2633273.6561 | 1225828.8024 | 2633242.6983 | 1225861.5358
38 | 2633273.6561 | 1225828.8024 | 2633307.9191 | 1225860.9909
39 | 2633297.2832 | 1225870.7151 | 2633307.9191 | 1225860.9909
40 | 2633441.7574 | 1225836.5369 | 2633441.7574 | 1225836.5369 | 2633437.2527 | 1225839.0814
41 | 2633450.1329 | 1225812.2804 | 2633450.703 | 1225818.7542 | 2633441.7574 | 1225836.5369
42 | 2633450.1329 | 1225812.2804 | 2633452.8729 | 1225811.6399 | 2633461.2255 | 1225805.8985
43 | 2633416.5572 | 1225808.9901 | 2633447.6739 | 1225812.8447 | 2633450.1329 | 1225812.2804
44 | 2633517.0862 | 1225765.1617 | 2633497.5707 | 1225776.77 | 2633481.929 | 1225789.6565 | 2633471.082 | 1225799.1235 | 2633461.2255 | 1225805.8985

## bus_geodata
| x | y | coords
0 | 2633406.1022 | 1225705.3019
1 | 2633435.1643 | 1225720.0176
2 | 2633395.2107 | 1225699.7492
3 | 2633439.5767 | 1225722.2152
4 | 2633374.0112 | 1225722.3401
5 | 2633338.7354 | 1225665.2107
6 | 2633404.2694 | 1225689.7855
7 | 2633486.1997 | 1225864.5811
8 | 2633491.6111 | 1225866.9132
9 | 2633453.5121 | 1225729.1309
10 | 2633354.0327 | 1225743.6339
11 | 2633310.0067 | 1225647.6411
12 | 2633415.5685 | 1225677.3573
13 | 2633463.4818 | 1225734.0786
14 | 2633345.0341 | 1225753.1689
15 | 2633398.4444 | 1225771.9329
16 | 2633335.5378 | 1225602.8836
17 | 2633323.1976 | 1225776.3072
18 | 2633440.2773 | 1225893.765
19 | 2633422.9997 | 1225845.5482
20 | 2633443.7293 | 1225894.4513
21 | 2633308.4568 | 1225791.9269
22 | 2633355.2116 | 1225837.8451
23 | 2633321.3945 | 1225873.4515
24 | 2633464.4747 | 1225978.2491
25 | 2633456.3612 | 1225999.8207
26 | 2633474.7116 | 1225954.415
27 | 2633453.9361 | 1226008.2863
28 | 2633438.9089 | 1225950.1099
29 | 2633495.3009 | 1225912.1386
30 | 2633366.2972 | 1226006.6629
31 | 2633406.5695 | 1225945.3947
32 | 2633475.5971 | 1225904.4851
33 | 2633510.9788 | 1225875.2601
34 | 2633397.0474 | 1225944.0063
35 | 2633469.6276 | 1225902.1664
36 | 2633273.6561 | 1225828.8024
37 | 2633242.6983 | 1225861.5358
38 | 2633307.9191 | 1225860.9909
39 | 2633297.2832 | 1225870.7151
40 | 2633437.2527 | 1225839.0814
41 | 2633441.7574 | 1225836.5369
42 | 2633450.1329 | 1225812.2804
43 | 2633461.2255 | 1225805.8985
44 | 2633416.5572 | 1225808.9901
45 | 2633517.0862 | 1225765.1617
46 | 2633359.473 | 1225833.3582

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98554 | -0.10081 | 0.0010645 | 0.00026679
1 | 0.98446 | -0.10843 | 0.0017175 | 0.00043045
2 | 0.98596 | -0.097905 | 0 | 0
3 | 0.9843 | -0.10955 | 0.0020488 | 0.00051347
4 | 0.98713 | -0.089663 | 0.0022459 | 0.00056289
5 | 0.98533 | -0.10235 | 0.0011838 | 0.0002967
6 | 0.98592 | -0.098179 | 0.00017527 | 4.3927e-05
7 | 0.97482 | -0.17705 | 0.0026048 | 0.00065282
8 | 0.97484 | -0.17689 | 0.0011319 | 0.00028367
9 | 0.98382 | -0.113 | 0.00083696 | 0.00020976
10 | 0.98826 | -0.081689 | 0 | 0
11 | 0.98507 | -0.1042 | 0 | 0
12 | 0.98587 | -0.09849 | 0.001805 | 0.00045237
13 | 0.98347 | -0.11543 | 0.0015468 | 0.00038765
14 | 0.9888 | -0.077917 | 0.0019722 | 0.00049428
15 | 0.98793 | -0.08406 | 0.0043992 | 0.0011025
16 | 0.98467 | -0.10703 | 0.0053405 | 0.0013385
17 | 0.99013 | -0.068569 | 0.0036195 | 0.00090713
18 | 0.97709 | -0.16077 | 0.0013134 | 0.00032916
19 | 0.97814 | -0.15334 | 0.00052696 | 0.00013207
20 | 0.97703 | -0.16127 | 0.0022702 | 0.00056898
21 | 0.99107 | -0.062008 | 0.012588 | 0.0031548
22 | 1 | 0 | -0.12106 | -0.030392
23 | 0.99719 | -0.019393 | 0 | 0
24 | 0.97294 | -0.19058 | 0.0026575 | 0.00066602
25 | 0.97282 | -0.19141 | 0.001573 | 0.00039424
26 | 0.97317 | -0.18891 | 0 | 0
27 | 0.9728 | -0.19158 | 0 | 0
28 | 0.97195 | -0.19769 | 0.0058196 | 0.0014585
29 | 0.97518 | -0.17448 | 0 | 0
30 | 0.97255 | -0.19336 | 0.0018529 | 0.00046439
31 | 0.97112 | -0.20366 | 0.0014051 | 0.00035216
32 | 0.9762 | -0.16718 | 0.0014157 | 0.00035482
33 | 0.97496 | -0.17606 | 0 | 0
34 | 0.97089 | -0.20527 | 0.015852 | 0.0039729
35 | 0.97652 | -0.16488 | 0.0037713 | 0.00094518
36 | 0.99359 | -0.044416 | 0 | 0
37 | 0.99295 | -0.048898 | 0.0098317 | 0.0024641
38 | 0.99614 | -0.026658 | 0 | 0
39 | 0.99602 | -0.027499 | 0.0058084 | 0.0014557
40 | 0.97846 | -0.15103 | 0.00065789 | 0.00016488
41 | 0.97857 | -0.15026 | 0.0017126 | 0.00042922
42 | 0.97914 | -0.14617 | 0 | 0
43 | 0.9795 | -0.14361 | 0.0050393 | 0.001263
44 | 0.97854 | -0.15052 | 0.012349 | 0.003095
45 | 0.9816 | -0.12873 | 0 | 0
46 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.068774 | 0.017308 | -0.068701 | -0.017282 | 7.3094e-05 | 2.6869e-05 | 0.10386 | 0.10386 | 0.10386 | 0.98554 | -0.10081 | 0.98446 | -0.10843 | 12.8227
1 | -0.069838 | -0.017575 | 0.069867 | 0.017586 | 2.8287e-05 | 1.0412e-05 | 0.10547 | 0.10547 | 0.10547 | 0.98554 | -0.10081 | 0.98596 | -0.097905 | 13.0211
2 | 0.066983 | 0.016851 | -0.066973 | -0.016847 | 1.0515e-05 | 3.8562e-06 | 0.10127 | 0.10127 | 0.10127 | 0.98446 | -0.10843 | 0.9843 | -0.10955 | 12.5022
3 | -0.078379 | -0.019718 | 0.078469 | 0.019751 | 9.0206e-05 | 3.3508e-05 | 0.11832 | 0.11832 | 0.11832 | 0.98596 | -0.097905 | 0.98713 | -0.089663 | 14.607
4 | 0.0065318 | 0.0016361 | -0.0065278 | -0.0016354 | 4.0141e-06 | 7.0016e-07 | 0.0098575 | 0.0098578 | 0.0098578 | 0.98596 | -0.097905 | 0.98533 | -0.10235 | 3.6511
5 | 0.0019804 | 0.00049597 | -0.0019803 | -0.00049611 | 7.506e-08 | -1.4286e-07 | 0.0029887 | 0.0029888 | 0.0029888 | 0.98596 | -0.097905 | 0.98592 | -0.098179 | 1.107
6 | 0.064924 | 0.016334 | -0.064893 | -0.016322 | 3.1186e-05 | 1.1402e-05 | 0.098171 | 0.098171 | 0.098171 | 0.9843 | -0.10955 | 0.98382 | -0.113 | 12.1199
7 | -0.080715 | -0.020314 | 0.080805 | 0.020348 | 8.9954e-05 | 3.3477e-05 | 0.1217 | 0.1217 | 0.1217 | 0.98713 | -0.089663 | 0.98826 | -0.081689 | 15.0249
8 | 0.0053439 | 0.0013387 | -0.0053426 | -0.0013386 | 1.3685e-06 | 9.7542e-08 | 0.00807 | 0.0080702 | 0.0080702 | 0.98533 | -0.10235 | 0.98507 | -0.1042 | 2.989
9 | 0.0018051 | 0.00045219 | -0.001805 | -0.00045237 | 7.7789e-08 | -1.8427e-07 | 0.0027243 | 0.0027243 | 0.0027243 | 0.98592 | -0.098179 | 0.98587 | -0.09849 | 1.009
10 | -0.0026048 | -0.00065282 | 0.0026049 | 0.00065277 | 5.8129e-08 | -5.1105e-08 | 0.0039761 | 0.0039761 | 0.0039761 | 0.97482 | -0.17705 | 0.97484 | -0.17689 | 1.4726
11 | -0.0037367 | -0.00093645 | 0.0037372 | 0.00093635 | 4.2813e-07 | -9.8304e-08 | 0.0057038 | 0.0057037 | 0.0057038 | 0.97484 | -0.17689 | 0.97496 | -0.17606 | 2.1125
12 | 0.064056 | 0.016113 | -0.064034 | -0.016105 | 2.1739e-05 | 7.9375e-06 | 0.096905 | 0.096905 | 0.096905 | 0.98382 | -0.113 | 0.98347 | -0.11543 | 11.9636
13 | -0.085206 | -0.02145 | 0.085251 | 0.021467 | 4.4908e-05 | 1.6768e-05 | 0.12833 | 0.12833 | 0.12833 | 0.98826 | -0.081689 | 0.9888 | -0.077917 | 15.8429
14 | 0.0044006 | 0.0011024 | -0.0043992 | -0.0011025 | 1.4441e-06 | -1.1976e-07 | 0.0066258 | 0.0066261 | 0.0066261 | 0.98826 | -0.081689 | 0.98793 | -0.08406 | 2.4541
15 | 0.0053426 | 0.0013386 | -0.0053405 | -0.0013385 | 2.0941e-06 | 1.4973e-07 | 0.0080702 | 0.0080704 | 0.0080704 | 0.98507 | -0.1042 | 0.98467 | -0.10703 | 2.989
16 | 0.062487 | 0.015717 | -0.062372 | -0.015675 | 0.00011564 | 4.2114e-05 | 0.094565 | 0.094566 | 0.094566 | 0.98347 | -0.11543 | 0.9816 | -0.12873 | 11.6748
17 | -0.087223 | -0.021961 | 0.087337 | 0.022004 | 0.00011408 | 4.265e-05 | 0.1313 | 0.13129 | 0.1313 | 0.9888 | -0.077917 | 0.99013 | -0.068569 | 16.2093
18 | -0.090956 | -0.022911 | 0.09104 | 0.022942 | 8.352e-05 | 3.1294e-05 | 0.13673 | 0.13673 | 0.13673 | 0.99013 | -0.068569 | 0.99107 | -0.062008 | 16.8808
19 | -0.041842 | -0.010504 | 0.041885 | 0.010519 | 4.3266e-05 | 1.4714e-05 | 0.063728 | 0.063727 | 0.063728 | 0.97709 | -0.16077 | 0.97814 | -0.15334 | 7.8676
20 | 0.040529 | 0.010175 | -0.040526 | -0.010174 | 2.7894e-06 | 9.4061e-07 | 0.061728 | 0.061728 | 0.061728 | 0.97709 | -0.16077 | 0.97703 | -0.16127 | 7.6207
21 | -0.042412 | -0.010651 | 0.042426 | 0.010656 | 1.3587e-05 | 4.6348e-06 | 0.064529 | 0.064528 | 0.064529 | 0.97814 | -0.15334 | 0.97846 | -0.15103 | 7.9665
22 | 0.038256 | 0.0096052 | -0.038237 | -0.0095989 | 1.9157e-05 | 6.3496e-06 | 0.05827 | 0.05827 | 0.05827 | 0.97703 | -0.16127 | 0.97652 | -0.16488 | 7.1939
23 | -0.10363 | -0.026097 | 0.10388 | 0.026193 | 0.00025545 | 9.6285e-05 | 0.15563 | 0.15563 | 0.15563 | 0.99107 | -0.062008 | 0.99359 | -0.044416 | 19.214
24 | 0.12026 | 0.030392 | -0.11994 | -0.030268 | 0.00032742 | 0.000124 | 0.17904 | 0.17904 | 0.17904 | 1 | 0 | 0.99719 | -0.019393 | 22.104
25 | 0.11994 | 0.030268 | -0.11981 | -0.030222 | 0.00012219 | 4.628e-05 | 0.17904 | 0.17904 | 0.17904 | 0.99719 | -0.019393 | 0.99614 | -0.026658 | 22.104
26 | 0.0034269 | 0.00085745 | -0.0034265 | -0.00085759 | 3.957e-07 | -1.3452e-07 | 0.0052406 | 0.0052407 | 0.0052407 | 0.97294 | -0.19058 | 0.97282 | -0.19141 | 1.941
27 | -0.0060843 | -0.0015235 | 0.0060857 | 0.0015237 | 1.4014e-06 | 2.1679e-07 | 0.0093049 | 0.0093048 | 0.0093049 | 0.97294 | -0.19058 | 0.97317 | -0.18891 | 3.4463
28 | 0.0018534 | 0.00046335 | -0.0018534 | -0.00046344 | 4.4152e-08 | -9.2351e-08 | 0.0028346 | 0.0028346 | 0.0028346 | 0.97282 | -0.19141 | 0.9728 | -0.19158 | 1.0499
29 | 0.023123 | 0.0058003 | -0.023095 | -0.0057899 | 2.8138e-05 | 1.0375e-05 | 0.035358 | 0.035358 | 0.035358 | 0.97317 | -0.18891 | 0.97195 | -0.19769 | 13.0955
30 | -0.029209 | -0.007324 | 0.029267 | 0.0073459 | 5.8531e-05 | 2.1927e-05 | 0.044663 | 0.044662 | 0.044663 | 0.97317 | -0.18891 | 0.97518 | -0.17448 | 16.5417
31 | 0.0018534 | 0.00046344 | -0.0018529 | -0.00046439 | 4.542e-07 | -9.4955e-07 | 0.0028346 | 0.002835 | 0.002835 | 0.9728 | -0.19158 | 0.97255 | -0.19336 | 1.05
32 | 0.017275 | 0.0043314 | -0.017261 | -0.0043263 | 1.4265e-05 | 5.082e-06 | 0.026448 | 0.026448 | 0.026448 | 0.97195 | -0.19769 | 0.97112 | -0.20366 | 9.7957
33 | -0.033005 | -0.0082821 | 0.033039 | 0.0082947 | 3.346e-05 | 1.2605e-05 | 0.050366 | 0.050366 | 0.050366 | 0.97518 | -0.17448 | 0.9762 | -0.16718 | 18.654
34 | 0.003738 | 0.00093616 | -0.0037372 | -0.00093635 | 8.1751e-07 | -1.8791e-07 | 0.0057035 | 0.0057037 | 0.0057037 | 0.97518 | -0.17448 | 0.97496 | -0.17606 | 2.1125
35 | 0.015856 | 0.0039742 | -0.015852 | -0.0039729 | 3.5443e-06 | 1.2442e-06 | 0.024295 | 0.024295 | 0.024295 | 0.97112 | -0.20366 | 0.97089 | -0.20527 | 8.9983
36 | -0.034454 | -0.0086495 | 0.034465 | 0.0086537 | 1.1024e-05 | 4.1599e-06 | 0.052524 | 0.052524 | 0.052524 | 0.9762 | -0.16718 | 0.97652 | -0.16488 | 19.4532
37 | 0.0098378 | 0.0024658 | -0.0098317 | -0.0024641 | 6.1027e-06 | 1.7641e-06 | 0.014733 | 0.014734 | 0.014734 | 0.99359 | -0.044416 | 0.99295 | -0.048898 | 5.4569
38 | -0.11372 | -0.028659 | 0.114 | 0.028766 | 0.00028339 | 0.00010717 | 0.17037 | 0.17037 | 0.17037 | 0.99359 | -0.044416 | 0.99614 | -0.026658 | 21.0328
39 | 0.005809 | 0.0014558 | -0.0058084 | -0.0014557 | 6.7607e-07 | 7.273e-08 | 0.0086774 | 0.0086774 | 0.0086774 | 0.99614 | -0.026658 | 0.99602 | -0.027499 | 3.2139
40 | -0.043084 | -0.010821 | 0.043088 | 0.010822 | 4.6209e-06 | 1.5823e-06 | 0.065529 | 0.065529 | 0.065529 | 0.97846 | -0.15103 | 0.97857 | -0.15026 | 8.09
41 | -0.044801 | -0.011251 | 0.044827 | 0.01126 | 2.5495e-05 | 8.8101e-06 | 0.068133 | 0.068133 | 0.068133 | 0.97857 | -0.15026 | 0.97914 | -0.14617 | 8.4115
42 | -0.057183 | -0.014358 | 0.057204 | 0.014365 | 2.0345e-05 | 7.3363e-06 | 0.086911 | 0.086911 | 0.086911 | 0.97914 | -0.14617 | 0.9795 | -0.14361 | 10.7298
43 | 0.012357 | 0.0030974 | -0.012349 | -0.003095 | 7.4333e-06 | 2.4343e-06 | 0.018779 | 0.018779 | 0.018779 | 0.97914 | -0.14617 | 0.97854 | -0.15052 | 6.9552
44 | -0.062243 | -0.015628 | 0.062372 | 0.015675 | 0.00012896 | 4.6977e-05 | 0.094567 | 0.094566 | 0.094567 | 0.9795 | -0.14361 | 0.9816 | -0.12873 | 11.6749

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.13643 | 0.034244

## res_load
| p_mw | q_mvar
0 | 0.0010645 | 0.00026679
1 | 0.0017175 | 0.00043045
2 | 0.0020488 | 0.00051347
3 | 0.0022459 | 0.00056289
4 | 0.0011838 | 0.0002967
5 | 0.00017527 | 4.3927e-05
6 | 0.0026048 | 0.00065282
7 | 0.0011319 | 0.00028367
8 | 0.00083696 | 0.00020976
9 | 0.001805 | 0.00045237
10 | 0.0015468 | 0.00038765
11 | 0.0019722 | 0.00049428
12 | 0.0043992 | 0.0011025
13 | 0.0053405 | 0.0013385
14 | 0.0036195 | 0.00090713
15 | 0.0013134 | 0.00032916
16 | 0.00052696 | 0.00013207
17 | 0.0022702 | 0.00056898
18 | 0.012588 | 0.0031548
19 | 0.015369 | 0.0038519
20 | 0.0026575 | 0.00066602
21 | 0.001573 | 0.00039424
22 | 0.0058196 | 0.0014585
23 | 0.0018529 | 0.00046439
24 | 0.0014051 | 0.00035216
25 | 0.0014157 | 0.00035482
26 | 0.015852 | 0.0039729
27 | 0.0037713 | 0.00094518
28 | 0.0098317 | 0.0024641
29 | 0.0058084 | 0.0014557
30 | 0.00065789 | 0.00016488
31 | 0.0017126 | 0.00042922
32 | 0.0050393 | 0.001263
33 | 0.012349 | 0.003095

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1