## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1122-5_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1122-5_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1122-5_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1122-5_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1122-5_0_2_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1122-5_0_2_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1122-5_0_2_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1122-5_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1122-5_0_2_node_25 | 0.4 | n |  | TRUE
9 | bus_LV_1122-5_0_2_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_1122-5_0_2_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1122-5_0_2_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_1122-5_0_2_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1122-5_0_2_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1122-5_0_2_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1122-5_0_2_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1122-5_0_2_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1122-5_0_2_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1122-5_0_2_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1122-5_0_2_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_1122-5_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1122-5_0_2_node_30 | 0.4 | n |  | TRUE
22 | bus_LV_1122-5_0_2_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1122-5_0_2_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_1122-5_0_2_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1122-5_0_2_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_1122-5_0_2_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_1122-5_0_2_node_40 | 0.4 | n |  | TRUE
28 | bus_LV_1122-5_0_2_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_1122-5_0_2_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1122-5_0_2_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1122-5_0_2_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1122-5_0_2_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1122-5_0_2_node_28 | 0.4 | n |  | TRUE
34 | bus_LV_1122-5_0_2_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_1122-5_0_2_node_35 | 0.4 | n |  | TRUE
36 | bus_LV_1122-5_0_2_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_1122-5_0_2_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_1122-5_0_2_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1122-5_0_2_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_1122-5_0_2_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_1122-5_0_2_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_1122-5_0_2_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_1122-5_0_2_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_1122-5_0_2_node_47 | 0.4 | n |  | TRUE
45 | bus_LV_1122-5_0_2_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_1122-5_0_2_node_38 | 0.4 | n |  | TRUE
47 | bus_MV_129_0_node_12 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1122-5_0_2_load_0 | 0 | 0.0012854 | 0.00032216 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1122-5_0_2_load_1 | 1 | 0.0017844 | 0.00044722 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1122-5_0_2_load_16 | 6 | 0.0041631 | 0.0010434 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1122-5_0_2_load_5 | 7 | 0.0035336 | 0.0008856 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1122-5_0_2_load_25 | 8 | 0.00094738 | 0.00023744 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1122-5_0_2_load_21 | 9 | 0.0020658 | 0.00051774 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1122-5_0_2_load_11 | 10 | 0.0015634 | 0.00039182 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1122-5_0_2_load_7 | 12 | 0.0022622 | 0.00056696 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1122-5_0_2_load_8 | 13 | 0.0022348 | 0.0005601 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1122-5_0_2_load_10 | 15 | 0.0042746 | 0.0010713 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1122-5_0_2_load_12 | 16 | 0.0022702 | 0.00056897 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1122-5_0_2_load_13 | 17 | 0.0021549 | 0.00054006 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1122-5_0_2_load_14 | 18 | 0.0025541 | 0.00064012 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1122-5_0_2_load_17 | 19 | 0.0070597 | 0.0017693 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1122-5_0_2_load_30 | 21 | 0.0030723 | 0.00076998 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1122-5_0_2_load_19 | 23 | 0.0031351 | 0.00078572 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1122-5_0_2_load_20 | 24 | 0.0062756 | 0.0015728 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1122-5_0_2_load_36 | 25 | 0.0068858 | 0.0017257 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1122-5_0_2_load_23 | 28 | 0.0018856 | 0.00047258 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1122-5_0_2_load_27 | 30 | 0.0052611 | 0.0013185 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1122-5_0_2_load_31 | 31 | 0.0052647 | 0.0013194 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1122-5_0_2_load_26 | 32 | 0.0025741 | 0.00064514 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1122-5_0_2_load_35 | 35 | 0.0060849 | 0.001525 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1122-5_0_2_load_33 | 36 | 0.0019639 | 0.0004922 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1122-5_0_2_load_32 | 37 | 0.0068969 | 0.0017285 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1122-5_0_2_load_34 | 38 | 0.009684 | 0.002427 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1122-5_0_2_load_42 | 40 | 0.0032063 | 0.00080358 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1122-5_0_2_load_43 | 41 | 0.0073967 | 0.0018538 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1122-5_0_2_load_45 | 42 | 0.001218 | 0.00030526 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1122-5_0_2_load_46 | 43 | 0.0017329 | 0.00043431 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1122-5_0_2_load_47 | 44 | 0.0032856 | 0.00082345 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1122-5_0_2_load_37 | 45 | 0.0013642 | 0.0003419 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1122-5_0_2_load_38 | 46 | 0.002147 | 0.00053809 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 21 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1122-5_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0012352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1122-5_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.040625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1122-5_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.016115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1122-5_0_2_line_3 | NAYY 4x150 SE | 3 | 7 | 0.0058579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1122-5_0_2_line_4 | NAYY 4x150 SE | 4 | 5 | 0.002079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1122-5_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.012453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1122-5_0_2_line_6 | NAYY 4x150 SE | 5 | 8 | 0.011127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1122-5_0_2_line_7 | NAYY 4x150 SE | 5 | 9 | 0.012471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1122-5_0_2_line_8 | NAYY 4x150 SE | 6 | 10 | 0.00068709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1122-5_0_2_line_9 | NAYY 4x150 SE | 7 | 11 | 0.023857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1122-5_0_2_line_10 | NAYY 4x150 SE | 8 | 21 | 0.019138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1122-5_0_2_line_11 | NAYY 4x150 SE | 9 | 22 | 0.0064131 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1122-5_0_2_line_12 | NAYY 4x150 SE | 10 | 14 | 0.019225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1122-5_0_2_line_13 | NAYY 4x150 SE | 11 | 12 | 0.028624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1122-5_0_2_line_14 | NAYY 4x150 SE | 12 | 13 | 0.018651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1122-5_0_2_line_15 | NAYY 4x150 SE | 13 | 14 | 0.02352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1122-5_0_2_line_16 | NAYY 4x150 SE | 14 | 15 | 0.006557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1122-5_0_2_line_17 | NAYY 4x150 SE | 15 | 16 | 0.0047909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1122-5_0_2_line_18 | NAYY 4x150 SE | 16 | 17 | 0.00082114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1122-5_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.024704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1122-5_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.0040245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1122-5_0_2_line_21 | NAYY 4x150 SE | 19 | 20 | 0.017933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1122-5_0_2_line_22 | NAYY 4x150 SE | 20 | 23 | 0.036554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1122-5_0_2_line_23 | NAYY 4x150 SE | 20 | 24 | 0.02075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1122-5_0_2_line_24 | NAYY 4x150 SE | 21 | 31 | 0.024807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1122-5_0_2_line_25 | NAYY 4x150 SE | 22 | 28 | 0.019212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1122-5_0_2_line_26 | NAYY 4x150 SE | 23 | 25 | 0.011091 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1122-5_0_2_line_27 | NAYY 4x150 SE | 24 | 26 | 0.027441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1122-5_0_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.029691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1122-5_0_2_line_29 | NAYY 4x150 SE | 27 | 46 | 0.014025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1122-5_0_2_line_30 | NAYY 4x150 SE | 29 | 30 | 0.019529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1122-5_0_2_line_31 | NAYY 4x150 SE | 29 | 31 | 0.0068883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1122-5_0_2_line_32 | NAYY 4x150 SE | 30 | 32 | 0.003473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1122-5_0_2_line_33 | NAYY 4x150 SE | 32 | 33 | 0.059919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1122-5_0_2_line_34 | NAYY 4x150 SE | 33 | 34 | 0.090192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1122-5_0_2_line_35 | NAYY 4x150 SE | 34 | 35 | 0.078469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1122-5_0_2_line_36 | NAYY 4x150 SE | 35 | 36 | 0.015435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1122-5_0_2_line_37 | NAYY 4x150 SE | 36 | 37 | 0.029934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1122-5_0_2_line_38 | NAYY 4x150 SE | 37 | 38 | 0.060822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1122-5_0_2_line_39 | NAYY 4x150 SE | 37 | 39 | 0.041462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1122-5_0_2_line_40 | NAYY 4x150 SE | 39 | 40 | 0.037013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1122-5_0_2_line_41 | NAYY 4x150 SE | 40 | 41 | 0.024541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1122-5_0_2_line_42 | NAYY 4x150 SE | 41 | 42 | 0.067654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1122-5_0_2_line_43 | NAYY 4x150 SE | 42 | 43 | 0.029002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1122-5_0_2_line_44 | NAYY 4x150 SE | 43 | 44 | 0.013453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1122-5_0_2_line_45 | NAYY 4x150 SE | 45 | 46 | 0.034934 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1122-5_0_2_trafo_30 | 0.25 MVA 20/0.4 kV | 47 | 21 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2633639.4893 | 1225955.9144 | 2633639.0508 | 1225957.069
1 | 2633653.9132 | 1225917.9357 | 2633639.4893 | 1225955.9144
2 | 2633639.1085 | 1225911.4705 | 2633653.9132 | 1225917.9357
3 | 2633639.1085 | 1225911.4705 | 2633633.6502 | 1225909.344
4 | 2633612.7993 | 1225982.587 | 2633612.5754 | 1225984.6537
5 | 2633612.7993 | 1225982.587 | 2633601.6179 | 1225977.1057
6 | 2633612.5754 | 1225984.6537 | 2633608.2238 | 1225994.8943
7 | 2633612.5754 | 1225984.6537 | 2633623.931 | 1225989.8097
8 | 2633601.6179 | 1225977.1057 | 2633601.0009 | 1225976.8032
9 | 2633611.4197 | 1225900.6855 | 2633621.7056 | 1225904.6904 | 2633633.6502 | 1225909.344
10 | 2633608.2238 | 1225994.8943 | 2633600.739 | 1226012.5084
11 | 2633622.8418 | 1225996.1296 | 2633623.931 | 1225989.8097
12 | 2633585.6262 | 1225966.4463 | 2633587.4698 | 1225970.1701 | 2633601.0009 | 1225976.8032
13 | 2633611.4197 | 1225900.6855 | 2633602.8248 | 1225927.9883
14 | 2633602.8248 | 1225927.9883 | 2633601.1623 | 1225933.2695 | 2633595.6008 | 1225945.1459
15 | 2633585.6262 | 1225966.4463 | 2633595.6008 | 1225945.1459
16 | 2633585.6262 | 1225966.4463 | 2633582.6703 | 1225967.7527 | 2633579.6313 | 1225966.4026
17 | 2633579.6313 | 1225966.4026 | 2633575.253 | 1225964.4576
18 | 2633575.253 | 1225964.4576 | 2633574.5026 | 1225964.1243
19 | 2633551.926 | 1225954.0949 | 2633574.5026 | 1225964.1243
20 | 2633551.926 | 1225954.0949 | 2633548.2481 | 1225952.4611
21 | 2633531.2261 | 1225947.6842 | 2633538.8177 | 1225948.2718 | 2633548.2481 | 1225952.4611
22 | 2633531.2261 | 1225947.6842 | 2633531.0398 | 1225951.1519 | 2633519.3508 | 1225982.0989
23 | 2633531.2261 | 1225947.6842 | 2633528.8245 | 1225944.769 | 2633513.1469 | 1225938.2652
24 | 2633600.739 | 1226012.5084 | 2633596.4286 | 1226022.6521 | 2633609.8809 | 1226025.6638
25 | 2633622.8418 | 1225996.1296 | 2633641.6694 | 1226000.2161
26 | 2633514.302 | 1225991.8711 | 2633517.1822 | 1225987.8405 | 2633519.3508 | 1225982.0989
27 | 2633487.8001 | 1225927.7503 | 2633513.1469 | 1225938.2652
28 | 2633487.8001 | 1225927.7503 | 2633474.7116 | 1225954.415
29 | 2633474.7116 | 1225954.415 | 2633469.1766 | 1225967.302
30 | 2633616.6028 | 1226027.1686 | 2633635.578 | 1226031.7862
31 | 2633616.6028 | 1226027.1686 | 2633609.8809 | 1226025.6638
32 | 2633638.9525 | 1226032.6074 | 2633635.578 | 1226031.7862
33 | 2633697.1075 | 1226047.0353 | 2633679.98 | 1226042.5913 | 2633638.9525 | 1226032.6074
34 | 2633656.9575 | 1226116.9171 | 2633664.163 | 1226116.035 | 2633671.1041 | 1226113.6617 | 2633678.5189 | 1226109.2899 | 2633684.9689 | 1226102.6112 | 2633691.3759 | 1226091.4963 | 2633693.8252 | 1226079.2472 | 2633694.1544 | 1226077.3257 | 2633697.1075 | 1226047.0353
35 | 2633656.9575 | 1226116.9171 | 2633659.8675 | 1226096.8881 | 2633658.6805 | 1226091.0001 | 2633655.246 | 1226087.1339 | 2633648.3486 | 1226084.46 | 2633619.3018 | 1226079.4264 | 2633609.4642 | 1226076.8311
36 | 2633594.5401 | 1226072.8938 | 2633609.4642 | 1226076.8311
37 | 2633566.3367 | 1226063.118 | 2633577.7037 | 1226066.2283 | 2633590.2773 | 1226071.7692 | 2633594.5401 | 1226072.8938
38 | 2633566.3367 | 1226063.118 | 2633566.3367 | 1226063.118 | 2633551.9037 | 1226062.0249 | 2633528.5563 | 1226057.035 | 2633524.5064 | 1226054.7775 | 2633522.9008 | 1226050.5103 | 2633523.9346 | 1226047.2809 | 2633527.4011 | 1226045.4771 | 2633533.3371 | 1226046.1899
39 | 2633566.3367 | 1226063.118 | 2633543.0107 | 1226097.3961
40 | 2633543.0107 | 1226097.3961 | 2633540.4971 | 1226110.3453 | 2633554.1197 | 1226109.9663 | 2633557.122 | 1226109.8275 | 2633560.0244 | 1226108.5764 | 2633560.4566 | 1226112.5813
41 | 2633560.4566 | 1226112.5813 | 2633554.2926 | 1226115.5928 | 2633536.7195 | 1226117.5379
42 | 2633536.7195 | 1226117.5379 | 2633527.3382 | 1226118.5762 | 2633518.8441 | 1226120.8187 | 2633497.7826 | 1226124.5025 | 2633476.0113 | 1226127.7154 | 2633470.1829 | 1226129.3069
43 | 2633442.2055 | 1226136.9463 | 2633470.1829 | 1226129.3069
44 | 2633442.2055 | 1226136.9463 | 2633436.3552 | 1226138.5437 | 2633429.0383 | 1226139.5675
45 | 2633456.3806 | 1225999.7531 | 2633458.6677 | 1225991.7696 | 2633469.1766 | 1225967.302

## bus_geodata
| x | y | coords
0 | 2633639.4893 | 1225955.9144
1 | 2633639.0508 | 1225957.069
2 | 2633653.9132 | 1225917.9357
3 | 2633639.1085 | 1225911.4705
4 | 2633612.7993 | 1225982.587
5 | 2633612.5754 | 1225984.6537
6 | 2633601.6179 | 1225977.1057
7 | 2633633.6502 | 1225909.344
8 | 2633608.2238 | 1225994.8943
9 | 2633623.931 | 1225989.8097
10 | 2633601.0009 | 1225976.8032
11 | 2633611.4197 | 1225900.6855
12 | 2633602.8248 | 1225927.9883
13 | 2633595.6008 | 1225945.1459
14 | 2633585.6262 | 1225966.4463
15 | 2633579.6313 | 1225966.4026
16 | 2633575.253 | 1225964.4576
17 | 2633574.5026 | 1225964.1243
18 | 2633551.926 | 1225954.0949
19 | 2633548.2481 | 1225952.4611
20 | 2633531.2261 | 1225947.6842
21 | 2633600.739 | 1226012.5084
22 | 2633622.8418 | 1225996.1296
23 | 2633519.3508 | 1225982.0989
24 | 2633513.1469 | 1225938.2652
25 | 2633514.302 | 1225991.8711
26 | 2633487.8001 | 1225927.7503
27 | 2633474.7116 | 1225954.415
28 | 2633641.6694 | 1226000.2161
29 | 2633616.6028 | 1226027.1686
30 | 2633635.578 | 1226031.7862
31 | 2633609.8809 | 1226025.6638
32 | 2633638.9525 | 1226032.6074
33 | 2633697.1075 | 1226047.0353
34 | 2633656.9575 | 1226116.9171
35 | 2633609.4642 | 1226076.8311
36 | 2633594.5401 | 1226072.8938
37 | 2633566.3367 | 1226063.118
38 | 2633533.3371 | 1226046.1899
39 | 2633543.0107 | 1226097.3961
40 | 2633560.4566 | 1226112.5813
41 | 2633536.7195 | 1226117.5379
42 | 2633470.1829 | 1226129.3069
43 | 2633442.2055 | 1226136.9462
44 | 2633429.0383 | 1226139.5675
45 | 2633456.3806 | 1225999.7531
46 | 2633469.1766 | 1225967.302
47 | 2633612.5754 | 1225984.6537

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99348 | -0.045704 | 0.0012854 | 0.00032216
1 | 0.99348 | -0.045726 | 0.0017844 | 0.00044722
2 | 0.99366 | -0.044442 | 0 | 0
3 | 0.99373 | -0.043941 | 0 | 0
4 | 0.99725 | -0.01918 | 0 | 0
5 | 0.99742 | -0.018033 | 0 | 0
6 | 0.99627 | -0.026058 | 0.0041631 | 0.0010434
7 | 0.99375 | -0.043759 | 0.0035336 | 0.0008856
8 | 0.99836 | -0.011459 | 0.00094738 | 0.00023744
9 | 0.99735 | -0.018527 | 0.0020658 | 0.00051774
10 | 0.99622 | -0.026409 | 0.0015634 | 0.00039182
11 | 0.99398 | -0.042166 | 0 | 0
12 | 0.99425 | -0.040254 | 0.0022622 | 0.00056696
13 | 0.99449 | -0.038583 | 0.0022348 | 0.0005601
14 | 0.99486 | -0.035946 | 0 | 0
15 | 0.9945 | -0.038469 | 0.0042746 | 0.0010713
16 | 0.99427 | -0.040106 | 0.0022702 | 0.00056897
17 | 0.99423 | -0.040368 | 0.0021549 | 0.00054006
18 | 0.99319 | -0.047719 | 0.0025541 | 0.00064012
19 | 0.99303 | -0.048814 | 0.0070597 | 0.0017693
20 | 0.99252 | -0.052415 | 0 | 0
21 | 1 | 0 | -0.11648 | -0.029149
22 | 0.99733 | -0.018649 | 0 | 0
23 | 0.992 | -0.056129 | 0.0031351 | 0.00078572
24 | 0.99223 | -0.054475 | 0.0062756 | 0.0015728
25 | 0.99189 | -0.056903 | 0.0068858 | 0.0017257
26 | 0.99209 | -0.055454 | 0 | 0
27 | 0.99194 | -0.056513 | 0 | 0
28 | 0.99728 | -0.019013 | 0.0018856 | 0.00047258
29 | 0.99754 | -0.016959 | 0 | 0
30 | 0.99615 | -0.02664 | 0.0052611 | 0.0013185
31 | 0.99804 | -0.013551 | 0.0052647 | 0.0013194
32 | 0.99592 | -0.028181 | 0.0025741 | 0.00064514
33 | 0.99231 | -0.053304 | 0 | 0
34 | 0.98686 | -0.091461 | 0 | 0
35 | 0.98212 | -0.125 | 0.0060849 | 0.001525
36 | 0.98133 | -0.13066 | 0.0019639 | 0.0004922
37 | 0.97987 | -0.14105 | 0.0068969 | 0.0017285
38 | 0.97901 | -0.14718 | 0.009684 | 0.002427
39 | 0.97885 | -0.14832 | 0 | 0
40 | 0.97794 | -0.15482 | 0.0032063 | 0.00080358
41 | 0.97745 | -0.15832 | 0.0073967 | 0.0018538
42 | 0.97684 | -0.16274 | 0.001218 | 0.00030526
43 | 0.97662 | -0.16426 | 0.0017329 | 0.00043431
44 | 0.97656 | -0.16472 | 0.0032856 | 0.00082345
45 | 0.99181 | -0.057498 | 0.0013642 | 0.0003419
46 | 0.99187 | -0.057014 | 0.002147 | 0.00053809
47 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0017844 | 0.00044721 | -0.0017844 | -0.00044722 | 5.5057e-09 | -1.3876e-08 | 0.0026727 | 0.0026727 | 0.0026727 | 0.99348 | -0.045704 | 0.99348 | -0.045726 | 0.98989
1 | -0.0030699 | -0.00076937 | 0.0030704 | 0.00076905 | 5.3592e-07 | -3.2002e-07 | 0.004598 | 0.0045978 | 0.004598 | 0.99348 | -0.045704 | 0.99366 | -0.044442 | 1.703
2 | -0.0030704 | -0.00076905 | 0.0030706 | 0.00076892 | 2.1257e-07 | -1.27e-07 | 0.0045978 | 0.0045977 | 0.0045978 | 0.99366 | -0.044442 | 0.99373 | -0.043941 | 1.7029
3 | -0.0030706 | -0.00076892 | 0.0030707 | 0.00076887 | 7.727e-08 | -4.6173e-08 | 0.0045977 | 0.0045977 | 0.0045977 | 0.99373 | -0.043941 | 0.99375 | -0.043759 | 1.7029
4 | -0.055155 | -0.013845 | 0.055164 | 0.013849 | 8.7881e-06 | 3.3529e-06 | 0.082305 | 0.082305 | 0.082305 | 0.99725 | -0.01918 | 0.99742 | -0.018033 | 30.4834
5 | 0.055155 | 0.013845 | -0.055102 | -0.013825 | 5.2639e-05 | 2.0083e-05 | 0.082305 | 0.082305 | 0.082305 | 0.99725 | -0.01918 | 0.99627 | -0.026058 | 30.4834
6 | -0.059115 | -0.014839 | 0.059169 | 0.014859 | 5.4013e-05 | 2.0629e-05 | 0.088201 | 0.088201 | 0.088201 | 0.99742 | -0.018033 | 0.99836 | -0.011459 | 32.6669
7 | 0.0039518 | 0.00098998 | -0.0039515 | -0.00099003 | 2.7048e-07 | -5.8729e-08 | 0.0058954 | 0.0058955 | 0.0058955 | 0.99742 | -0.018033 | 0.99735 | -0.018527 | 2.1835
8 | 0.050939 | 0.012782 | -0.050937 | -0.012781 | 2.4821e-06 | 9.4571e-07 | 0.076087 | 0.076087 | 0.076087 | 0.99627 | -0.026058 | 0.99622 | -0.026409 | 28.1805
9 | -0.0066043 | -0.0016545 | 0.0066057 | 0.0016547 | 1.4557e-06 | 2.5074e-07 | 0.0098888 | 0.0098886 | 0.0098888 | 0.99375 | -0.043759 | 0.99398 | -0.042166 | 3.6625
10 | -0.060117 | -0.015097 | 0.060213 | 0.015133 | 9.5902e-05 | 3.6635e-05 | 0.089613 | 0.089613 | 0.089613 | 0.99836 | -0.011459 | 1 | 0 | 33.1899
11 | 0.0018857 | 0.00047229 | -0.0018857 | -0.00047237 | 3.1674e-08 | -7.1505e-08 | 0.0028134 | 0.0028134 | 0.0028134 | 0.99735 | -0.018527 | 0.99733 | -0.018649 | 1.042
12 | 0.049373 | 0.012389 | -0.049308 | -0.012364 | 6.5252e-05 | 2.4847e-05 | 0.073752 | 0.073752 | 0.073752 | 0.99622 | -0.026409 | 0.99486 | -0.035946 | 27.3157
13 | -0.0066057 | -0.0016547 | 0.0066075 | 0.001655 | 1.7465e-06 | 3.0063e-07 | 0.0098886 | 0.0098885 | 0.0098886 | 0.99398 | -0.042166 | 0.99425 | -0.040254 | 3.6625
14 | -0.0088697 | -0.002222 | 0.0088717 | 0.0022225 | 2.0507e-06 | 5.4678e-07 | 0.013274 | 0.013274 | 0.013274 | 0.99425 | -0.040254 | 0.99449 | -0.038583 | 4.9164
15 | -0.011107 | -0.0027826 | 0.011111 | 0.0027839 | 4.053e-06 | 1.2536e-06 | 0.016618 | 0.016618 | 0.016618 | 0.99449 | -0.038583 | 0.99486 | -0.035946 | 6.1548
16 | 0.038197 | 0.0095804 | -0.038184 | -0.0095753 | 1.3356e-05 | 5.052e-06 | 0.057134 | 0.057134 | 0.057134 | 0.99486 | -0.035946 | 0.9945 | -0.038469 | 21.1609
17 | 0.033909 | 0.008504 | -0.033902 | -0.0085011 | 7.6963e-06 | 2.8979e-06 | 0.050739 | 0.050739 | 0.050739 | 0.9945 | -0.038469 | 0.99427 | -0.040106 | 18.7921
18 | 0.031632 | 0.0079321 | -0.03163 | -0.0079317 | 1.1484e-06 | 4.3103e-07 | 0.047341 | 0.047341 | 0.047341 | 0.99427 | -0.040106 | 0.99423 | -0.040368 | 17.5337
19 | 0.029476 | 0.0073916 | -0.029446 | -0.0073804 | 3.0002e-05 | 1.1219e-05 | 0.044116 | 0.044116 | 0.044116 | 0.99423 | -0.040368 | 0.99319 | -0.047719 | 16.3393
20 | 0.026891 | 0.0067403 | -0.026887 | -0.0067388 | 4.0764e-06 | 1.5158e-06 | 0.040289 | 0.040289 | 0.040289 | 0.99319 | -0.047719 | 0.99303 | -0.048814 | 14.922
21 | 0.019828 | 0.0049694 | -0.019818 | -0.0049659 | 9.8782e-06 | 3.5674e-06 | 0.029711 | 0.029711 | 0.029711 | 0.99303 | -0.048814 | 0.99252 | -0.052415 | 11.004
22 | 0.010027 | 0.0025131 | -0.010022 | -0.0025116 | 5.1544e-06 | 1.5103e-06 | 0.015032 | 0.015033 | 0.015033 | 0.99252 | -0.052415 | 0.992 | -0.056129 | 5.5676
23 | 0.009791 | 0.0024528 | -0.0097882 | -0.002452 | 2.7898e-06 | 8.049e-07 | 0.014678 | 0.014679 | 0.014679 | 0.99252 | -0.052415 | 0.99223 | -0.054475 | 5.4365
24 | 0.055471 | 0.014016 | -0.055366 | -0.013975 | 0.00010557 | 4.0278e-05 | 0.082582 | 0.082582 | 0.082582 | 1 | 0 | 0.99804 | -0.013551 | 30.586
25 | 0.0018857 | 0.00047237 | -0.0018856 | -0.00047258 | 9.4893e-08 | -2.1419e-07 | 0.0028134 | 0.0028135 | 0.0028135 | 0.99733 | -0.018649 | 0.99728 | -0.019013 | 1.042
26 | 0.0068865 | 0.0017259 | -0.0068858 | -0.0017257 | 7.3853e-07 | 1.4087e-07 | 0.01033 | 0.01033 | 0.01033 | 0.992 | -0.056129 | 0.99189 | -0.056903 | 3.8259
27 | 0.0035126 | 0.00087914 | -0.0035121 | -0.00087931 | 4.7508e-07 | -1.7167e-07 | 0.0052672 | 0.0052674 | 0.0052674 | 0.99223 | -0.054475 | 0.99209 | -0.055454 | 1.9509
28 | 0.0035121 | 0.00087931 | -0.0035116 | -0.00087949 | 5.1405e-07 | -1.8562e-07 | 0.0052674 | 0.0052675 | 0.0052675 | 0.99209 | -0.055454 | 0.99194 | -0.056513 | 1.9509
29 | 0.0035116 | 0.00087949 | -0.0035113 | -0.00087958 | 2.4284e-07 | -8.764e-08 | 0.0052675 | 0.0052676 | 0.0052676 | 0.99194 | -0.056513 | 0.99187 | -0.057014 | 1.9509
30 | 0.050077 | 0.012647 | -0.050009 | -0.012621 | 6.8059e-05 | 2.5922e-05 | 0.074733 | 0.074733 | 0.074733 | 0.99754 | -0.016959 | 0.99615 | -0.02664 | 27.6789
31 | -0.050077 | -0.012647 | 0.050101 | 0.012656 | 2.4006e-05 | 9.1431e-06 | 0.074733 | 0.074733 | 0.074733 | 0.99754 | -0.016959 | 0.99804 | -0.013551 | 27.6789
32 | 0.044748 | 0.011302 | -0.044738 | -0.011299 | 9.6918e-06 | 3.6824e-06 | 0.066874 | 0.066874 | 0.066874 | 0.99615 | -0.02664 | 0.99592 | -0.028181 | 24.7682
33 | 0.042164 | 0.010653 | -0.042016 | -0.010597 | 0.00014853 | 5.6351e-05 | 0.063028 | 0.063028 | 0.063028 | 0.99592 | -0.028181 | 0.99231 | -0.053304 | 23.3439
34 | 0.042016 | 0.010597 | -0.041792 | -0.010512 | 0.00022358 | 8.4833e-05 | 0.063028 | 0.063029 | 0.063029 | 0.99231 | -0.053304 | 0.98686 | -0.091461 | 23.344
35 | 0.041792 | 0.010512 | -0.041597 | -0.010438 | 0.00019452 | 7.3817e-05 | 0.063029 | 0.063029 | 0.063029 | 0.98686 | -0.091461 | 0.98212 | -0.125 | 23.3442
36 | 0.035513 | 0.0089135 | -0.035485 | -0.0089029 | 2.7887e-05 | 1.0531e-05 | 0.05381 | 0.05381 | 0.05381 | 0.98212 | -0.125 | 0.98133 | -0.13066 | 19.9296
37 | 0.033521 | 0.0084107 | -0.033473 | -0.0083925 | 4.8264e-05 | 1.8186e-05 | 0.050832 | 0.050832 | 0.050832 | 0.98133 | -0.13066 | 0.97987 | -0.14105 | 18.8268
38 | 0.0096922 | 0.0024294 | -0.009684 | -0.002427 | 8.2222e-06 | 2.3969e-06 | 0.014719 | 0.014719 | 0.014719 | 0.97987 | -0.14105 | 0.97901 | -0.14718 | 5.4514
39 | 0.016883 | 0.0042346 | -0.016866 | -0.0042286 | 1.7009e-05 | 6.0202e-06 | 0.02564 | 0.02564 | 0.02564 | 0.97987 | -0.14105 | 0.97885 | -0.14832 | 9.4964
40 | 0.016866 | 0.0042286 | -0.016851 | -0.0042232 | 1.5184e-05 | 5.3752e-06 | 0.02564 | 0.02564 | 0.02564 | 0.97885 | -0.14832 | 0.97794 | -0.15482 | 9.4965
41 | 0.013645 | 0.0034196 | -0.013638 | -0.0034174 | 6.6009e-06 | 2.2311e-06 | 0.020762 | 0.020762 | 0.020762 | 0.97794 | -0.15482 | 0.97745 | -0.15832 | 7.6896
42 | 0.0062416 | 0.0015636 | -0.0062378 | -0.001563 | 3.8114e-06 | 6.1845e-07 | 0.0095016 | 0.0095019 | 0.0095019 | 0.97745 | -0.15832 | 0.97684 | -0.16274 | 3.5192
43 | 0.0050198 | 0.0012577 | -0.0050187 | -0.0012577 | 1.0581e-06 | 4.3992e-08 | 0.0076465 | 0.0076466 | 0.0076466 | 0.97684 | -0.16274 | 0.97662 | -0.16426 | 2.8321
44 | 0.0032858 | 0.00082336 | -0.0032856 | -0.00082345 | 2.1039e-07 | -8.7403e-08 | 0.0050063 | 0.0050064 | 0.0050064 | 0.97662 | -0.16426 | 0.97656 | -0.16472 | 1.8542
45 | -0.0013642 | -0.0003419 | 0.0013643 | 0.00034149 | 9.1311e-08 | -4.1573e-07 | 0.0020467 | 0.0020466 | 0.0020467 | 0.99181 | -0.057498 | 0.99187 | -0.057014 | 0.75805

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.11956 | 0.029919

## res_load
| p_mw | q_mvar
0 | 0.0012854 | 0.00032216
1 | 0.0017844 | 0.00044722
2 | 0.0041631 | 0.0010434
3 | 0.0035336 | 0.0008856
4 | 0.00094738 | 0.00023744
5 | 0.0020658 | 0.00051774
6 | 0.0015634 | 0.00039182
7 | 0.0022622 | 0.00056696
8 | 0.0022348 | 0.0005601
9 | 0.0042746 | 0.0010713
10 | 0.0022702 | 0.00056897
11 | 0.0021549 | 0.00054006
12 | 0.0025541 | 0.00064012
13 | 0.0070597 | 0.0017693
14 | 0.0030723 | 0.00076998
15 | 0.0031351 | 0.00078572
16 | 0.0062756 | 0.0015728
17 | 0.0068858 | 0.0017257
18 | 0.0018856 | 0.00047258
19 | 0.0052611 | 0.0013185
20 | 0.0052647 | 0.0013194
21 | 0.0025741 | 0.00064514
22 | 0.0060849 | 0.001525
23 | 0.0019639 | 0.0004922
24 | 0.0068969 | 0.0017285
25 | 0.009684 | 0.002427
26 | 0.0032063 | 0.00080358
27 | 0.0073967 | 0.0018538
28 | 0.001218 | 0.00030526
29 | 0.0017329 | 0.00043431
30 | 0.0032856 | 0.00082345
31 | 0.0013642 | 0.0003419
32 | 0.002147 | 0.00053809

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1