## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1123-3_1_2_node_24 | 0.4 | n |  | TRUE
1 | bus_LV_1123-3_1_2_node_20 | 0.4 | n |  | TRUE
2 | bus_LV_1123-3_1_2_node_1 | 0.4 | n |  | TRUE
3 | bus_LV_1123-3_1_2_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1123-3_1_2_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1123-3_1_2_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1123-3_1_2_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1123-3_1_2_node_41 | 0.4 | n |  | TRUE
8 | bus_LV_1123-3_1_2_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_1123-3_1_2_node_39 | 0.4 | n |  | TRUE
10 | bus_LV_1123-3_1_2_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1123-3_1_2_node_47 | 0.4 | n |  | TRUE
12 | bus_LV_1123-3_1_2_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1123-3_1_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1123-3_1_2_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1123-3_1_2_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1123-3_1_2_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_1123-3_1_2_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1123-3_1_2_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_1123-3_1_2_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1123-3_1_2_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1123-3_1_2_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_1123-3_1_2_node_51 | 0.4 | n |  | TRUE
23 | bus_LV_1123-3_1_2_node_48 | 0.4 | n |  | TRUE
24 | bus_LV_1123-3_1_2_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1123-3_1_2_node_55 | 0.4 | n |  | TRUE
26 | bus_LV_1123-3_1_2_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_1123-3_1_2_node_54 | 0.4 | n |  | TRUE
28 | bus_LV_1123-3_1_2_node_42 | 0.4 | n |  | TRUE
29 | bus_LV_1123-3_1_2_node_56 | 0.4 | n |  | TRUE
30 | bus_LV_1123-3_1_2_node_45 | 0.4 | n |  | TRUE
31 | bus_LV_1123-3_1_2_node_53 | 0.4 | n |  | TRUE
32 | bus_LV_1123-3_1_2_node_43 | 0.4 | n |  | TRUE
33 | bus_LV_1123-3_1_2_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_1123-3_1_2_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_1123-3_1_2_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_1123-3_1_2_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_1123-3_1_2_node_49 | 0.4 | n |  | TRUE
38 | bus_LV_1123-3_1_2_node_52 | 0.4 | n |  | TRUE
39 | bus_LV_1123-3_1_2_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_1123-3_1_2_node_58 | 0.4 | n |  | TRUE
41 | bus_MV_0_node_57 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1123-3_1_2_load_24 | 0 | 0.0028536 | 0.00071517 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1123-3_1_2_load_20 | 1 | 0.00053975 | 0.00013528 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1123-3_1_2_load_1 | 2 | 0.0032863 | 0.00082363 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1123-3_1_2_load_2 | 3 | 0.0028162 | 0.0007058 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1123-3_1_2_load_4 | 5 | 0.00094227 | 0.00023615 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1123-3_1_2_load_5 | 6 | 0.00785 | 0.0019674 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1123-3_1_2_load_39 | 9 | 0.0024524 | 0.00061462 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1123-3_1_2_load_47 | 11 | 0.003902 | 0.00097794 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1123-3_1_2_load_11 | 13 | 0.00092214 | 0.00023111 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1123-3_1_2_load_12 | 14 | 0.0010486 | 0.00026281 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1123-3_1_2_load_14 | 15 | 0.0011578 | 0.00029018 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1123-3_1_2_load_15 | 16 | 0.00078111 | 0.00019576 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1123-3_1_2_load_23 | 17 | 0.0013187 | 0.0003305 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1123-3_1_2_load_17 | 20 | 0.0036818 | 0.00092275 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1123-3_1_2_load_50 | 21 | 0.00040236 | 0.00010084 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1123-3_1_2_load_51 | 22 | 0.00039201 | 9.8247e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1123-3_1_2_load_48 | 23 | 0.0028225 | 0.00070738 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1123-3_1_2_load_18 | 24 | 0.0013269 | 0.00033256 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1123-3_1_2_load_55 | 25 | 0.00087489 | 0.00021927 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1123-3_1_2_load_46 | 26 | 0.00089567 | 0.00022448 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1123-3_1_2_load_54 | 27 | 0.0010224 | 0.00025623 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1123-3_1_2_load_42 | 28 | 0.0014825 | 0.00037155 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1123-3_1_2_load_56 | 29 | 0.00089993 | 0.00022554 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1123-3_1_2_load_45 | 30 | 0.0016663 | 0.00041761 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1123-3_1_2_load_53 | 31 | 0.00041742 | 0.00010462 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1123-3_1_2_load_43 | 32 | 0.0014868 | 0.00037263 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1123-3_1_2_load_37 | 33 | 0.0023057 | 0.00057785 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1123-3_1_2_load_38 | 34 | 0.002259 | 0.00056617 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1123-3_1_2_load_40 | 35 | 0.01023 | 0.0025639 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1123-3_1_2_load_44 | 36 | 0.0013928 | 0.00034906 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1123-3_1_2_load_49 | 37 | 0.0016092 | 0.00040331 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1123-3_1_2_load_52 | 38 | 0.0003825 | 9.5864e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1123-3_1_2_load_57 | 39 | 0.00090586 | 0.00022703 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1123-3_1_2_load_58 | 40 | 0.003886 | 0.00097392 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1123-3_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.017768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1123-3_1_2_line_1 | NAYY 4x150 SE | 1 | 24 | 0.062396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1123-3_1_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.024348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1123-3_1_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.069241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1123-3_1_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.11551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1123-3_1_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.1205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1123-3_1_2_line_6 | NAYY 4x150 SE | 6 | 7 | 0.069628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1123-3_1_2_line_7 | NAYY 4x150 SE | 7 | 8 | 0.073689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1123-3_1_2_line_8 | NAYY 4x150 SE | 7 | 9 | 0.025765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1123-3_1_2_line_9 | NAYY 4x150 SE | 8 | 28 | 0.067199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1123-3_1_2_line_10 | NAYY 4x150 SE | 9 | 33 | 0.0069903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1123-3_1_2_line_11 | NAYY 4x150 SE | 10 | 11 | 0.025092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1123-3_1_2_line_12 | NAYY 4x150 SE | 10 | 12 | 0.043174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1123-3_1_2_line_13 | NAYY 4x150 SE | 11 | 23 | 0.051902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1123-3_1_2_line_14 | NAYY 4x150 SE | 12 | 16 | 0.013213 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1123-3_1_2_line_15 | NAYY 4x150 SE | 12 | 13 | 0.024845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1123-3_1_2_line_16 | NAYY 4x150 SE | 13 | 14 | 0.010374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1123-3_1_2_line_17 | NAYY 4x150 SE | 14 | 15 | 0.01336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1123-3_1_2_line_18 | NAYY 4x150 SE | 15 | 17 | 0.00756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1123-3_1_2_line_19 | NAYY 4x150 SE | 16 | 18 | 0.019135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1123-3_1_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.019495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1123-3_1_2_line_21 | NAYY 4x150 SE | 18 | 20 | 0.018828 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1123-3_1_2_line_22 | NAYY 4x150 SE | 19 | 25 | 0.031539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1123-3_1_2_line_23 | NAYY 4x150 SE | 19 | 26 | 0.013777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1123-3_1_2_line_24 | NAYY 4x150 SE | 19 | 27 | 0.018307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1123-3_1_2_line_25 | NAYY 4x150 SE | 20 | 24 | 0.044829 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1123-3_1_2_line_26 | NAYY 4x150 SE | 21 | 22 | 3.8681e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1123-3_1_2_line_27 | NAYY 4x150 SE | 22 | 38 | 9.0547e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1123-3_1_2_line_28 | NAYY 4x150 SE | 23 | 37 | 0.016839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1123-3_1_2_line_29 | NAYY 4x150 SE | 25 | 29 | 0.00056853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1123-3_1_2_line_30 | NAYY 4x150 SE | 26 | 30 | 0.026392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1123-3_1_2_line_31 | NAYY 4x150 SE | 27 | 31 | 0.022079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1123-3_1_2_line_32 | NAYY 4x150 SE | 28 | 32 | 0.018784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1123-3_1_2_line_33 | NAYY 4x150 SE | 29 | 39 | 0.018384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1123-3_1_2_line_34 | NAYY 4x150 SE | 30 | 36 | 0.021622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1123-3_1_2_line_35 | NAYY 4x150 SE | 31 | 38 | 0.00018176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1123-3_1_2_line_36 | NAYY 4x150 SE | 32 | 36 | 0.022039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1123-3_1_2_line_37 | NAYY 4x150 SE | 33 | 34 | 0.01235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1123-3_1_2_line_38 | NAYY 4x150 SE | 34 | 35 | 0.010794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1123-3_1_2_line_39 | NAYY 4x150 SE | 39 | 40 | 0.014519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1123-3_1_2_trafo_57 | 0.25 MVA 20/0.4 kV | 41 | 39 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2640216.3344 | 1227692.3744 | 2640222.9115 | 1227675.8687
1 | 2640169.7048 | 1227656.3508 | 2640215.4797 | 1227663.2553 | 2640220.7406 | 1227666.326 | 2640222.7439 | 1227670.3976 | 2640222.9115 | 1227675.8687 | 2640222.9115 | 1227675.8687
2 | 2639839.5118 | 1227584.3556 | 2639839.3833 | 1227584.3347 | 2639815.2043 | 1227582.961
3 | 2639905.5536 | 1227604.4789 | 2639856.2405 | 1227587.0825 | 2639839.5118 | 1227584.3556
4 | 2639815.2043 | 1227582.961 | 2639815.2043 | 1227582.961 | 2639807.598 | 1227596.285 | 2639801.4115 | 1227609.2071 | 2639799.0255 | 1227621.5209 | 2639796.4437 | 1227652.934 | 2639796.7019 | 1227694.7175
5 | 2639905.5536 | 1227604.4789 | 2639938.3678 | 1227556.6474 | 2639949.3129 | 1227546.081 | 2639962.7377 | 1227537.5103 | 2639991.3971 | 1227524.7883
6 | 2640054.8443 | 1227496.1149 | 2640028.1933 | 1227508.4544 | 2639991.3971 | 1227524.7883
7 | 2640054.8443 | 1227496.1149 | 2640120.2677 | 1227461.8454
8 | 2640054.8443 | 1227496.1149 | 2640052.7539 | 1227521.7947
9 | 2640120.2677 | 1227461.8454 | 2640113.9513 | 1227528.7471
10 | 2640052.1868 | 1227528.762 | 2640052.7539 | 1227521.7947
11 | 2640095.5381 | 1227717.602 | 2640080.771 | 1227716.2351 | 2640070.5093 | 1227716.166
12 | 2640103.7845 | 1227679.0673 | 2640099.5593 | 1227717.9737 | 2640095.5381 | 1227717.602
13 | 2640070.5093 | 1227716.166 | 2640070.2008 | 1227716.1639 | 2640059.1486 | 1227717.8906 | 2640035.4474 | 1227716.5415 | 2640030.1 | 1227715.0602 | 2640026.738 | 1227712.436 | 2640025.7505 | 1227707.1595 | 2640025.9092 | 1227705.6821
14 | 2640103.7845 | 1227679.0673 | 2640104.9998 | 1227665.9104
15 | 2640103.7845 | 1227679.0673 | 2640128.4138 | 1227682.3353
16 | 2640138.6977 | 1227683.6998 | 2640128.4138 | 1227682.3353
17 | 2640151.9414 | 1227685.4571 | 2640138.6977 | 1227683.6998
18 | 2640151.9414 | 1227685.4571 | 2640159.4357 | 1227686.4515
19 | 2640106.7599 | 1227646.8565 | 2640104.9998 | 1227665.9104
20 | 2640106.7599 | 1227646.8565 | 2640108.153 | 1227631.2897 | 2640104.3061 | 1227630.908
21 | 2640106.7599 | 1227646.8565 | 2640125.3771 | 1227649.6646
22 | 2640104.3061 | 1227630.908 | 2640072.9206 | 1227627.7948
23 | 2640104.3061 | 1227630.908 | 2640105.601 | 1227617.192
24 | 2640104.3061 | 1227630.908 | 2640102.5869 | 1227649.1342
25 | 2640169.7048 | 1227656.3508 | 2640125.3771 | 1227649.6646
26 | 2640100.4844 | 1227671.4252 | 2640100.488 | 1227671.3867
27 | 2640100.488 | 1227671.3867 | 2640100.4965 | 1227671.2965
28 | 2640027.7069 | 1227688.9393 | 2640025.9092 | 1227705.6821
29 | 2640072.3549 | 1227627.7387 | 2640072.9206 | 1227627.7948
30 | 2640108.0818 | 1227590.9165 | 2640105.601 | 1227617.192
31 | 2640100.5136 | 1227671.1156 | 2640102.5869 | 1227649.1342
32 | 2640113.9513 | 1227528.7471 | 2640112.1857 | 1227547.4483
33 | 2640072.3549 | 1227627.7387 | 2640054.0609 | 1227625.9241
34 | 2640110.1141 | 1227569.3901 | 2640108.0818 | 1227590.9165
35 | 2640100.4965 | 1227671.2965 | 2640100.5136 | 1227671.1156
36 | 2640110.1141 | 1227569.3901 | 2640112.1857 | 1227547.4483
37 | 2640052.1868 | 1227528.762 | 2640051.1848 | 1227541.0714
38 | 2640050.3091 | 1227551.8296 | 2640051.1848 | 1227541.0714
39 | 2640039.613 | 1227624.491 | 2640054.0609 | 1227625.9241

## bus_geodata
| x | y | coords
0 | 2640216.3344 | 1227692.3744
1 | 2640222.9115 | 1227675.8687
2 | 2639839.5118 | 1227584.3556
3 | 2639815.2043 | 1227582.961
4 | 2639905.5536 | 1227604.4789
5 | 2639796.7019 | 1227694.7175
6 | 2639991.3971 | 1227524.7883
7 | 2640054.8443 | 1227496.1149
8 | 2640120.2677 | 1227461.8454
9 | 2640052.7539 | 1227521.7947
10 | 2640095.5381 | 1227717.602
11 | 2640070.5093 | 1227716.166
12 | 2640103.7845 | 1227679.0673
13 | 2640128.4138 | 1227682.3353
14 | 2640138.6977 | 1227683.6998
15 | 2640151.9414 | 1227685.4571
16 | 2640104.9998 | 1227665.9104
17 | 2640159.4357 | 1227686.4515
18 | 2640106.7599 | 1227646.8565
19 | 2640104.3061 | 1227630.908
20 | 2640125.3771 | 1227649.6646
21 | 2640100.4844 | 1227671.4252
22 | 2640100.488 | 1227671.3867
23 | 2640025.9092 | 1227705.6821
24 | 2640169.7048 | 1227656.3508
25 | 2640072.9206 | 1227627.7948
26 | 2640105.601 | 1227617.192
27 | 2640102.5869 | 1227649.1342
28 | 2640113.9513 | 1227528.7471
29 | 2640072.3549 | 1227627.7387
30 | 2640108.0818 | 1227590.9165
31 | 2640100.5136 | 1227671.1156
32 | 2640112.1857 | 1227547.4483
33 | 2640052.1868 | 1227528.762
34 | 2640051.1848 | 1227541.0714
35 | 2640050.3091 | 1227551.8296
36 | 2640110.1141 | 1227569.3901
37 | 2640027.7069 | 1227688.9393
38 | 2640100.4965 | 1227671.2965
39 | 2640054.0609 | 1227625.9241
40 | 2640039.613 | 1227624.491
41 | 2640054.0609 | 1227625.9241

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99379 | -0.043329 | 0.0028536 | 0.00071517
1 | 0.99387 | -0.042816 | 0.00053975 | 0.00013528
2 | 0.97986 | -0.14172 | 0.0032863 | 0.00082363
3 | 0.97973 | -0.14268 | 0.0028162 | 0.0007058
4 | 0.98057 | -0.13664 | 0 | 0
5 | 0.97957 | -0.14382 | 0.00094227 | 0.00023615
6 | 0.98181 | -0.12781 | 0.00785 | 0.0019674
7 | 0.98331 | -0.11707 | 0 | 0
8 | 0.98675 | -0.09267 | 0 | 0
9 | 0.98267 | -0.12166 | 0.0024524 | 0.00061462
10 | 0.99357 | -0.044907 | 0 | 0
11 | 0.99327 | -0.047023 | 0.003902 | 0.00097794
12 | 0.99408 | -0.041266 | 0 | 0
13 | 0.99393 | -0.042383 | 0.00092214 | 0.00023111
14 | 0.99387 | -0.042753 | 0.0010486 | 0.00026281
15 | 0.99383 | -0.043087 | 0.0011578 | 0.00029018
16 | 0.99433 | -0.039558 | 0.00078111 | 0.00019576
17 | 0.99381 | -0.043188 | 0.0013187 | 0.0003305
18 | 0.9947 | -0.036936 | 0 | 0
19 | 0.99531 | -0.032612 | 0 | 0
20 | 0.99447 | -0.038534 | 0.0036818 | 0.00092275
21 | 0.99519 | -0.033453 | 0.00040236 | 0.00010084
22 | 0.99519 | -0.033453 | 0.00039201 | 9.8247e-05
23 | 0.99294 | -0.049353 | 0.0028225 | 0.00070738
24 | 0.99417 | -0.040675 | 0.0013269 | 0.00033256
25 | 0.99821 | -0.012413 | 0.00087489 | 0.00021927
26 | 0.99453 | -0.038048 | 0.00089567 | 0.00022448
27 | 0.99524 | -0.033095 | 0.0010224 | 0.00025623
28 | 0.98989 | -0.070564 | 0.0014825 | 0.00037155
29 | 0.99826 | -0.012045 | 0.00089993 | 0.00022554
30 | 0.99307 | -0.048244 | 0.0016663 | 0.00041761
31 | 0.99519 | -0.03345 | 0.00041742 | 0.00010462
32 | 0.99081 | -0.064126 | 0.0014868 | 0.00037263
33 | 0.98252 | -0.12273 | 0.0023057 | 0.00057785
34 | 0.98229 | -0.12432 | 0.002259 | 0.00056617
35 | 0.98213 | -0.12546 | 0.01023 | 0.0025639
36 | 0.99193 | -0.056255 | 0.0013928 | 0.00034906
37 | 0.9929 | -0.049627 | 0.0016092 | 0.00040331
38 | 0.99519 | -0.033452 | 0.0003825 | 9.5864e-05
39 | 1 | 0 | -0.070897 | -0.017658
40 | 0.99992 | -0.00056324 | 0.003886 | 0.00097392
41 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0028536 | -0.00071517 | 0.0028538 | 0.00071502 | 2.024e-07 | -1.5239e-07 | 0.0042727 | 0.0042726 | 0.0042727 | 0.99379 | -0.043329 | 0.99387 | -0.042816 | 1.5825
1 | -0.0033935 | -0.0008503 | 0.0033945 | 0.00084987 | 1.005e-06 | -4.2228e-07 | 0.0050807 | 0.0050804 | 0.0050807 | 0.99387 | -0.042816 | 0.99417 | -0.040675 | 1.8818
2 | 0.0037591 | 0.00094044 | -0.0037586 | -0.00094055 | 4.9501e-07 | -1.1626e-07 | 0.0057079 | 0.005708 | 0.005708 | 0.97986 | -0.14172 | 0.97973 | -0.14268 | 2.1141
3 | -0.0070454 | -0.0017641 | 0.0070503 | 0.0017651 | 4.9452e-06 | 1.0292e-06 | 0.010699 | 0.010698 | 0.010699 | 0.97986 | -0.14172 | 0.98057 | -0.13664 | 3.9624
4 | 0.00094241 | 0.00023476 | -0.00094227 | -0.00023615 | 1.4762e-07 | -1.3976e-06 | 0.0014308 | 0.0014314 | 0.0014314 | 0.97973 | -0.14268 | 0.97957 | -0.14382 | 0.53013
5 | -0.0070503 | -0.0017651 | 0.007059 | 0.0017669 | 8.6056e-06 | 1.7879e-06 | 0.010698 | 0.010698 | 0.010698 | 0.98057 | -0.13664 | 0.98181 | -0.12781 | 3.9623
6 | -0.014909 | -0.0037343 | 0.014931 | 0.0037419 | 2.2181e-05 | 7.6493e-06 | 0.022595 | 0.022595 | 0.022595 | 0.98181 | -0.12781 | 0.98331 | -0.11707 | 8.3685
7 | -0.032196 | -0.0080705 | 0.032305 | 0.0081115 | 0.00010915 | 4.1042e-05 | 0.048721 | 0.048721 | 0.048721 | 0.98331 | -0.11707 | 0.98675 | -0.09267 | 18.0449
8 | 0.017265 | 0.0043285 | -0.017254 | -0.0043247 | 1.0974e-05 | 3.8942e-06 | 0.026126 | 0.026127 | 0.026127 | 0.98331 | -0.11707 | 0.98267 | -0.12166 | 9.6765
9 | -0.032305 | -0.0081115 | 0.032404 | 0.0081489 | 9.9535e-05 | 3.7422e-05 | 0.048721 | 0.048721 | 0.048721 | 0.98675 | -0.09267 | 0.98989 | -0.070564 | 18.0448
10 | 0.014801 | 0.00371 | -0.014799 | -0.0037093 | 2.1912e-06 | 7.5423e-07 | 0.022413 | 0.022413 | 0.022413 | 0.98267 | -0.12166 | 0.98252 | -0.12273 | 8.3012
11 | 0.0083376 | 0.0020889 | -0.0083352 | -0.0020883 | 2.4413e-06 | 6.1407e-07 | 0.012487 | 0.012487 | 0.012487 | 0.99357 | -0.044907 | 0.99327 | -0.047023 | 4.6247
12 | -0.0083376 | -0.0020889 | 0.0083418 | 0.00209 | 4.2003e-06 | 1.0561e-06 | 0.012487 | 0.012486 | 0.012487 | 0.99357 | -0.044907 | 0.99408 | -0.041266 | 4.6247
13 | 0.0044332 | 0.0011104 | -0.0044317 | -0.0011105 | 1.4284e-06 | -1.2216e-07 | 0.0066411 | 0.0066413 | 0.0066413 | 0.99327 | -0.047023 | 0.99294 | -0.049353 | 2.4598
14 | -0.01279 | -0.0032042 | 0.012793 | 0.0032052 | 3.0219e-06 | 9.9092e-07 | 0.019145 | 0.019145 | 0.019145 | 0.99408 | -0.041266 | 0.99433 | -0.039558 | 7.0906
15 | 0.0044483 | 0.0011143 | -0.0044476 | -0.0011143 | 6.8733e-07 | -5.7698e-08 | 0.0066583 | 0.0066584 | 0.0066584 | 0.99408 | -0.041266 | 0.99393 | -0.042383 | 2.4661
16 | 0.0035255 | 0.00088321 | -0.0035253 | -0.00088327 | 1.8032e-07 | -6.5088e-08 | 0.0052779 | 0.0052779 | 0.0052779 | 0.99393 | -0.042383 | 0.99387 | -0.042753 | 1.9548
17 | 0.0024767 | 0.00062046 | -0.0024766 | -0.00062059 | 1.1462e-07 | -1.2904e-07 | 0.003708 | 0.003708 | 0.003708 | 0.99387 | -0.042753 | 0.99383 | -0.043087 | 1.3734
18 | 0.0013187 | 0.00033041 | -0.0013187 | -0.0003305 | 1.8391e-08 | -9.0886e-08 | 0.0019745 | 0.0019745 | 0.0019745 | 0.99383 | -0.043087 | 0.99381 | -0.043188 | 0.73129
19 | -0.013574 | -0.003401 | 0.013579 | 0.0034026 | 4.927e-06 | 1.6467e-06 | 0.020314 | 0.020314 | 0.020314 | 0.99433 | -0.039558 | 0.9947 | -0.036936 | 7.5236
20 | -0.021986 | -0.0055083 | 0.021999 | 0.0055131 | 1.3158e-05 | 4.8077e-06 | 0.032889 | 0.032889 | 0.032889 | 0.9947 | -0.036936 | 0.99531 | -0.032612 | 12.1811
21 | 0.0084066 | 0.0021056 | -0.0084047 | -0.0021051 | 1.8579e-06 | 4.7024e-07 | 0.012575 | 0.012575 | 0.012575 | 0.9947 | -0.036936 | 0.99447 | -0.038534 | 4.6576
22 | -0.06414 | -0.016127 | 0.064321 | 0.016196 | 0.00018103 | 6.9216e-05 | 0.095909 | 0.095908 | 0.095909 | 0.99531 | -0.032612 | 0.99821 | -0.012413 | 35.5217
23 | 0.039524 | 0.0099581 | -0.039494 | -0.0099468 | 3.0035e-05 | 1.1373e-05 | 0.059108 | 0.059108 | 0.059108 | 0.99531 | -0.032612 | 0.99453 | -0.038048 | 21.8917
24 | 0.0026169 | 0.00065537 | -0.0026168 | -0.00065554 | 1.7485e-07 | -1.7067e-07 | 0.0039122 | 0.0039123 | 0.0039123 | 0.99531 | -0.032612 | 0.99524 | -0.033095 | 1.449
25 | 0.0047229 | 0.0011824 | -0.0047215 | -0.0011824 | 1.3968e-06 | -4.422e-08 | 0.0070663 | 0.0070665 | 0.0070665 | 0.99447 | -0.038534 | 0.99417 | -0.040675 | 2.6172
26 | -0.00040236 | -0.00010084 | 0.00040236 | 0.00010084 | 8.4423e-12 | -4.9989e-10 | 0.00060161 | 0.00060161 | 0.00060161 | 0.99519 | -0.033453 | 0.99519 | -0.033453 | 0.22282
27 | -0.00079437 | -0.00019909 | 0.00079437 | 0.00019909 | 8.0833e-11 | -1.146e-09 | 0.0011877 | 0.0011877 | 0.0011877 | 0.99519 | -0.033453 | 0.99519 | -0.033452 | 0.43991
28 | 0.0016093 | 0.00040311 | -0.0016092 | -0.00040331 | 6.1111e-08 | -1.9429e-07 | 0.0024116 | 0.0024117 | 0.0024117 | 0.99294 | -0.049353 | 0.9929 | -0.049627 | 0.89321
29 | -0.065196 | -0.016415 | 0.065199 | 0.016416 | 3.3526e-06 | 1.282e-06 | 0.097213 | 0.097213 | 0.097213 | 0.99821 | -0.012413 | 0.99826 | -0.012045 | 36.0047
30 | 0.038598 | 0.0097223 | -0.038543 | -0.0097015 | 5.4958e-05 | 2.0796e-05 | 0.057768 | 0.057768 | 0.057768 | 0.99453 | -0.038048 | 0.99307 | -0.048244 | 21.3954
31 | 0.0015944 | 0.00039931 | -0.0015943 | -0.00039956 | 7.8286e-08 | -2.5679e-07 | 0.0023837 | 0.0023838 | 0.0023838 | 0.99524 | -0.033095 | 0.99519 | -0.03345 | 0.88289
32 | -0.033887 | -0.0085205 | 0.033917 | 0.0085319 | 3.0427e-05 | 1.1461e-05 | 0.050949 | 0.050949 | 0.050949 | 0.98989 | -0.070564 | 0.99081 | -0.064126 | 18.87
33 | -0.066099 | -0.016642 | 0.06621 | 0.016684 | 0.00011142 | 4.2613e-05 | 0.098554 | 0.098554 | 0.098554 | 0.99826 | -0.012045 | 1 | 0 | 36.5015
34 | 0.036877 | 0.0092839 | -0.036836 | -0.0092683 | 4.1217e-05 | 1.5573e-05 | 0.055271 | 0.055271 | 0.055271 | 0.99307 | -0.048244 | 0.99193 | -0.056255 | 20.4708
35 | 0.0011769 | 0.00029495 | -0.0011769 | -0.00029495 | 3.5117e-10 | -2.2266e-09 | 0.0017597 | 0.0017597 | 0.0017597 | 0.99519 | -0.03345 | 0.99519 | -0.033452 | 0.65173
36 | -0.035404 | -0.0089046 | 0.035443 | 0.0089192 | 3.8896e-05 | 1.4676e-05 | 0.053182 | 0.053182 | 0.053182 | 0.99081 | -0.064126 | 0.99193 | -0.056255 | 19.697
37 | 0.012493 | 0.0031314 | -0.012491 | -0.0031305 | 2.759e-06 | 9.0479e-07 | 0.018921 | 0.018921 | 0.018921 | 0.98252 | -0.12273 | 0.98229 | -0.12432 | 7.0079
38 | 0.010232 | 0.0025644 | -0.01023 | -0.0025639 | 1.618e-06 | 4.8569e-07 | 0.015499 | 0.015499 | 0.015499 | 0.98229 | -0.12432 | 0.98213 | -0.12546 | 5.7405
39 | 0.0038863 | 0.00097385 | -0.003886 | -0.00097392 | 3.0297e-07 | -7.3934e-08 | 0.0057828 | 0.0057829 | 0.0057829 | 1 | 0 | 0.99992 | -0.00056324 | 2.1418

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.071802 | 0.017885

## res_load
| p_mw | q_mvar
0 | 0.0028536 | 0.00071517
1 | 0.00053975 | 0.00013528
2 | 0.0032863 | 0.00082363
3 | 0.0028162 | 0.0007058
4 | 0.00094227 | 0.00023615
5 | 0.00785 | 0.0019674
6 | 0.0024524 | 0.00061462
7 | 0.003902 | 0.00097794
8 | 0.00092214 | 0.00023111
9 | 0.0010486 | 0.00026281
10 | 0.0011578 | 0.00029018
11 | 0.00078111 | 0.00019576
12 | 0.0013187 | 0.0003305
13 | 0.0036818 | 0.00092275
14 | 0.00040236 | 0.00010084
15 | 0.00039201 | 9.8247e-05
16 | 0.0028225 | 0.00070738
17 | 0.0013269 | 0.00033256
18 | 0.00087489 | 0.00021927
19 | 0.00089567 | 0.00022448
20 | 0.0010224 | 0.00025623
21 | 0.0014825 | 0.00037155
22 | 0.00089993 | 0.00022554
23 | 0.0016663 | 0.00041761
24 | 0.00041742 | 0.00010462
25 | 0.0014868 | 0.00037263
26 | 0.0023057 | 0.00057785
27 | 0.002259 | 0.00056617
28 | 0.01023 | 0.0025639
29 | 0.0013928 | 0.00034906
30 | 0.0016092 | 0.00040331
31 | 0.0003825 | 9.5864e-05
32 | 0.00090586 | 0.00022703
33 | 0.003886 | 0.00097392

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1