## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1127-2_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1127-2_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1127-2_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1127-2_0_5_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1127-2_0_5_node_21 | 0.4 | n |  | TRUE
5 | bus_LV_1127-2_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1127-2_0_5_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1127-2_0_5_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1127-2_0_5_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1127-2_0_5_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1127-2_0_5_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_1127-2_0_5_node_75 | 0.4 | n |  | TRUE
12 | bus_LV_1127-2_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1127-2_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1127-2_0_5_node_77 | 0.4 | n |  | TRUE
15 | bus_LV_1127-2_0_5_node_66 | 0.4 | n |  | TRUE
16 | bus_LV_1127-2_0_5_node_64 | 0.4 | n |  | TRUE
17 | bus_LV_1127-2_0_5_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1127-2_0_5_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1127-2_0_5_node_16 | 0.4 | n |  | TRUE
20 | bus_LV_1127-2_0_5_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1127-2_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1127-2_0_5_node_39 | 0.4 | n |  | TRUE
23 | bus_LV_1127-2_0_5_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_1127-2_0_5_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1127-2_0_5_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_1127-2_0_5_node_42 | 0.4 | n |  | TRUE
27 | bus_LV_1127-2_0_5_node_49 | 0.4 | n |  | TRUE
28 | bus_LV_1127-2_0_5_node_65 | 0.4 | n |  | TRUE
29 | bus_LV_1127-2_0_5_node_74 | 0.4 | n |  | TRUE
30 | bus_LV_1127-2_0_5_node_12 | 0.4 | n |  | TRUE
31 | bus_LV_1127-2_0_5_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_1127-2_0_5_node_31 | 0.4 | n |  | TRUE
33 | bus_LV_1127-2_0_5_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1127-2_0_5_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1127-2_0_5_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_1127-2_0_5_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_1127-2_0_5_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_1127-2_0_5_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_1127-2_0_5_node_28 | 0.4 | n |  | TRUE
40 | bus_LV_1127-2_0_5_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_1127-2_0_5_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_1127-2_0_5_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_1127-2_0_5_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1127-2_0_5_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_1127-2_0_5_node_48 | 0.4 | n |  | TRUE
46 | bus_LV_1127-2_0_5_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_1127-2_0_5_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_1127-2_0_5_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_1127-2_0_5_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_1127-2_0_5_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_1127-2_0_5_node_55 | 0.4 | n |  | TRUE
52 | bus_LV_1127-2_0_5_node_53 | 0.4 | n |  | TRUE
53 | bus_LV_1127-2_0_5_node_57 | 0.4 | n |  | TRUE
54 | bus_LV_1127-2_0_5_node_56 | 0.4 | n |  | TRUE
55 | bus_LV_1127-2_0_5_node_50 | 0.4 | n |  | TRUE
56 | bus_LV_1127-2_0_5_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_1127-2_0_5_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_1127-2_0_5_node_67 | 0.4 | n |  | TRUE
59 | bus_LV_1127-2_0_5_node_63 | 0.4 | n |  | TRUE
60 | bus_LV_1127-2_0_5_node_68 | 0.4 | n |  | TRUE
61 | bus_LV_1127-2_0_5_node_61 | 0.4 | n |  | TRUE
62 | bus_LV_1127-2_0_5_node_60 | 0.4 | n |  | TRUE
63 | bus_LV_1127-2_0_5_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_1127-2_0_5_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_1127-2_0_5_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_1127-2_0_5_node_73 | 0.4 | n |  | TRUE
67 | bus_LV_1127-2_0_5_node_71 | 0.4 | n |  | TRUE
68 | bus_LV_1127-2_0_5_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_1127-2_0_5_node_76 | 0.4 | n |  | TRUE
70 | bus_LV_1127-2_0_5_node_70 | 0.4 | n |  | TRUE
71 | bus_LV_1127-2_0_5_node_72 | 0.4 | n |  | TRUE
72 | bus_MV_131_0_node_207 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1127-2_0_5_load_0 | 0 | 0.025243 | 0.0063264 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1127-2_0_5_load_21 | 4 | 0.0031286 | 0.0007841 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1127-2_0_5_load_10 | 6 | 0.0028877 | 0.00072372 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1127-2_0_5_load_19 | 7 | 0.0014006 | 0.00035102 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1127-2_0_5_load_18 | 8 | 0.0024945 | 0.00062519 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1127-2_0_5_load_20 | 10 | 0.0032379 | 0.00081149 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1127-2_0_5_load_77 | 14 | 0.0058797 | 0.0014736 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1127-2_0_5_load_64 | 16 | 0.0015885 | 0.00039811 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1127-2_0_5_load_22 | 17 | 0.0031787 | 0.00079667 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1127-2_0_5_load_11 | 18 | 0.0025266 | 0.00063322 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1127-2_0_5_load_17 | 20 | 0.0030334 | 0.00076024 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1127-2_0_5_load_15 | 21 | 0.0034119 | 0.0008551 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1127-2_0_5_load_38 | 25 | 0.00076349 | 0.00019135 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1127-2_0_5_load_49 | 27 | 0.0038203 | 0.00095746 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1127-2_0_5_load_65 | 28 | 0.0015839 | 0.00039695 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1127-2_0_5_load_74 | 29 | 0.0066023 | 0.0016547 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1127-2_0_5_load_12 | 30 | 0.0024832 | 0.00062235 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1127-2_0_5_load_31 | 32 | 0.0010879 | 0.00027266 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1127-2_0_5_load_27 | 33 | 0.0026057 | 0.00065305 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1127-2_0_5_load_25 | 34 | 0.0054231 | 0.0013592 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1127-2_0_5_load_32 | 35 | 0.0023939 | 0.00059996 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1127-2_0_5_load_33 | 36 | 0.0024934 | 0.0006249 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1127-2_0_5_load_30 | 37 | 0.00066392 | 0.00016639 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1127-2_0_5_load_26 | 38 | 0.0040694 | 0.0010199 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1127-2_0_5_load_28 | 39 | 0.0043203 | 0.0010828 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1127-2_0_5_load_29 | 40 | 0.0041129 | 0.0010308 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1127-2_0_5_load_34 | 41 | 0.0023748 | 0.00059518 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1127-2_0_5_load_37 | 42 | 0.0010293 | 0.00025796 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1127-2_0_5_load_35 | 43 | 0.0008134 | 0.00020386 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1127-2_0_5_load_36 | 44 | 0.00083096 | 0.00020826 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1127-2_0_5_load_48 | 45 | 0.0058941 | 0.0014772 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1127-2_0_5_load_43 | 46 | 0.0035722 | 0.00089528 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1127-2_0_5_load_44 | 47 | 0.00095048 | 0.00023821 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1127-2_0_5_load_45 | 48 | 0.0077129 | 0.001933 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1127-2_0_5_load_47 | 50 | 0.0018638 | 0.00046711 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1127-2_0_5_load_55 | 51 | 0.0026713 | 0.00066949 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1127-2_0_5_load_53 | 52 | 0.00037901 | 9.4989e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1127-2_0_5_load_57 | 53 | 0.0009531 | 0.00023887 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1127-2_0_5_load_51 | 56 | 0.0079002 | 0.00198 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1127-2_0_5_load_52 | 57 | 0.0022051 | 0.00055266 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1127-2_0_5_load_67 | 58 | 0.0058113 | 0.0014564 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1127-2_0_5_load_63 | 59 | 0.0023971 | 0.00060078 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1127-2_0_5_load_68 | 60 | 0.00088595 | 0.00022204 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1127-2_0_5_load_61 | 61 | 0.0009445 | 0.00023671 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1127-2_0_5_load_60 | 62 | 0.00022804 | 5.7152e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1127-2_0_5_load_58 | 63 | 0.0006323 | 0.00015847 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1127-2_0_5_load_62 | 65 | 0.0065162 | 0.0016331 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1127-2_0_5_load_69 | 68 | 0.0077609 | 0.0019451 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1127-2_0_5_load_76 | 69 | 0.0015245 | 0.00038208 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1127-2_0_5_load_70 | 70 | 0.0045549 | 0.0011416 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1127-2_0_5_load_72 | 71 | 0.000494 | 0.00012381 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1127-2_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.015015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1127-2_0_5_line_1 | NAYY 4x150 SE | 1 | 2 | 0.010542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1127-2_0_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.002178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1127-2_0_5_line_3 | NAYY 4x150 SE | 2 | 4 | 0.097637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1127-2_0_5_line_4 | NAYY 4x150 SE | 3 | 5 | 0.023202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1127-2_0_5_line_5 | NAYY 4x150 SE | 3 | 6 | 0.030136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1127-2_0_5_line_6 | NAYY 4x150 SE | 4 | 17 | 0.045417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1127-2_0_5_line_7 | NAYY 4x150 SE | 5 | 7 | 0.02922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1127-2_0_5_line_8 | NAYY 4x150 SE | 5 | 8 | 0.0053256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1127-2_0_5_line_9 | NAYY 4x150 SE | 6 | 18 | 0.029024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1127-2_0_5_line_10 | NAYY 4x150 SE | 7 | 10 | 0.02165 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1127-2_0_5_line_11 | NAYY 4x150 SE | 9 | 10 | 0.080653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1127-2_0_5_line_12 | NAYY 4x150 SE | 9 | 11 | 0.055854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1127-2_0_5_line_13 | NAYY 4x150 SE | 11 | 20 | 0.021264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1127-2_0_5_line_14 | NAYY 4x150 SE | 12 | 13 | 0.071626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1127-2_0_5_line_15 | NAYY 4x150 SE | 12 | 14 | 0.022107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1127-2_0_5_line_16 | NAYY 4x150 SE | 13 | 15 | 0.00886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1127-2_0_5_line_17 | NAYY 4x150 SE | 13 | 16 | 0.058591 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1127-2_0_5_line_18 | NAYY 4x150 SE | 15 | 29 | 0.0074903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1127-2_0_5_line_19 | NAYY 4x150 SE | 16 | 28 | 0.031749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1127-2_0_5_line_20 | NAYY 4x150 SE | 17 | 31 | 0.092303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1127-2_0_5_line_21 | NAYY 4x150 SE | 18 | 30 | 0.022753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1127-2_0_5_line_22 | NAYY 4x150 SE | 19 | 20 | 0.024705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1127-2_0_5_line_23 | NAYY 4x150 SE | 19 | 21 | 0.024579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1127-2_0_5_line_24 | NAYY 4x150 SE | 22 | 23 | 0.045741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1127-2_0_5_line_25 | NAYY 4x150 SE | 22 | 24 | 0.010221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
26 | LV_1127-2_0_5_line_26 | NAYY 4x150 SE | 22 | 25 | 0.03335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1127-2_0_5_line_27 | NAYY 4x150 SE | 23 | 26 | 0.019784 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1127-2_0_5_line_28 | NAYY 4x150 SE | 23 | 27 | 0.027691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1127-2_0_5_line_29 | NAYY 4x150 SE | 24 | 32 | 0.056545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1127-2_0_5_line_30 | NAYY 4x150 SE | 24 | 31 | 0.060012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1127-2_0_5_line_31 | NAYY 4x150 SE | 25 | 44 | 0.020452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1127-2_0_5_line_32 | NAYY 4x150 SE | 26 | 28 | 0.039387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1127-2_0_5_line_33 | NAYY 4x150 SE | 27 | 45 | 0.034072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1127-2_0_5_line_34 | NAYY 4x150 SE | 32 | 37 | 0.017984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1127-2_0_5_line_35 | NAYY 4x150 SE | 33 | 34 | 0.037521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1127-2_0_5_line_36 | NAYY 4x150 SE | 34 | 38 | 0.026722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1127-2_0_5_line_37 | NAYY 4x150 SE | 35 | 36 | 0.026333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1127-2_0_5_line_38 | NAYY 4x150 SE | 36 | 41 | 0.028479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1127-2_0_5_line_39 | NAYY 4x150 SE | 37 | 40 | 0.026988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1127-2_0_5_line_40 | NAYY 4x150 SE | 38 | 39 | 0.014266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1127-2_0_5_line_41 | NAYY 4x150 SE | 39 | 40 | 0.015928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1127-2_0_5_line_42 | NAYY 4x150 SE | 41 | 42 | 0.020045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1127-2_0_5_line_43 | NAYY 4x150 SE | 42 | 43 | 0.0065948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1127-2_0_5_line_44 | NAYY 4x150 SE | 43 | 44 | 0.023924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1127-2_0_5_line_45 | NAYY 4x150 SE | 45 | 55 | 0.012587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1127-2_0_5_line_46 | NAYY 4x150 SE | 46 | 47 | 0.0046578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1127-2_0_5_line_47 | NAYY 4x150 SE | 46 | 48 | 0.061466 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1127-2_0_5_line_48 | NAYY 4x150 SE | 47 | 49 | 0.018364 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1127-2_0_5_line_49 | NAYY 4x150 SE | 48 | 50 | 0.0036798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1127-2_0_5_line_50 | NAYY 4x150 SE | 49 | 51 | 0.012955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1127-2_0_5_line_51 | NAYY 4x150 SE | 49 | 52 | 0.019366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1127-2_0_5_line_52 | NAYY 4x150 SE | 50 | 53 | 0.016847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1127-2_0_5_line_53 | NAYY 4x150 SE | 51 | 54 | 0.023671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1127-2_0_5_line_54 | NAYY 4x150 SE | 54 | 62 | 0.031078 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1127-2_0_5_line_55 | NAYY 4x150 SE | 54 | 63 | 0.052415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1127-2_0_5_line_56 | NAYY 4x150 SE | 55 | 56 | 0.063301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1127-2_0_5_line_57 | NAYY 4x150 SE | 55 | 57 | 0.047147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1127-2_0_5_line_58 | NAYY 4x150 SE | 56 | 58 | 0.0046225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1127-2_0_5_line_59 | NAYY 4x150 SE | 57 | 59 | 0.0039526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1127-2_0_5_line_60 | NAYY 4x150 SE | 58 | 60 | 0.013698 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1127-2_0_5_line_61 | NAYY 4x150 SE | 59 | 61 | 0.048084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1127-2_0_5_line_62 | NAYY 4x150 SE | 60 | 68 | 0.018221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1127-2_0_5_line_63 | NAYY 4x150 SE | 61 | 64 | 0.020514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1127-2_0_5_line_64 | NAYY 4x150 SE | 63 | 64 | 0.02206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1127-2_0_5_line_65 | NAYY 4x150 SE | 64 | 65 | 0.070968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1127-2_0_5_line_66 | NAYY 4x150 SE | 65 | 66 | 0.13272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1127-2_0_5_line_67 | NAYY 4x150 SE | 66 | 67 | 0.14801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1127-2_0_5_line_68 | NAYY 4x150 SE | 67 | 70 | 0.11524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1127-2_0_5_line_69 | NAYY 4x150 SE | 68 | 69 | 0.0066381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1127-2_0_5_line_70 | NAYY 4x150 SE | 70 | 71 | 0.011153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1127-2_0_5_trafo_9 | 0.25 MVA 20/0.4 kV | 72 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2643161.4642 | 1226259.8291 | 2643152.2434 | 1226261.441 | 2643146.6207 | 1226262.0339
1 | 2643161.4642 | 1226259.8291 | 2643161.8284 | 1226259.765 | 2643171.8983 | 1226258.1259
2 | 2643161.82 | 1226261.9774 | 2643161.4642 | 1226259.8291
3 | 2643171.8983 | 1226258.1259 | 2643178.9695 | 1226257.1432 | 2643193.449 | 1226255.7362 | 2643208.9235 | 1226255.0925 | 2643232.6705 | 1226255.0315 | 2643242.737 | 1226254.9045 | 2643249.2679 | 1226254.2293 | 2643254.3754 | 1226253.3325 | 2643260.8455 | 1226251.634 | 2643268.4659 | 1226248.5865
4 | 2643161.82 | 1226261.9774 | 2643162.2117 | 1226264.3929 | 2643163.4023 | 1226271.6281 | 2643163.3734 | 1226275.6193 | 2643164.9999 | 1226281.2678 | 2643163.2645 | 1226284.3683
5 | 2643161.82 | 1226261.9774 | 2643171.7009 | 1226260.2702 | 2643181.1158 | 1226259.0599 | 2643191.6888 | 1226258.0996
6 | 2643268.4659 | 1226248.5865 | 2643269.6102 | 1226248.1288 | 2643282.0352 | 1226242.6157 | 2643294.7676 | 1226236.5268 | 2643302.0009 | 1226234.1112 | 2643310.6258 | 1226232.1172 | 2643310.6258 | 1226232.1172
7 | 2643163.2645 | 1226284.3683 | 2643191.9773 | 1226289.7895
8 | 2643163.2645 | 1226284.3683 | 2643159.1813 | 1226286.162 | 2643158.341 | 1226286.3704
9 | 2643191.6888 | 1226258.0996 | 2643201.8594 | 1226257.1759 | 2643220.67 | 1226256.993
10 | 2643213.2512 | 1226293.8062 | 2643191.9773 | 1226289.7895
11 | 2643292.6335 | 1226307.9772 | 2643286.1722 | 1226306.396 | 2643223.4615 | 1226295.734 | 2643213.2512 | 1226293.8062
12 | 2643247.5037 | 1226328.0394 | 2643249.7762 | 1226321.9744 | 2643253.0496 | 1226318.963 | 2643259.5718 | 1226317.3872 | 2643282.738 | 1226317.9559 | 2643286.8182 | 1226316.5736 | 2643291.3179 | 1226312.7484 | 2643292.6335 | 1226307.9772
13 | 2643247.5037 | 1226328.0394 | 2643226.5818 | 1226324.2408
14 | 2643192.1998 | 1226149.0063 | 2643192.0989 | 1226145.1476 | 2643192.0113 | 1226141.5559 | 2643204.0905 | 1226139.8536 | 2643241.0033 | 1226134.6516 | 2643255.6275 | 1226133.1902
15 | 2643192.1998 | 1226149.0063 | 2643214.2322 | 1226147.1888
16 | 2643254.9564 | 1226124.3577 | 2643255.5436 | 1226132.2113 | 2643255.6275 | 1226133.1902
17 | 2643255.6275 | 1226133.1902 | 2643261.0737 | 1226132.6406 | 2643304.1025 | 1226131.7305 | 2643314.1744 | 1226132.097
18 | 2643254.9564 | 1226124.3577 | 2643262.4245 | 1226123.781
19 | 2643314.1744 | 1226132.097 | 2643345.9028 | 1226133.2515
20 | 2643402.627 | 1226233.0541 | 2643399.2138 | 1226232.3399 | 2643386.9122 | 1226230.2713 | 2643364.0868 | 1226230.7275 | 2643341.204 | 1226230.761 | 2643319.4094 | 1226231.2249 | 2643310.6258 | 1226232.1172
21 | 2643243.4216 | 1226256.7718 | 2643220.67 | 1226256.993
22 | 2643202.5036 | 1226328.2018 | 2643208.4775 | 1226325.9327 | 2643217.64 | 1226323.9757 | 2643226.5818 | 1226324.2408
23 | 2643202.5036 | 1226328.2018 | 2643179.5343 | 1226336.9517
24 | 2643399.0037 | 1226163.4407 | 2643400.2608 | 1226151.1201 | 2643402.7398 | 1226145.8682 | 2643408.7718 | 1226140.8536 | 2643411.2644 | 1226136.8582 | 2643411.0746 | 1226134.8111 | 2643410.8497 | 1226131.3518 | 2643405.3819 | 1226132.7906 | 2643404.7272 | 1226129.028
25 | 2643399.0037 | 1226163.4407 | 2643396.6422 | 1226173.3851
26 | 2643399.0037 | 1226163.4407 | 2643365.6586 | 1226163.992
27 | 2643404.7272 | 1226129.028 | 2643393.5986 | 1226131.3261 | 2643385.1996 | 1226132.4656
28 | 2643404.7272 | 1226129.028 | 2643404.6179 | 1226128.4157 | 2643403.9849 | 1226124.7977 | 2643402.9462 | 1226109.2362 | 2643399.2824 | 1226102.3497 | 2643399.2824 | 1226102.3497
29 | 2643396.6422 | 1226173.3851 | 2643393.1506 | 1226178.2182 | 2643388.243 | 1226181.8402 | 2643381.5221 | 1226183.6145 | 2643343.9986 | 1226184.4085
30 | 2643396.6422 | 1226173.3851 | 2643401.3253 | 1226209.9194 | 2643402.4389 | 1226229.7507 | 2643402.627 | 1226233.0541
31 | 2643345.209 | 1226164.3301 | 2643365.6586 | 1226163.992
32 | 2643385.1996 | 1226132.4656 | 2643378.9648 | 1226132.0199 | 2643364.3938 | 1226133.4591 | 2643350.3186 | 1226133.4122 | 2643345.9028 | 1226133.2515
33 | 2643367.2531 | 1226090.9086 | 2643370.5239 | 1226092.1006 | 2643393.2329 | 1226099.3483 | 2643399.2824 | 1226102.3497
34 | 2643343.9986 | 1226184.4085 | 2643326.019 | 1226184.7889
35 | 2643205.1014 | 1226188.5463 | 2643208.3905 | 1226188.6035 | 2643222.6619 | 1226189.7744 | 2643231.6168 | 1226189.3169 | 2643239.9816 | 1226186.6093 | 2643242.1343 | 1226186.5638
36 | 2643268.8506 | 1226185.9985 | 2643242.1343 | 1226186.5638
37 | 2643239.8481 | 1226166.072 | 2643266.1773 | 1226165.6367
38 | 2643266.1773 | 1226165.6367 | 2643294.6527 | 1226165.1659
39 | 2643299.0371 | 1226185.3598 | 2643326.019 | 1226184.7889
40 | 2643268.8506 | 1226185.9985 | 2643283.1131 | 1226185.6967
41 | 2643299.0371 | 1226185.3598 | 2643283.1131 | 1226185.6967
42 | 2643314.6947 | 1226164.8346 | 2643294.6527 | 1226165.1659
43 | 2643321.2886 | 1226164.7255 | 2643314.6947 | 1226164.8346
44 | 2643321.2886 | 1226164.7255 | 2643345.209 | 1226164.3301
45 | 2643355.4272 | 1226086.5985 | 2643367.2531 | 1226090.9086
46 | 2643445.7151 | 1225943.463 | 2643442.3456 | 1225943.0551 | 2643441.0823 | 1225943.0842
47 | 2643445.7151 | 1225943.463 | 2643453.5842 | 1225944.4157 | 2643463.7464 | 1225946.8357 | 2643504.1054 | 1225961.9403
48 | 2643422.8899 | 1225941.7457 | 2643430.2687 | 1225943.3338 | 2643441.0823 | 1225943.0842
49 | 2643507.5518 | 1225963.2301 | 2643504.1054 | 1225961.9403
50 | 2643422.8899 | 1225941.7457 | 2643411.7497 | 1225935.1325
51 | 2643422.8899 | 1225941.7457 | 2643425.9073 | 1225922.6158
52 | 2643523.3338 | 1225969.1246 | 2643519.6166 | 1225967.7454 | 2643507.5518 | 1225963.2301
53 | 2643391.3952 | 1225923.0492 | 2643411.7497 | 1225935.1325
54 | 2643391.3952 | 1225923.0492 | 2643384.3468 | 1225918.7619 | 2643364.5925 | 1225907.3221
55 | 2643391.3952 | 1225923.0492 | 2643352.8002 | 1225952.9531 | 2643350.3726 | 1225955.5992
56 | 2643355.4272 | 1226086.5985 | 2643348.3922 | 1226091.9505 | 2643340.0404 | 1226093.8798 | 2643294.1526 | 1226094.2506
57 | 2643355.4272 | 1226086.5985 | 2643348.0743 | 1226079.3961 | 2643338.4176 | 1226065.8842 | 2643334.6764 | 1226051.904 | 2643334.6603 | 1226046.1294
58 | 2643289.5303 | 1226094.288 | 2643294.1526 | 1226094.2506
59 | 2643334.6493 | 1226042.1768 | 2643334.6603 | 1226046.1294
60 | 2643289.5303 | 1226094.288 | 2643275.8323 | 1226094.3986
61 | 2643335.2102 | 1225994.1003 | 2643334.822 | 1226006.922 | 2643334.5946 | 1226022.541 | 2643334.6493 | 1226042.1768
62 | 2643275.8323 | 1226094.3986 | 2643257.6115 | 1226094.5459
63 | 2643338.6244 | 1225973.9739 | 2643335.4207 | 1225987.1476 | 2643335.2102 | 1225994.1003
64 | 2643338.6244 | 1225973.9739 | 2643343.9448 | 1225962.6057 | 2643350.3726 | 1225955.5992
65 | 2643338.6244 | 1225973.9739 | 2643319.1262 | 1225971.2193 | 2643313.8624 | 1225968.5683 | 2643310.8926 | 1225963.1434 | 2643303.5517 | 1225955.3074 | 2643294.0596 | 1225951.4249 | 2643275.8703 | 1225950.6601
66 | 2643160.3126 | 1225897.021 | 2643226.7317 | 1225935.1704 | 2643227.2355 | 1225940.9443 | 2643234.2837 | 1225944.2308 | 2643248.125 | 1225945.2096 | 2643260.1726 | 1225950.0001 | 2643275.8703 | 1225950.6601
67 | 2643074.0288 | 1225971.5308 | 2643125.2949 | 1225876.8995 | 2643160.3126 | 1225897.021
68 | 2643074.0288 | 1225971.5308 | 2643080.5161 | 1225973.7791 | 2643188.2697 | 1225985.4067
69 | 2643250.9735 | 1226094.5995 | 2643257.6115 | 1226094.5459
70 | 2643199.3587 | 1225986.6033 | 2643188.2697 | 1225985.4067

## bus_geodata
| x | y | coords
0 | 2643146.6207 | 1226262.0339
1 | 2643161.4642 | 1226259.8291
2 | 2643171.8983 | 1226258.1259
3 | 2643161.82 | 1226261.9774
4 | 2643268.4659 | 1226248.5865
5 | 2643163.2645 | 1226284.3683
6 | 2643191.6888 | 1226258.0996
7 | 2643191.9773 | 1226289.7895
8 | 2643158.341 | 1226286.3704
9 | 2643292.6335 | 1226307.9772
10 | 2643213.2512 | 1226293.8062
11 | 2643247.5037 | 1226328.0394
12 | 2643192.1998 | 1226149.0063
13 | 2643255.6275 | 1226133.1902
14 | 2643214.2322 | 1226147.1888
15 | 2643254.9564 | 1226124.3577
16 | 2643314.1744 | 1226132.097
17 | 2643310.6258 | 1226232.1172
18 | 2643220.67 | 1226256.993
19 | 2643202.5036 | 1226328.2018
20 | 2643226.5818 | 1226324.2408
21 | 2643179.5343 | 1226336.9517
22 | 2643399.0037 | 1226163.4407
23 | 2643404.7272 | 1226129.028
24 | 2643396.6422 | 1226173.3851
25 | 2643365.6586 | 1226163.992
26 | 2643385.1996 | 1226132.4656
27 | 2643399.2824 | 1226102.3497
28 | 2643345.9028 | 1226133.2515
29 | 2643262.4245 | 1226123.781
30 | 2643243.4216 | 1226256.7718
31 | 2643402.627 | 1226233.0541
32 | 2643343.9986 | 1226184.4085
33 | 2643205.1014 | 1226188.5463
34 | 2643242.1343 | 1226186.5638
35 | 2643239.8481 | 1226166.072
36 | 2643266.1773 | 1226165.6367
37 | 2643326.019 | 1226184.7889
38 | 2643268.8506 | 1226185.9985
39 | 2643283.1131 | 1226185.6967
40 | 2643299.0371 | 1226185.3598
41 | 2643294.6527 | 1226165.1659
42 | 2643314.6947 | 1226164.8346
43 | 2643321.2886 | 1226164.7255
44 | 2643345.209 | 1226164.3301
45 | 2643367.2531 | 1226090.9086
46 | 2643445.7151 | 1225943.463
47 | 2643441.0823 | 1225943.0842
48 | 2643504.1054 | 1225961.9403
49 | 2643422.8899 | 1225941.7457
50 | 2643507.5518 | 1225963.2301
51 | 2643411.7497 | 1225935.1325
52 | 2643425.9073 | 1225922.6158
53 | 2643523.3338 | 1225969.1246
54 | 2643391.3952 | 1225923.0492
55 | 2643355.4272 | 1226086.5985
56 | 2643294.1526 | 1226094.2506
57 | 2643334.6603 | 1226046.1294
58 | 2643289.5303 | 1226094.288
59 | 2643334.6493 | 1226042.1768
60 | 2643275.8323 | 1226094.3986
61 | 2643335.2102 | 1225994.1003
62 | 2643364.5925 | 1225907.3221
63 | 2643350.3726 | 1225955.5992
64 | 2643338.6244 | 1225973.9739
65 | 2643275.8703 | 1225950.6601
66 | 2643160.3126 | 1225897.021
67 | 2643074.0288 | 1225971.5308
68 | 2643257.6115 | 1226094.5459
69 | 2643250.9735 | 1226094.5995
70 | 2643188.2697 | 1225985.4067
71 | 2643199.3587 | 1225986.6033
72 | 2643256.0798 | 1226138.7414

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97271 | -0.19173 | 0.025243 | 0.0063264
1 | 0.97327 | -0.18774 | 0 | 0
2 | 0.97399 | -0.18255 | 0 | 0
3 | 0.9732 | -0.18823 | 0 | 0
4 | 0.98068 | -0.13484 | 0.0031286 | 0.0007841
5 | 0.97274 | -0.19156 | 0 | 0
6 | 0.97285 | -0.19074 | 0.0028877 | 0.00072372
7 | 0.97226 | -0.19498 | 0.0014006 | 0.00035102
8 | 0.97272 | -0.1917 | 0.0024945 | 0.00062519
9 | 0.97119 | -0.20271 | 0 | 0
10 | 0.97195 | -0.1972 | 0.0032379 | 0.00081149
11 | 0.97066 | -0.20653 | 0 | 0
12 | 0.9994 | -0.0042097 | 0 | 0
13 | 1 | 0 | -0.17571 | -0.044278
14 | 0.99921 | -0.005509 | 0.0058797 | 0.0014736
15 | 0.99992 | -0.00058396 | 0 | 0
16 | 0.99547 | -0.031159 | 0.0015885 | 0.00039811
17 | 0.98234 | -0.12311 | 0.0031787 | 0.00079667
18 | 0.97264 | -0.19228 | 0.0025266 | 0.00063322
19 | 0.97034 | -0.20888 | 0 | 0
20 | 0.97046 | -0.20798 | 0.0030334 | 0.00076024
21 | 0.97021 | -0.20976 | 0.0034119 | 0.0008551
22 | 0.98665 | -0.092698 | 0 | 0
23 | 0.98857 | -0.079258 | 0 | 0
24 | 0.98628 | -0.095334 | 0 | 0
25 | 0.98614 | -0.096363 | 0.00076349 | 0.00019135
26 | 0.99006 | -0.068772 | 0 | 0
27 | 0.98575 | -0.099045 | 0.0038203 | 0.00095746
28 | 0.99305 | -0.04799 | 0.0015839 | 0.00039695
29 | 0.99985 | -0.0010777 | 0.0066023 | 0.0016547
30 | 0.97256 | -0.19287 | 0.0024832 | 0.00062235
31 | 0.98473 | -0.10625 | 0 | 0
32 | 0.98445 | -0.10829 | 0.0010879 | 0.00027266
33 | 0.98201 | -0.12567 | 0.0026057 | 0.00065305
34 | 0.98215 | -0.12465 | 0.0054231 | 0.0013592
35 | 0.98495 | -0.10483 | 0.0023939 | 0.00059996
36 | 0.98504 | -0.10418 | 0.0024934 | 0.0006249
37 | 0.9839 | -0.11222 | 0.00066392 | 0.00016639
38 | 0.98246 | -0.12243 | 0.0040694 | 0.0010199
39 | 0.98271 | -0.12065 | 0.0043203 | 0.0010828
40 | 0.98309 | -0.11794 | 0.0041129 | 0.0010308
41 | 0.98524 | -0.10275 | 0.0023748 | 0.00059518
42 | 0.98545 | -0.10125 | 0.0010293 | 0.00025796
43 | 0.98553 | -0.10069 | 0.0008134 | 0.00020386
44 | 0.98584 | -0.098451 | 0.00083096 | 0.00020826
45 | 0.98247 | -0.1222 | 0.0058941 | 0.0014772
46 | 0.9721 | -0.1963 | 0.0035722 | 0.00089528
47 | 0.9722 | -0.1956 | 0.00095048 | 0.00023821
48 | 0.97115 | -0.20314 | 0.0077129 | 0.001933
49 | 0.9726 | -0.19269 | 0 | 0
50 | 0.97114 | -0.20325 | 0.0018638 | 0.00046711
51 | 0.9729 | -0.19058 | 0.0026713 | 0.00066949
52 | 0.97259 | -0.19276 | 0.00037901 | 9.4989e-05
53 | 0.97111 | -0.20342 | 0.0009531 | 0.00023887
54 | 0.97352 | -0.18606 | 0 | 0
55 | 0.98137 | -0.13002 | 0 | 0
56 | 0.97917 | -0.14573 | 0.0079002 | 0.00198
57 | 0.97888 | -0.14773 | 0.0022051 | 0.00055266
58 | 0.97906 | -0.1465 | 0.0058113 | 0.0014564
59 | 0.97868 | -0.14913 | 0.0023971 | 0.00060078
60 | 0.97886 | -0.14795 | 0.00088595 | 0.00022204
61 | 0.97647 | -0.16497 | 0.0009445 | 0.00023671
62 | 0.97351 | -0.18613 | 0.00022804 | 5.7152e-05
63 | 0.97493 | -0.17594 | 0.0006323 | 0.00015847
64 | 0.97555 | -0.17155 | 0 | 0
65 | 0.97435 | -0.1802 | 0.0065162 | 0.0016331
66 | 0.97336 | -0.18729 | 0 | 0
67 | 0.97227 | -0.1952 | 0 | 0
68 | 0.97861 | -0.14971 | 0.0077609 | 0.0019451
69 | 0.9786 | -0.14982 | 0.0015245 | 0.00038208
70 | 0.97141 | -0.20136 | 0.0045549 | 0.0011416
71 | 0.9714 | -0.20142 | 0.000494 | 0.00012381
72 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.025243 | -0.0063264 | 0.025257 | 0.0063316 | 1.397e-05 | 5.1867e-06 | 0.038615 | 0.038615 | 0.038615 | 0.97271 | -0.19173 | 0.97327 | -0.18774 | 14.3019
1 | -0.046763 | -0.011721 | 0.046796 | 0.011734 | 3.3625e-05 | 1.2802e-05 | 0.071495 | 0.071495 | 0.071495 | 0.97327 | -0.18774 | 0.97399 | -0.18255 | 26.4797
2 | 0.021506 | 0.0053895 | -0.021505 | -0.0053889 | 1.4693e-06 | 5.3806e-07 | 0.03288 | 0.03288 | 0.03288 | 0.97327 | -0.18774 | 0.9732 | -0.18823 | 12.1779
3 | -0.046796 | -0.011734 | 0.047108 | 0.011852 | 0.00031142 | 0.00011855 | 0.071495 | 0.071495 | 0.071495 | 0.97399 | -0.18255 | 0.98068 | -0.13484 | 26.4797
4 | 0.013603 | 0.0034091 | -0.013597 | -0.003407 | 6.2634e-06 | 2.1208e-06 | 0.020799 | 0.020799 | 0.020799 | 0.9732 | -0.18823 | 0.97274 | -0.19156 | 7.7035
5 | 0.0079015 | 0.0019798 | -0.0078987 | -0.0019791 | 2.7447e-06 | 6.8132e-07 | 0.012081 | 0.012081 | 0.012081 | 0.9732 | -0.18823 | 0.97285 | -0.19074 | 4.4745
6 | -0.050236 | -0.012636 | 0.050319 | 0.012667 | 8.2369e-05 | 3.0532e-05 | 0.076242 | 0.076242 | 0.076242 | 0.98068 | -0.13484 | 0.98234 | -0.12311 | 14.1189
7 | 0.011102 | 0.0027818 | -0.011097 | -0.0027802 | 5.2592e-06 | 1.6602e-06 | 0.016983 | 0.016983 | 0.016983 | 0.97274 | -0.19156 | 0.97226 | -0.19498 | 6.2902
8 | 0.0024946 | 0.00062514 | -0.0024945 | -0.00062519 | 4.8391e-08 | -4.7497e-08 | 0.003816 | 0.003816 | 0.003816 | 0.97274 | -0.19156 | 0.97272 | -0.1917 | 1.4133
9 | 0.005011 | 0.0012554 | -0.00501 | -0.0012554 | 1.0639e-06 | 4.8894e-08 | 0.0076644 | 0.0076645 | 0.0076645 | 0.97285 | -0.19074 | 0.97264 | -0.19228 | 2.8387
10 | 0.0096966 | 0.0024292 | -0.0096936 | -0.0024283 | 2.9751e-06 | 8.7587e-07 | 0.01484 | 0.01484 | 0.01484 | 0.97226 | -0.19498 | 0.97195 | -0.1972 | 5.4963
11 | -0.0064508 | -0.0016159 | 0.0064557 | 0.0016168 | 4.9159e-06 | 8.919e-07 | 0.0098833 | 0.009883 | 0.0098833 | 0.97119 | -0.20271 | 0.97195 | -0.1972 | 3.6605
12 | 0.0064508 | 0.0016159 | -0.0064474 | -0.0016153 | 3.4045e-06 | 6.1866e-07 | 0.0098833 | 0.0098836 | 0.0098836 | 0.97119 | -0.20271 | 0.97066 | -0.20653 | 3.6606
13 | 0.0064474 | 0.0016153 | -0.0064461 | -0.0016151 | 1.2962e-06 | 2.3574e-07 | 0.0098836 | 0.0098837 | 0.0098837 | 0.97066 | -0.20653 | 0.97046 | -0.20798 | 3.6606
14 | -0.0058808 | -0.0014737 | 0.0058842 | 0.0014741 | 3.4264e-06 | 3.7873e-07 | 0.0087559 | 0.0087556 | 0.0087559 | 0.9994 | -0.0042097 | 1 | 0 | 3.2429
15 | 0.0058808 | 0.0014737 | -0.0058797 | -0.0014736 | 1.0576e-06 | 1.1714e-07 | 0.0087559 | 0.008756 | 0.008756 | 0.9994 | -0.0042097 | 0.99921 | -0.005509 | 3.243
16 | 0.0066032 | 0.0016548 | -0.0066027 | -0.0016548 | 5.3376e-07 | 8.9066e-08 | 0.0098257 | 0.0098257 | 0.0098257 | 1 | 0 | 0.99992 | -0.00058396 | 3.6392
17 | 0.16243 | 0.041149 | -0.16171 | -0.040877 | 0.00071283 | 0.00027187 | 0.24185 | 0.24185 | 0.24185 | 1 | 0 | 0.99547 | -0.031159 | 29.8581
18 | 0.0066027 | 0.0016548 | -0.0066023 | -0.0016547 | 4.5125e-07 | 7.5313e-08 | 0.0098257 | 0.0098258 | 0.0098258 | 0.99992 | -0.00058396 | 0.99985 | -0.0010777 | 3.6392
19 | 0.16013 | 0.040479 | -0.15975 | -0.040334 | 0.00037873 | 0.00014443 | 0.23948 | 0.23948 | 0.23948 | 0.99547 | -0.031159 | 0.99305 | -0.04799 | 29.565
20 | -0.053497 | -0.013464 | 0.053624 | 0.013509 | 0.00012614 | 4.5001e-05 | 0.081057 | 0.081055 | 0.081057 | 0.98234 | -0.12311 | 0.98473 | -0.10625 | 10.007
21 | 0.0024834 | 0.00062214 | -0.0024832 | -0.00062235 | 2.0493e-07 | -2.0354e-07 | 0.0037992 | 0.0037993 | 0.0037993 | 0.97264 | -0.19228 | 0.97256 | -0.19287 | 1.4071
22 | -0.0034123 | -0.00085495 | 0.0034127 | 0.00085481 | 4.221e-07 | -1.4287e-07 | 0.0052327 | 0.0052326 | 0.0052327 | 0.97034 | -0.20888 | 0.97046 | -0.20798 | 1.938
23 | 0.0034123 | 0.00085495 | -0.0034119 | -0.0008551 | 4.1997e-07 | -1.4205e-07 | 0.0052327 | 0.0052328 | 0.0052328 | 0.97034 | -0.20888 | 0.97021 | -0.20976 | 1.9381
24 | -0.08681 | -0.021846 | 0.086974 | 0.021907 | 0.00016316 | 6.0997e-05 | 0.13095 | 0.13095 | 0.13095 | 0.98665 | -0.092698 | 0.98857 | -0.079258 | 16.1673
25 | 0.076097 | 0.019161 | -0.076069 | -0.019151 | 2.8017e-05 | 1.0384e-05 | 0.1148 | 0.1148 | 0.1148 | 0.98665 | -0.092698 | 0.98628 | -0.095334 | 14.1725
26 | 0.010714 | 0.002685 | -0.010708 | -0.0026833 | 5.433e-06 | 1.6639e-06 | 0.016158 | 0.016158 | 0.016158 | 0.98665 | -0.092698 | 0.98614 | -0.096363 | 5.9844
27 | -0.15747 | -0.039673 | 0.1577 | 0.039762 | 0.00023134 | 8.8216e-05 | 0.2371 | 0.2371 | 0.2371 | 0.98857 | -0.079258 | 0.99006 | -0.068772 | 29.2721
28 | 0.070498 | 0.017766 | -0.070303 | -0.017692 | 0.0001947 | 7.4532e-05 | 0.10615 | 0.10615 | 0.10615 | 0.98857 | -0.079258 | 0.98575 | -0.099045 | 39.315
29 | 0.022363 | 0.005613 | -0.022323 | -0.0055983 | 4.0174e-05 | 1.4731e-05 | 0.033743 | 0.033743 | 0.033743 | 0.98628 | -0.095334 | 0.98445 | -0.10829 | 12.4974
30 | 0.053706 | 0.013538 | -0.053624 | -0.013509 | 8.2009e-05 | 2.9248e-05 | 0.081055 | 0.081055 | 0.081055 | 0.98628 | -0.095334 | 0.98473 | -0.10625 | 10.0068
31 | 0.0099447 | 0.002492 | -0.0099418 | -0.0024911 | 2.8737e-06 | 8.4443e-07 | 0.015006 | 0.015006 | 0.015006 | 0.98614 | -0.096363 | 0.98584 | -0.098451 | 5.5577
32 | -0.1577 | -0.039762 | 0.15816 | 0.039937 | 0.00046056 | 0.00017562 | 0.2371 | 0.2371 | 0.2371 | 0.99006 | -0.068772 | 0.99305 | -0.04799 | 29.2721
33 | 0.066483 | 0.016734 | -0.066269 | -0.016652 | 0.00021424 | 8.1968e-05 | 0.10038 | 0.10038 | 0.10038 | 0.98575 | -0.099045 | 0.98247 | -0.1222 | 37.1791
34 | 0.021235 | 0.0053256 | -0.021224 | -0.0053214 | 1.1562e-05 | 4.2184e-06 | 0.032099 | 0.032099 | 0.032099 | 0.98445 | -0.10829 | 0.9839 | -0.11222 | 11.8884
35 | -0.0026057 | -0.00065305 | 0.0026061 | 0.00065271 | 3.6498e-07 | -3.3439e-07 | 0.0039483 | 0.0039482 | 0.0039483 | 0.98201 | -0.12567 | 0.98215 | -0.12465 | 1.4623
36 | -0.0080292 | -0.0020119 | 0.0080316 | 0.0020125 | 2.4674e-06 | 6.1072e-07 | 0.012164 | 0.012164 | 0.012164 | 0.98215 | -0.12465 | 0.98246 | -0.12243 | 4.5054
37 | -0.0023939 | -0.00059996 | 0.0023941 | 0.00059971 | 2.1491e-07 | -2.5252e-07 | 0.0036165 | 0.0036164 | 0.0036165 | 0.98495 | -0.10483 | 0.98504 | -0.10418 | 1.3395
38 | -0.0048874 | -0.0012246 | 0.0048884 | 0.0012246 | 9.6865e-07 | 9.9534e-09 | 0.007383 | 0.0073828 | 0.007383 | 0.98504 | -0.10418 | 0.98524 | -0.10275 | 2.7344
39 | 0.02056 | 0.005155 | -0.020543 | -0.0051491 | 1.6283e-05 | 5.9201e-06 | 0.031095 | 0.031095 | 0.031095 | 0.9839 | -0.11222 | 0.98309 | -0.11794 | 11.5166
40 | -0.012101 | -0.0030324 | 0.012104 | 0.0030333 | 2.9902e-06 | 9.6938e-07 | 0.018328 | 0.018328 | 0.018328 | 0.98246 | -0.12243 | 0.98271 | -0.12065 | 6.7881
41 | -0.016424 | -0.0041161 | 0.01643 | 0.0041183 | 6.147e-06 | 2.1624e-06 | 0.024869 | 0.024869 | 0.024869 | 0.98271 | -0.12065 | 0.98309 | -0.11794 | 9.2109
42 | -0.0072632 | -0.0018198 | 0.0072647 | 0.0018201 | 1.5051e-06 | 3.2355e-07 | 0.01097 | 0.010969 | 0.01097 | 0.98524 | -0.10275 | 0.98545 | -0.10125 | 4.0628
43 | -0.008294 | -0.0020781 | 0.0082946 | 0.0020782 | 6.4542e-07 | 1.6421e-07 | 0.012524 | 0.012524 | 0.012524 | 0.98545 | -0.10125 | 0.98553 | -0.10069 | 4.6384
44 | -0.009108 | -0.0022821 | 0.0091108 | 0.0022829 | 2.8231e-06 | 7.8085e-07 | 0.013752 | 0.013752 | 0.013752 | 0.98553 | -0.10069 | 0.98584 | -0.098451 | 5.0932
45 | 0.060375 | 0.015175 | -0.060309 | -0.01515 | 6.5695e-05 | 2.5108e-05 | 0.091457 | 0.091457 | 0.091457 | 0.98247 | -0.1222 | 0.98137 | -0.13002 | 33.8729
46 | -0.014112 | -0.0035371 | 0.014113 | 0.0035376 | 1.3563e-06 | 4.6389e-07 | 0.021602 | 0.021602 | 0.021602 | 0.9721 | -0.1963 | 0.9722 | -0.1956 | 8.0006
47 | 0.01054 | 0.0026419 | -0.01053 | -0.0026388 | 9.9837e-06 | 3.0786e-06 | 0.016134 | 0.016134 | 0.016134 | 0.9721 | -0.1963 | 0.97115 | -0.20314 | 5.9755
48 | -0.015064 | -0.0037758 | 0.01507 | 0.0037779 | 6.0917e-06 | 2.1152e-06 | 0.023056 | 0.023056 | 0.023056 | 0.9722 | -0.1956 | 0.9726 | -0.19269 | 8.5394
49 | 0.0028169 | 0.00070575 | -0.0028169 | -0.00070578 | 4.2775e-08 | -2.9079e-08 | 0.0043161 | 0.0043161 | 0.0043161 | 0.97115 | -0.20314 | 0.97114 | -0.20325 | 1.5986
50 | -0.015449 | -0.0038727 | 0.015454 | 0.0038743 | 4.5163e-06 | 1.5762e-06 | 0.023636 | 0.023636 | 0.023636 | 0.9726 | -0.19269 | 0.9729 | -0.19058 | 8.7541
51 | 0.00037902 | 9.475e-05 | -0.00037901 | -9.4989e-05 | 4.0628e-09 | -2.3878e-07 | 0.00057978 | 0.00057987 | 0.00057987 | 0.9726 | -0.19269 | 0.97259 | -0.19276 | 0.21477
52 | 0.00095312 | 0.00023867 | -0.0009531 | -0.00023887 | 2.242e-08 | -1.9982e-07 | 0.0014603 | 0.0014604 | 0.0014604 | 0.97114 | -0.20325 | 0.97111 | -0.20342 | 0.54089
53 | -0.018125 | -0.0045438 | 0.018136 | 0.0045478 | 1.1351e-05 | 4.0717e-06 | 0.027722 | 0.027722 | 0.027722 | 0.9729 | -0.19058 | 0.97352 | -0.18606 | 10.2673
54 | 0.00022804 | 5.6766e-05 | -0.00022804 | -5.7152e-05 | 2.3551e-09 | -3.855e-07 | 0.00034842 | 0.00034856 | 0.00034856 | 0.97352 | -0.18606 | 0.97351 | -0.18613 | 0.12909
55 | -0.018364 | -0.0046046 | 0.01839 | 0.0046139 | 2.5771e-05 | 9.2592e-06 | 0.02807 | 0.02807 | 0.02807 | 0.97352 | -0.18606 | 0.97493 | -0.17594 | 10.3963
56 | 0.023941 | 0.0060066 | -0.023889 | -0.0059874 | 5.2057e-05 | 1.9224e-05 | 0.036303 | 0.036303 | 0.036303 | 0.98137 | -0.13002 | 0.97917 | -0.14573 | 13.4457
57 | 0.036368 | 0.0091432 | -0.036279 | -0.0091094 | 8.9494e-05 | 3.3827e-05 | 0.055154 | 0.055154 | 0.055154 | 0.98137 | -0.13002 | 0.97888 | -0.14773 | 20.4274
58 | 0.015989 | 0.0040074 | -0.015987 | -0.0040068 | 1.7029e-06 | 5.9683e-07 | 0.024298 | 0.024298 | 0.024298 | 0.97917 | -0.14573 | 0.97906 | -0.1465 | 8.9992
59 | 0.034073 | 0.0085567 | -0.034067 | -0.0085542 | 6.6185e-06 | 2.4959e-06 | 0.051802 | 0.051802 | 0.051802 | 0.97888 | -0.14773 | 0.97868 | -0.14913 | 19.1859
60 | 0.010176 | 0.0025504 | -0.010174 | -0.0025498 | 2.0445e-06 | 6.1411e-07 | 0.015466 | 0.015466 | 0.015466 | 0.97906 | -0.1465 | 0.97886 | -0.14795 | 5.728
61 | 0.03167 | 0.0079534 | -0.0316 | -0.0079273 | 6.9584e-05 | 2.616e-05 | 0.048157 | 0.048158 | 0.048158 | 0.97868 | -0.14913 | 0.97647 | -0.16497 | 17.8361
62 | 0.0092877 | 0.0023277 | -0.0092855 | -0.0023271 | 2.2665e-06 | 6.4275e-07 | 0.014119 | 0.014119 | 0.014119 | 0.97886 | -0.14795 | 0.97861 | -0.14971 | 5.2292
63 | 0.030656 | 0.0076906 | -0.030628 | -0.0076801 | 2.7938e-05 | 1.0489e-05 | 0.046718 | 0.046718 | 0.046718 | 0.97647 | -0.16497 | 0.97555 | -0.17155 | 17.3031
64 | -0.019022 | -0.0047723 | 0.019034 | 0.0047765 | 1.1605e-05 | 4.188e-06 | 0.029035 | 0.029035 | 0.029035 | 0.97493 | -0.17594 | 0.97555 | -0.17155 | 10.7537
65 | 0.011594 | 0.0029036 | -0.01158 | -0.0028991 | 1.3848e-05 | 4.4412e-06 | 0.017683 | 0.017684 | 0.017684 | 0.97555 | -0.17155 | 0.97435 | -0.1802 | 6.5495
66 | 0.0050637 | 0.001266 | -0.0050588 | -0.0012658 | 4.9518e-06 | 2.5319e-07 | 0.0077322 | 0.0077328 | 0.0077328 | 0.97435 | -0.1802 | 0.97336 | -0.18729 | 2.864
67 | 0.0050588 | 0.0012658 | -0.0050532 | -0.0012655 | 5.5232e-06 | 2.8664e-07 | 0.0077328 | 0.0077334 | 0.0077334 | 0.97336 | -0.18729 | 0.97227 | -0.1952 | 2.8642
68 | 0.0050532 | 0.0012655 | -0.0050489 | -0.0012652 | 4.3011e-06 | 2.263e-07 | 0.0077334 | 0.007734 | 0.007734 | 0.97227 | -0.1952 | 0.97141 | -0.20136 | 2.8644
69 | 0.0015245 | 0.000382 | -0.0015245 | -0.00038208 | 2.2258e-08 | -7.484e-08 | 0.0023181 | 0.0023181 | 0.0023181 | 0.97861 | -0.14971 | 0.9786 | -0.14982 | 0.85856
70 | 0.000494 | 0.00012367 | -0.000494 | -0.00012381 | 3.985e-09 | -1.3654e-07 | 0.00075666 | 0.00075671 | 0.00075671 | 0.97141 | -0.20136 | 0.9714 | -0.20142 | 0.28026

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17571 | 0.044278

## res_load
| p_mw | q_mvar
0 | 0.025243 | 0.0063264
1 | 0.0031286 | 0.0007841
2 | 0.0028877 | 0.00072372
3 | 0.0014006 | 0.00035102
4 | 0.0024945 | 0.00062519
5 | 0.0032379 | 0.00081149
6 | 0.0058797 | 0.0014736
7 | 0.0015885 | 0.00039811
8 | 0.0031787 | 0.00079667
9 | 0.0025266 | 0.00063322
10 | 0.0030334 | 0.00076024
11 | 0.0034119 | 0.0008551
12 | 0.00076349 | 0.00019135
13 | 0.0038203 | 0.00095746
14 | 0.0015839 | 0.00039695
15 | 0.0066023 | 0.0016547
16 | 0.0024832 | 0.00062235
17 | 0.0010879 | 0.00027266
18 | 0.0026057 | 0.00065305
19 | 0.0054231 | 0.0013592
20 | 0.0023939 | 0.00059996
21 | 0.0024934 | 0.0006249
22 | 0.00066392 | 0.00016639
23 | 0.0040694 | 0.0010199
24 | 0.0043203 | 0.0010828
25 | 0.0041129 | 0.0010308
26 | 0.0023748 | 0.00059518
27 | 0.0010293 | 0.00025796
28 | 0.0008134 | 0.00020386
29 | 0.00083096 | 0.00020826
30 | 0.0058941 | 0.0014772
31 | 0.0035722 | 0.00089528
32 | 0.00095048 | 0.00023821
33 | 0.0077129 | 0.001933
34 | 0.0018638 | 0.00046711
35 | 0.0026713 | 0.00066949
36 | 0.00037901 | 9.4989e-05
37 | 0.0009531 | 0.00023887
38 | 0.0079002 | 0.00198
39 | 0.0022051 | 0.00055266
40 | 0.0058113 | 0.0014564
41 | 0.0023971 | 0.00060078
42 | 0.00088595 | 0.00022204
43 | 0.0009445 | 0.00023671
44 | 0.00022804 | 5.7152e-05
45 | 0.0006323 | 0.00015847
46 | 0.0065162 | 0.0016331
47 | 0.0077609 | 0.0019451
48 | 0.0015245 | 0.00038208
49 | 0.0045549 | 0.0011416
50 | 0.000494 | 0.00012381

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1