## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1127-3_2_3_node_6 | 0.4 | n |  | TRUE
1 | bus_LV_1127-3_2_3_node_8 | 0.4 | n |  | TRUE
2 | bus_LV_1127-3_2_3_node_9 | 0.4 | n |  | TRUE
3 | bus_LV_1127-3_2_3_node_34 | 0.4 | n |  | TRUE
4 | bus_LV_1127-3_2_3_node_23 | 0.4 | n |  | TRUE
5 | bus_LV_1127-3_2_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1127-3_2_3_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1127-3_2_3_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_1127-3_2_3_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1127-3_2_3_node_44 | 0.4 | n |  | TRUE
10 | bus_LV_1127-3_2_3_node_62 | 0.4 | n |  | TRUE
11 | bus_LV_1127-3_2_3_node_61 | 0.4 | n |  | TRUE
12 | bus_LV_1127-3_2_3_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_1127-3_2_3_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1127-3_2_3_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_1127-3_2_3_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1127-3_2_3_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_1127-3_2_3_node_46 | 0.4 | n |  | TRUE
18 | bus_LV_1127-3_2_3_node_49 | 0.4 | n |  | TRUE
19 | bus_LV_1127-3_2_3_node_50 | 0.4 | n |  | TRUE
20 | bus_LV_1127-3_2_3_node_51 | 0.4 | n |  | TRUE
21 | bus_LV_1127-3_2_3_node_52 | 0.4 | n |  | TRUE
22 | bus_LV_1127-3_2_3_node_53 | 0.4 | n |  | TRUE
23 | bus_LV_1127-3_2_3_node_60 | 0.4 | n |  | TRUE
24 | bus_LV_1127-3_2_3_node_59 | 0.4 | n |  | TRUE
25 | bus_LV_1127-3_2_3_node_68 | 0.4 | n |  | TRUE
26 | bus_LV_1127-3_2_3_node_66 | 0.4 | n |  | TRUE
27 | bus_LV_1127-3_2_3_node_84 | 0.4 | n |  | TRUE
28 | bus_LV_1127-3_2_3_node_67 | 0.4 | n |  | TRUE
29 | bus_LV_1127-3_2_3_node_69 | 0.4 | n |  | TRUE
30 | bus_LV_1127-3_2_3_node_70 | 0.4 | n |  | TRUE
31 | bus_LV_1127-3_2_3_node_78 | 0.4 | n |  | TRUE
32 | bus_LV_1127-3_2_3_node_79 | 0.4 | n |  | TRUE
33 | bus_MV_131_0_node_7 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1127-3_2_3_load_8 | 1 | 0.0029454 | 0.00073819 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1127-3_2_3_load_9 | 2 | 0.0021691 | 0.00054362 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1127-3_2_3_load_34 | 3 | 0.0017523 | 0.00043917 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1127-3_2_3_load_23 | 4 | 0.0021555 | 0.00054021 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1127-3_2_3_load_10 | 5 | 0.011644 | 0.0029182 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1127-3_2_3_load_44 | 9 | 0.0070859 | 0.0017759 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1127-3_2_3_load_61 | 11 | 0.0037614 | 0.0009427 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1127-3_2_3_load_14 | 12 | 0.003274 | 0.00082055 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1127-3_2_3_load_20 | 13 | 0.006912 | 0.0017323 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1127-3_2_3_load_21 | 14 | 0.0022883 | 0.0005735 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1127-3_2_3_load_22 | 15 | 0.003566 | 0.00089371 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1127-3_2_3_load_24 | 16 | 0.001567 | 0.00039274 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1127-3_2_3_load_46 | 17 | 0.0033166 | 0.00083122 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1127-3_2_3_load_49 | 18 | 0.0027413 | 0.00068704 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1127-3_2_3_load_50 | 19 | 0.0026449 | 0.00066287 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1127-3_2_3_load_51 | 20 | 0.0026549 | 0.00066537 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1127-3_2_3_load_52 | 21 | 0.0055587 | 0.0013931 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1127-3_2_3_load_53 | 22 | 0.0031543 | 0.00079053 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1127-3_2_3_load_60 | 23 | 0.0066524 | 0.0016673 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1127-3_2_3_load_59 | 24 | 0.0033939 | 0.00085058 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1127-3_2_3_load_68 | 25 | 0.0029885 | 0.00074898 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1127-3_2_3_load_66 | 26 | 0.0024787 | 0.00062123 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1127-3_2_3_load_84 | 27 | 0.0017462 | 0.00043764 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1127-3_2_3_load_67 | 28 | 0.0011114 | 0.00027853 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1127-3_2_3_load_69 | 29 | 0.0028224 | 0.00070735 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1127-3_2_3_load_70 | 30 | 0.004212 | 0.0010556 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1127-3_2_3_load_78 | 31 | 0.0038742 | 0.00097096 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1127-3_2_3_load_79 | 32 | 0.0019867 | 0.00049793 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1127-3_2_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.010255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1127-3_2_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.032801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1127-3_2_3_line_2 | NAYY 4x150 SE | 0 | 3 | 0.032932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1127-3_2_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0001893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1127-3_2_3_line_4 | NAYY 4x150 SE | 3 | 12 | 0.028331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1127-3_2_3_line_5 | NAYY 4x150 SE | 4 | 14 | 0.011266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1127-3_2_3_line_6 | NAYY 4x150 SE | 5 | 6 | 0.082128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1127-3_2_3_line_7 | NAYY 4x150 SE | 5 | 7 | 0.035943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1127-3_2_3_line_8 | NAYY 4x150 SE | 6 | 8 | 0.23423 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1127-3_2_3_line_9 | NAYY 4x150 SE | 7 | 9 | 0.033585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1127-3_2_3_line_10 | NAYY 4x150 SE | 8 | 10 | 0.009402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1127-3_2_3_line_11 | NAYY 4x150 SE | 8 | 11 | 0.071122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1127-3_2_3_line_12 | NAYY 4x150 SE | 9 | 17 | 0.0014128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1127-3_2_3_line_13 | NAYY 4x150 SE | 9 | 16 | 0.014632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1127-3_2_3_line_14 | NAYY 4x150 SE | 10 | 25 | 0.073592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1127-3_2_3_line_15 | NAYY 4x150 SE | 11 | 21 | 0.028599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1127-3_2_3_line_16 | NAYY 4x150 SE | 13 | 14 | 0.017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1127-3_2_3_line_17 | NAYY 4x150 SE | 13 | 15 | 0.0024806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1127-3_2_3_line_18 | NAYY 4x150 SE | 15 | 16 | 0.010421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1127-3_2_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.014155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1127-3_2_3_line_20 | NAYY 4x150 SE | 18 | 20 | 0.018035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1127-3_2_3_line_21 | NAYY 4x150 SE | 19 | 21 | 0.024142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1127-3_2_3_line_22 | NAYY 4x150 SE | 20 | 22 | 0.020428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1127-3_2_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.0090941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1127-3_2_3_line_24 | NAYY 4x150 SE | 23 | 24 | 0.01457 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1127-3_2_3_line_25 | NAYY 4x150 SE | 25 | 28 | 0.0026291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1127-3_2_3_line_26 | NAYY 4x150 SE | 26 | 27 | 0.025739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1127-3_2_3_line_27 | NAYY 4x150 SE | 27 | 32 | 0.014754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1127-3_2_3_line_28 | NAYY 4x150 SE | 28 | 29 | 0.016616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1127-3_2_3_line_29 | NAYY 4x150 SE | 29 | 30 | 0.009388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1127-3_2_3_line_30 | NAYY 4x150 SE | 30 | 31 | 0.02007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1127-3_2_3_line_31 | NAYY 4x150 SE | 31 | 32 | 0.0081488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1127-3_2_3_trafo_50 | 0.25 MVA 20/0.4 kV | 33 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2642695.6051 | 1226268.3321 | 2642695.753 | 1226270.957 | 2642694.1049 | 1226274.5918 | 2642691.3914 | 1226277.0104
1 | 2642695.6051 | 1226268.3321 | 2642728.405 | 1226268.1276
2 | 2642692.1588 | 1226235.5806 | 2642695.6051 | 1226268.3321
3 | 2642728.405 | 1226268.1276 | 2642728.5943 | 1226268.1264
4 | 2642720.4863 | 1226235.1554 | 2642692.1588 | 1226235.5806
5 | 2642728.5943 | 1226268.1264 | 2642739.8597 | 1226268.0562
6 | 2642902.5976 | 1226233.0312 | 2642881.1813 | 1226233.5996 | 2642849.1907 | 1226234.292 | 2642820.4861 | 1226233.9891
7 | 2642784.5456 | 1226234.1939 | 2642809.4466 | 1226233.8726 | 2642820.4861 | 1226233.9891
8 | 2642897.9672 | 1226329.6793 | 2642920.5545 | 1226315.9225 | 2642973.8172 | 1226282.0525 | 2642977.4419 | 1226278.6543 | 2642979.4858 | 1226273.7661 | 2642984.9257 | 1226247.8339 | 2642985.5896 | 1226239.8672 | 2642985.162 | 1226235.05 | 2642982.6845 | 1226221.257 | 2642975.6634 | 1226222.6517 | 2642967.1242 | 1226224.3466 | 2642944.6037 | 1226228.7758 | 2642919.8113 | 1226231.899 | 2642902.5976 | 1226233.0312
9 | 2642784.5456 | 1226234.1939 | 2642784.3934 | 1226267.7786
10 | 2642897.9672 | 1226329.6793 | 2642889.9205 | 1226334.5799
11 | 2642897.9672 | 1226329.6793 | 2642886.0309 | 1226328.4592 | 2642832.9238 | 1226335.5814 | 2642827.4927 | 1226336.6772
12 | 2642785.8062 | 1226267.7698 | 2642784.3934 | 1226267.7786
13 | 2642784.3934 | 1226267.7786 | 2642769.7612 | 1226267.8698
14 | 2642889.9205 | 1226334.5799 | 2642864.0522 | 1226350.3366 | 2642848.1034 | 1226357.9487 | 2642826.6943 | 1226366.0219 | 2642824.2547 | 1226367.2901
15 | 2642827.4927 | 1226336.6772 | 2642816.4298 | 1226338.9093 | 2642799.6039 | 1226342.9872
16 | 2642756.8597 | 1226267.9502 | 2642739.8597 | 1226268.0562
17 | 2642759.3402 | 1226267.9348 | 2642756.8597 | 1226267.9502
18 | 2642759.3402 | 1226267.9348 | 2642769.7612 | 1226267.8698
19 | 2642762.3847 | 1226352.0076 | 2642776.141 | 1226348.6736
20 | 2642762.3847 | 1226352.0076 | 2642754.7246 | 1226353.8641 | 2642744.7379 | 1226355.6933
21 | 2642776.141 | 1226348.6736 | 2642799.6039 | 1226342.9872
22 | 2642744.7379 | 1226355.6933 | 2642740.8816 | 1226356.3996 | 2642724.4485 | 1226357.9695
23 | 2642715.3956 | 1226358.8344 | 2642724.4485 | 1226357.9695
24 | 2642700.892 | 1226360.22 | 2642715.3956 | 1226358.8344
25 | 2642821.922 | 1226368.5028 | 2642824.2547 | 1226367.2901
26 | 2642744.7392 | 1226422.9295 | 2642752.4057 | 1226418.1757 | 2642765.408 | 1226407.6667
27 | 2642776.8824 | 1226398.3926 | 2642765.408 | 1226407.6667
28 | 2642821.922 | 1226368.5028 | 2642808.4051 | 1226375.5296 | 2642807.2505 | 1226376.2879
29 | 2642799.4036 | 1226381.4415 | 2642807.2505 | 1226376.2879
30 | 2642799.4036 | 1226381.4415 | 2642791.1412 | 1226386.868 | 2642783.22 | 1226393.2703
31 | 2642783.22 | 1226393.2703 | 2642776.8824 | 1226398.3926

## bus_geodata
| x | y | coords
0 | 2642695.6051 | 1226268.3321
1 | 2642691.3914 | 1226277.0104
2 | 2642728.405 | 1226268.1276
3 | 2642692.1588 | 1226235.5806
4 | 2642728.5943 | 1226268.1264
5 | 2642820.4861 | 1226233.9891
6 | 2642902.5976 | 1226233.0312
7 | 2642784.5456 | 1226234.1939
8 | 2642897.9672 | 1226329.6793
9 | 2642784.3934 | 1226267.7786
10 | 2642889.9205 | 1226334.5799
11 | 2642827.4927 | 1226336.6772
12 | 2642720.4863 | 1226235.1554
13 | 2642756.8597 | 1226267.9502
14 | 2642739.8597 | 1226268.0562
15 | 2642759.3402 | 1226267.9348
16 | 2642769.7612 | 1226267.8698
17 | 2642785.8062 | 1226267.7698
18 | 2642762.3847 | 1226352.0076
19 | 2642776.141 | 1226348.6736
20 | 2642744.7379 | 1226355.6933
21 | 2642799.6039 | 1226342.9872
22 | 2642724.4485 | 1226357.9695
23 | 2642715.3957 | 1226358.8344
24 | 2642700.892 | 1226360.22
25 | 2642824.2547 | 1226367.2901
26 | 2642744.7392 | 1226422.9295
27 | 2642765.408 | 1226407.6667
28 | 2642821.922 | 1226368.5028
29 | 2642807.2505 | 1226376.2879
30 | 2642799.4036 | 1226381.4415
31 | 2642783.22 | 1226393.2703
32 | 2642776.8824 | 1226398.3926
33 | 2642897.9672 | 1226329.6793

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97355 | -0.18594 | 0 | 0
1 | 0.9735 | -0.18626 | 0.0029454 | 0.00073819
2 | 0.97393 | -0.18319 | 0.0021691 | 0.00054362
3 | 0.97331 | -0.18769 | 0.0017523 | 0.00043917
4 | 0.97393 | -0.18317 | 0.0021555 | 0.00054021
5 | 0.9793 | -0.14479 | 0.011644 | 0.0029182
6 | 0.98514 | -0.10342 | 0 | 0
7 | 0.97735 | -0.15868 | 0 | 0
8 | 0.99347 | -0.045221 | 0 | 0
9 | 0.97553 | -0.1717 | 0.0070859 | 0.0017759
10 | 0.99318 | -0.047241 | 0 | 0
11 | 0.99708 | -0.020143 | 0.0037614 | 0.0009427
12 | 0.97317 | -0.18867 | 0.003274 | 0.00082055
13 | 0.9745 | -0.1791 | 0.006912 | 0.0017323
14 | 0.97414 | -0.18171 | 0.0022883 | 0.0005735
15 | 0.97458 | -0.17854 | 0.003566 | 0.00089371
16 | 0.97496 | -0.1758 | 0.001567 | 0.00039274
17 | 0.97552 | -0.17175 | 0.0033166 | 0.00083122
18 | 0.99962 | -0.0026291 | 0.0027413 | 0.00068704
19 | 1 | 0 | -0.10003 | -0.025044
20 | 0.99922 | -0.0054871 | 0.0026549 | 0.00066537
21 | 0.99861 | -0.0095703 | 0.0055587 | 0.0013931
22 | 0.99883 | -0.0081844 | 0.0031543 | 0.00079053
23 | 0.9987 | -0.0090987 | 0.0066524 | 0.0016673
24 | 0.99863 | -0.0095936 | 0.0033939 | 0.00085058
25 | 0.99093 | -0.063087 | 0.0029885 | 0.00074898
26 | 0.98971 | -0.071698 | 0.0024787 | 0.00062123
27 | 0.9898 | -0.071048 | 0.0017462 | 0.00043764
28 | 0.99086 | -0.063574 | 0.0011114 | 0.00027853
29 | 0.99045 | -0.066468 | 0.0028224 | 0.00070735
30 | 0.99026 | -0.067835 | 0.004212 | 0.0010556
31 | 0.98997 | -0.069897 | 0.0038742 | 0.00097096
32 | 0.98989 | -0.070413 | 0.0019867 | 0.00049793
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0029455 | 0.00073811 | -0.0029454 | -0.00073819 | 1.297e-07 | -7.7624e-08 | 0.004502 | 0.0045021 | 0.0045021 | 0.97355 | -0.18594 | 0.9735 | -0.18626 | 1.6674
1 | -0.0079735 | -0.0019977 | 0.0079765 | 0.0019985 | 3.0398e-06 | 7.6113e-07 | 0.012187 | 0.012187 | 0.012187 | 0.97355 | -0.18594 | 0.97393 | -0.18319 | 4.5136
2 | 0.005028 | 0.0012596 | -0.0050268 | -0.0012595 | 1.2136e-06 | 5.7383e-08 | 0.0076848 | 0.0076849 | 0.0076849 | 0.97355 | -0.18594 | 0.97331 | -0.18769 | 2.8463
3 | -0.010146 | -0.0025421 | 0.010146 | 0.0025421 | 2.8382e-08 | 8.5604e-09 | 0.015501 | 0.015501 | 0.015501 | 0.97393 | -0.18319 | 0.97393 | -0.18317 | 5.741
4 | 0.0032745 | 0.00082036 | -0.003274 | -0.00082055 | 4.4303e-07 | -1.8166e-07 | 0.005006 | 0.0050061 | 0.0050061 | 0.97331 | -0.18769 | 0.97317 | -0.18867 | 1.8541
5 | -0.012301 | -0.0030823 | 0.012304 | 0.0030831 | 2.483e-06 | 8.1477e-07 | 0.018794 | 0.018794 | 0.018794 | 0.97393 | -0.18317 | 0.97414 | -0.18171 | 6.9607
6 | -0.048854 | -0.012265 | 0.049136 | 0.012372 | 0.00028245 | 0.0001076 | 0.074239 | 0.074239 | 0.074239 | 0.9793 | -0.14479 | 0.98514 | -0.10342 | 27.496
7 | 0.03721 | 0.0093465 | -0.037138 | -0.0093194 | 7.1716e-05 | 2.7132e-05 | 0.056547 | 0.056547 | 0.056547 | 0.9793 | -0.14479 | 0.97735 | -0.15868 | 20.9433
8 | -0.049136 | -0.012372 | 0.049539 | 0.012521 | 0.00040276 | 0.00014889 | 0.074239 | 0.074237 | 0.074239 | 0.98514 | -0.10342 | 0.99347 | -0.045221 | 13.7479
9 | 0.037138 | 0.0093194 | -0.037071 | -0.0092941 | 6.7011e-05 | 2.5354e-05 | 0.056547 | 0.056547 | 0.056547 | 0.97735 | -0.15868 | 0.97553 | -0.1717 | 20.9433
10 | 0.021287 | 0.0053418 | -0.021281 | -0.0053397 | 5.9652e-06 | 2.1726e-06 | 0.031887 | 0.031887 | 0.031887 | 0.99347 | -0.045221 | 0.99318 | -0.047241 | 11.8099
11 | -0.070826 | -0.017863 | 0.071076 | 0.017957 | 0.00024991 | 9.4269e-05 | 0.10612 | 0.10612 | 0.10612 | 0.99347 | -0.045221 | 0.99708 | -0.020143 | 19.6525
12 | 0.0033166 | 0.00083121 | -0.0033166 | -0.00083122 | 2.2562e-08 | -8.9605e-09 | 0.005059 | 0.005059 | 0.005059 | 0.97553 | -0.1717 | 0.97552 | -0.17175 | 1.8737
13 | 0.026668 | 0.006687 | -0.026653 | -0.0066813 | 1.511e-05 | 5.6289e-06 | 0.04068 | 0.04068 | 0.04068 | 0.97553 | -0.1717 | 0.97496 | -0.1758 | 15.0665
14 | 0.021281 | 0.0053397 | -0.021235 | -0.0053227 | 4.6692e-05 | 1.7008e-05 | 0.031887 | 0.031887 | 0.031887 | 0.99318 | -0.047241 | 0.99093 | -0.063087 | 11.81
15 | -0.074837 | -0.0189 | 0.074949 | 0.018942 | 0.0001114 | 4.21e-05 | 0.11174 | 0.11174 | 0.11174 | 0.99708 | -0.020143 | 0.99861 | -0.0095703 | 20.6919
16 | 0.014597 | 0.0036584 | -0.014592 | -0.0036566 | 5.2703e-06 | 1.8153e-06 | 0.022289 | 0.022289 | 0.022289 | 0.9745 | -0.1791 | 0.97414 | -0.18171 | 8.2553
17 | -0.021509 | -0.0053907 | 0.021511 | 0.0053913 | 1.6697e-06 | 6.1128e-07 | 0.032843 | 0.032843 | 0.032843 | 0.9745 | -0.1791 | 0.97458 | -0.17854 | 12.1642
18 | -0.025077 | -0.006285 | 0.025086 | 0.0062886 | 9.533e-06 | 3.5366e-06 | 0.038288 | 0.038288 | 0.038288 | 0.97458 | -0.17854 | 0.97496 | -0.1758 | 14.1808
19 | -0.018609 | -0.0046649 | 0.018616 | 0.0046673 | 6.778e-06 | 2.4213e-06 | 0.027702 | 0.027702 | 0.027702 | 0.99962 | -0.0026291 | 1 | 0 | 10.26
20 | 0.015868 | 0.0039778 | -0.015862 | -0.0039756 | 6.2791e-06 | 2.1787e-06 | 0.023621 | 0.023621 | 0.023621 | 0.99962 | -0.0026291 | 0.99922 | -0.0054871 | 8.7486
21 | 0.080616 | 0.020376 | -0.080508 | -0.020335 | 0.0001085 | 4.1098e-05 | 0.12002 | 0.12002 | 0.12002 | 1 | 0 | 0.99861 | -0.0095703 | 22.2257
22 | 0.013207 | 0.0033103 | -0.013202 | -0.0033086 | 4.9309e-06 | 1.629e-06 | 0.019668 | 0.019668 | 0.019668 | 0.99922 | -0.0054871 | 0.99883 | -0.0081844 | 7.2844
23 | 0.010048 | 0.0025181 | -0.010047 | -0.0025177 | 1.2715e-06 | 3.7002e-07 | 0.014969 | 0.014969 | 0.014969 | 0.99883 | -0.0081844 | 0.9987 | -0.0090987 | 5.544
24 | 0.0033941 | 0.00085048 | -0.0033939 | -0.00085058 | 2.325e-07 | -1.0121e-07 | 0.005057 | 0.0050571 | 0.0050571 | 0.9987 | -0.0090987 | 0.99863 | -0.0095936 | 1.873
25 | 0.018246 | 0.0045737 | -0.018245 | -0.0045732 | 1.2316e-06 | 4.3983e-07 | 0.0274 | 0.0274 | 0.0274 | 0.99093 | -0.063087 | 0.99086 | -0.063574 | 10.148
26 | -0.0024787 | -0.00062123 | 0.0024789 | 0.00062098 | 2.2306e-07 | -2.45e-07 | 0.0037267 | 0.0037266 | 0.0037267 | 0.98971 | -0.071698 | 0.9898 | -0.071048 | 1.3803
27 | -0.0042252 | -0.0010586 | 0.0042255 | 0.0010586 | 3.7143e-07 | -4.6793e-08 | 0.0063518 | 0.0063517 | 0.0063518 | 0.9898 | -0.071048 | 0.98989 | -0.070413 | 2.3525
28 | 0.017134 | 0.0042947 | -0.017127 | -0.0042923 | 6.8644e-06 | 2.4262e-06 | 0.025731 | 0.025731 | 0.025731 | 0.99086 | -0.063574 | 0.99045 | -0.066468 | 9.5299
29 | 0.014305 | 0.0035849 | -0.014302 | -0.003584 | 2.7055e-06 | 9.1978e-07 | 0.02149 | 0.021491 | 0.021491 | 0.99045 | -0.066468 | 0.99026 | -0.067835 | 7.9595
30 | 0.01009 | 0.0025284 | -0.010087 | -0.0025275 | 2.8788e-06 | 8.491e-07 | 0.015161 | 0.015161 | 0.015161 | 0.99026 | -0.067835 | 0.98997 | -0.069897 | 5.6153
31 | 0.0062127 | 0.0015566 | -0.0062123 | -0.0015565 | 4.4341e-07 | 6.5777e-08 | 0.0093382 | 0.0093382 | 0.0093382 | 0.98997 | -0.069897 | 0.98989 | -0.070413 | 3.4586

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.10268 | 0.025707

## res_load
| p_mw | q_mvar
0 | 0.0029454 | 0.00073819
1 | 0.0021691 | 0.00054362
2 | 0.0017523 | 0.00043917
3 | 0.0021555 | 0.00054021
4 | 0.011644 | 0.0029182
5 | 0.0070859 | 0.0017759
6 | 0.0037614 | 0.0009427
7 | 0.003274 | 0.00082055
8 | 0.006912 | 0.0017323
9 | 0.0022883 | 0.0005735
10 | 0.003566 | 0.00089371
11 | 0.001567 | 0.00039274
12 | 0.0033166 | 0.00083122
13 | 0.0027413 | 0.00068704
14 | 0.0026449 | 0.00066287
15 | 0.0026549 | 0.00066537
16 | 0.0055587 | 0.0013931
17 | 0.0031543 | 0.00079053
18 | 0.0066524 | 0.0016673
19 | 0.0033939 | 0.00085058
20 | 0.0029885 | 0.00074898
21 | 0.0024787 | 0.00062123
22 | 0.0017462 | 0.00043764
23 | 0.0011114 | 0.00027853
24 | 0.0028224 | 0.00070735
25 | 0.004212 | 0.0010556
26 | 0.0038742 | 0.00097096
27 | 0.0019867 | 0.00049793

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1