## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1127-9_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1127-9_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1127-9_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1127-9_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1127-9_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1127-9_0_3_node_26 | 0.4 | n |  | TRUE
6 | bus_LV_1127-9_0_3_node_16 | 0.4 | n |  | TRUE
7 | bus_LV_1127-9_0_3_node_18 | 0.4 | n |  | TRUE
8 | bus_LV_1127-9_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1127-9_0_3_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1127-9_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1127-9_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1127-9_0_3_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1127-9_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1127-9_0_3_node_29 | 0.4 | n |  | TRUE
15 | bus_LV_1127-9_0_3_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1127-9_0_3_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_1127-9_0_3_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1127-9_0_3_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_1127-9_0_3_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1127-9_0_3_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1127-9_0_3_node_28 | 0.4 | n |  | TRUE
22 | bus_LV_1127-9_0_3_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_1127-9_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1127-9_0_3_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1127-9_0_3_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1127-9_0_3_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_1127-9_0_3_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1127-9_0_3_node_27 | 0.4 | n |  | TRUE
29 | bus_MV_131_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1127-9_0_3_load_0 | 0 | 0.0024846 | 0.0006227 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1127-9_0_3_load_1 | 1 | 0.0027932 | 0.00070004 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1127-9_0_3_load_3 | 3 | 0.0030988 | 0.00077664 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1127-9_0_3_load_26 | 5 | 0.0031749 | 0.00079569 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1127-9_0_3_load_16 | 6 | 0.0028823 | 0.00072238 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1127-9_0_3_load_18 | 7 | 0.003404 | 0.00085312 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1127-9_0_3_load_5 | 8 | 0.021087 | 0.005285 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1127-9_0_3_load_24 | 12 | 0.015138 | 0.0037938 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1127-9_0_3_load_29 | 14 | 0.0078063 | 0.0019564 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1127-9_0_3_load_20 | 17 | 0.0032223 | 0.00080757 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1127-9_0_3_load_23 | 18 | 0.01446 | 0.0036239 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1127-9_0_3_load_15 | 19 | 0.0015451 | 0.00038724 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1127-9_0_3_load_11 | 20 | 0.018708 | 0.0046886 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1127-9_0_3_load_21 | 23 | 0.020734 | 0.0051965 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1127-9_0_3_load_12 | 24 | 0.013353 | 0.0033466 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1127-9_0_3_load_14 | 25 | 0.014265 | 0.0035753 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1127-9_0_3_load_25 | 26 | 0.0027892 | 0.00069904 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1127-9_0_3_load_27 | 28 | 0.043299 | 0.010852 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1127-9_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0078578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1127-9_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.041685 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1127-9_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.03391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1127-9_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.043753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1127-9_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.037733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1127-9_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.06724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1127-9_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.014391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1127-9_0_3_line_7 | NAYY 4x150 SE | 7 | 27 | 0.023794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1127-9_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.034086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1127-9_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.001926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1127-9_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.018486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1127-9_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.004676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1127-9_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.077373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1127-9_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.15923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1127-9_0_3_line_14 | NAYY 4x150 SE | 13 | 19 | 0.030744 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1127-9_0_3_line_15 | NAYY 4x150 SE | 13 | 20 | 0.040987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1127-9_0_3_line_16 | NAYY 4x150 SE | 14 | 21 | 0.096819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1127-9_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.055854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1127-9_0_3_line_18 | NAYY 4x150 SE | 15 | 17 | 0.042794 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1127-9_0_3_line_19 | NAYY 4x150 SE | 16 | 22 | 0.003498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1127-9_0_3_line_20 | NAYY 4x150 SE | 16 | 18 | 0.10565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1127-9_0_3_line_21 | NAYY 4x150 SE | 17 | 23 | 0.032707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1127-9_0_3_line_22 | NAYY 4x150 SE | 20 | 24 | 0.027506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
23 | LV_1127-9_0_3_line_23 | NAYY 4x150 SE | 21 | 28 | 0.20244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1127-9_0_3_line_24 | NAYY 4x150 SE | 22 | 26 | 0.0030688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1127-9_0_3_line_25 | NAYY 4x150 SE | 22 | 27 | 0.23845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1127-9_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.035978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1127-9_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.024389 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1127-9_0_3_trafo_5 | 0.25 MVA 20/0.4 kV | 29 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2643363.659 | 1226276.4176 | 2643355.8014 | 1226276.4713
1 | 2643405.006 | 1226278.9218 | 2643394.2478 | 1226276.2084 | 2643363.659 | 1226276.4176
2 | 2643321.892 | 1226276.7031 | 2643355.8014 | 1226276.4713
3 | 2643405.006 | 1226278.9218 | 2643402.8742 | 1226237.6143 | 2643402.7476 | 1226235.2341
4 | 2643284.8671 | 1226271.3666 | 2643287.1395 | 1226272.3933 | 2643297.6856 | 1226275.105 | 2643307.6403 | 1226276.8006 | 2643321.892 | 1226276.7031
5 | 2643402.7476 | 1226235.2341 | 2643387.6547 | 1226232.3891 | 2643335.7735 | 1226232.5054
6 | 2643271.7521 | 1226265.441 | 2643284.8671 | 1226271.3666
7 | 2643249.644 | 1226256.7113 | 2643261.6047 | 1226260.8563 | 2643271.7521 | 1226265.441
8 | 2643352.6508 | 1226368.9289 | 2643330.9627 | 1226368.3708 | 2643318.5922 | 1226367.6587
9 | 2643352.7557 | 1226367.0063 | 2643352.6508 | 1226368.9289
10 | 2643370.9813 | 1226371.5529 | 2643359.3093 | 1226369.4444 | 2643352.6508 | 1226368.9289
11 | 2643352.7557 | 1226367.0063 | 2643353.0323 | 1226362.3388
12 | 2643420.0531 | 1226338.9349 | 2643422.7513 | 1226344.1355 | 2643423.3256 | 1226351.6554 | 2643421.5809 | 1226360.159 | 2643417.3219 | 1226366.3095 | 2643411.0927 | 1226370.3221 | 2643399.2698 | 1226373.3156 | 2643370.9813 | 1226371.5529
13 | 2643370.9813 | 1226371.5529 | 2643359.3452 | 1226373.8807 | 2643342.2171 | 1226373.7115 | 2643264.2248 | 1226380.0594 | 2643248.5594 | 1226384.0814 | 2643234.1862 | 1226390.7145 | 2643217.2028 | 1226401.2449
14 | 2643420.0531 | 1226338.9349 | 2643446.6233 | 1226354.4015
15 | 2643420.0531 | 1226338.9349 | 2643399.5726 | 1226330.7473 | 2643381.022 | 1226326.9738
16 | 2643133.7393 | 1226450.0558 | 2643144.9079 | 1226445.2671 | 2643152.6754 | 1226441.2543 | 2643217.2028 | 1226401.2449
17 | 2643247.5037 | 1226328.0394 | 2643249.7762 | 1226321.9744 | 2643253.0496 | 1226318.963 | 2643259.5718 | 1226317.3872 | 2643282.738 | 1226317.9559 | 2643286.8182 | 1226316.5736 | 2643291.3179 | 1226312.7484 | 2643292.6335 | 1226307.9772
18 | 2643247.5037 | 1226328.0394 | 2643289.6086 | 1226335.6866
19 | 2643293.56 | 1226304.6041 | 2643292.6335 | 1226307.9772
20 | 2643292.6335 | 1226307.9772 | 2643334.9951 | 1226323.5838 | 2643348.3199 | 1226326.6826 | 2643374.7998 | 1226329.1214 | 2643383.6647 | 1226330.5757 | 2643394.5945 | 1226333.2247
21 | 2643321.7889 | 1226341.5312 | 2643289.6086 | 1226335.6866
22 | 2643353.6736 | 1226324.3796 | 2643376.1036 | 1226325.9734 | 2643381.022 | 1226326.9738
23 | 2643133.7393 | 1226450.0558 | 2643139.4327 | 1226456.1341 | 2643142.0685 | 1226458.4658 | 2643144.7723 | 1226459.7862 | 2643147.4744 | 1226460.3061 | 2643150.7345 | 1226460.1629 | 2643155.5994 | 1226459.2532 | 2643187.2257 | 1226453.2454 | 2643197.954 | 1226451.7 | 2643202.7457 | 1226451.468 | 2643207.0193 | 1226451.6324 | 2643215.8418 | 1226452.6304 | 2643315.4314 | 1226464.3499 | 2643330.7612 | 1226465.3215
24 | 2643293.56 | 1226304.6041 | 2643296.4337 | 1226305.681
25 | 2643293.56 | 1226304.6041 | 2643164.9999 | 1226281.2678 | 2643163.3734 | 1226275.6193 | 2643163.4023 | 1226271.6281 | 2643162.2117 | 1226264.3929 | 2643161.82 | 1226261.9774 | 2643171.7009 | 1226260.2702 | 2643181.1158 | 1226259.0599 | 2643201.8594 | 1226257.1759 | 2643249.644 | 1226256.7113
26 | 2643353.6736 | 1226324.3796 | 2643351.1727 | 1226324.2019 | 2643334.6498 | 1226320.0013 | 2643319.2722 | 1226314.239
27 | 2643296.4337 | 1226305.681 | 2643319.2722 | 1226314.239

## bus_geodata
| x | y | coords
0 | 2643363.659 | 1226276.4176
1 | 2643355.8014 | 1226276.4713
2 | 2643405.006 | 1226278.9218
3 | 2643321.892 | 1226276.7031
4 | 2643402.7476 | 1226235.2341
5 | 2643284.8671 | 1226271.3666
6 | 2643335.7735 | 1226232.5054
7 | 2643271.7521 | 1226265.441
8 | 2643318.5922 | 1226367.6588
9 | 2643352.6508 | 1226368.9289
10 | 2643352.7557 | 1226367.0063
11 | 2643370.9813 | 1226371.5529
12 | 2643353.0323 | 1226362.3388
13 | 2643420.0531 | 1226338.9349
14 | 2643217.2028 | 1226401.2449
15 | 2643247.5037 | 1226328.0394
16 | 2643292.6335 | 1226307.9772
17 | 2643289.6086 | 1226335.6866
18 | 2643394.5945 | 1226333.2247
19 | 2643446.6233 | 1226354.4015
20 | 2643381.022 | 1226326.9738
21 | 2643133.7393 | 1226450.0558
22 | 2643293.56 | 1226304.6041
23 | 2643321.7889 | 1226341.5312
24 | 2643353.6736 | 1226324.3796
25 | 2643319.2722 | 1226314.239
26 | 2643296.4337 | 1226305.681
27 | 2643249.644 | 1226256.7113
28 | 2643330.7612 | 1226465.3215
29 | 2643352.6508 | 1226368.9289

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97117 | -0.20311 | 0.0024846 | 0.0006227
1 | 0.97123 | -0.20266 | 0.0027932 | 0.00070004
2 | 0.97099 | -0.20439 | 0 | 0
3 | 0.97163 | -0.19973 | 0.0030988 | 0.00077664
4 | 0.97081 | -0.20573 | 0 | 0
5 | 0.97226 | -0.19523 | 0.0031749 | 0.00079569
6 | 0.97052 | -0.20778 | 0.0028823 | 0.00072238
7 | 0.97256 | -0.19304 | 0.003404 | 0.00085312
8 | 1 | 0 | -0.17764 | -0.044787
9 | 0.9957 | -0.029613 | 0 | 0
10 | 0.99566 | -0.029906 | 0 | 0
11 | 0.99357 | -0.044364 | 0 | 0
12 | 0.99556 | -0.030619 | 0.015138 | 0.0037938
13 | 0.98754 | -0.086477 | 0 | 0
14 | 0.98761 | -0.08579 | 0.0078063 | 0.0019564
15 | 0.97727 | -0.15929 | 0 | 0
16 | 0.97923 | -0.14533 | 0 | 0
17 | 0.97577 | -0.17002 | 0.0032223 | 0.00080757
18 | 0.977 | -0.16127 | 0.01446 | 0.0036239
19 | 0.98747 | -0.086963 | 0.0015451 | 0.00038724
20 | 0.9844 | -0.10867 | 0.018708 | 0.0046886
21 | 0.98454 | -0.10732 | 0 | 0
22 | 0.97943 | -0.14393 | 0 | 0
23 | 0.97478 | -0.17714 | 0.020734 | 0.0051965
24 | 0.98266 | -0.12097 | 0.013353 | 0.0033466
25 | 0.98073 | -0.13465 | 0.014265 | 0.0035753
26 | 0.97968 | -0.14213 | 0.0027892 | 0.00069904
27 | 0.97319 | -0.18856 | 0 | 0
28 | 0.97168 | -0.19879 | 0.043299 | 0.010852
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0053688 | -0.0013439 | 0.0053691 | 0.0013439 | 3.3174e-07 | 3.0357e-08 | 0.0082254 | 0.0082254 | 0.0082254 | 0.97117 | -0.20311 | 0.97123 | -0.20266 | 3.0465
1 | 0.0028842 | 0.0007212 | -0.0028837 | -0.00072152 | 5.0785e-07 | -3.2037e-07 | 0.0044185 | 0.0044187 | 0.0044187 | 0.97117 | -0.20311 | 0.97099 | -0.20439 | 1.6366
2 | -0.0081623 | -0.002044 | 0.0081656 | 0.0020448 | 3.3087e-06 | 8.5277e-07 | 0.012505 | 0.012505 | 0.012505 | 0.97123 | -0.20266 | 0.97163 | -0.19973 | 4.6314
3 | 0.0028837 | 0.00072152 | -0.0028831 | -0.00072186 | 5.3309e-07 | -3.3605e-07 | 0.0044187 | 0.0044189 | 0.0044189 | 0.97099 | -0.20439 | 0.97081 | -0.20573 | 1.6366
4 | -0.011264 | -0.0028215 | 0.011271 | 0.0028237 | 7.0064e-06 | 2.2271e-06 | 0.01725 | 0.01725 | 0.01725 | 0.97163 | -0.19973 | 0.97226 | -0.19523 | 6.389
5 | 0.0028831 | 0.00072186 | -0.0028823 | -0.00072238 | 8.1935e-07 | -5.1601e-07 | 0.0044189 | 0.0044192 | 0.0044192 | 0.97081 | -0.20573 | 0.97052 | -0.20778 | 1.6367
6 | -0.014446 | -0.0036194 | 0.014451 | 0.0036209 | 4.3897e-06 | 1.5098e-06 | 0.022109 | 0.022109 | 0.022109 | 0.97226 | -0.19523 | 0.97256 | -0.19304 | 8.1886
7 | -0.017855 | -0.004474 | 0.017866 | 0.004478 | 1.1079e-05 | 3.9659e-06 | 0.027317 | 0.027317 | 0.027317 | 0.97256 | -0.19304 | 0.97319 | -0.18856 | 10.1175
8 | 0.17684 | 0.044786 | -0.1761 | -0.044504 | 0.00073728 | 0.00028268 | 0.2633 | 0.2633 | 0.2633 | 1 | 0 | 0.9957 | -0.029613 | 48.7592
9 | 0.01514 | 0.0037946 | -0.015139 | -0.0037943 | 6.1523e-07 | 2.1158e-07 | 0.022625 | 0.022625 | 0.022625 | 0.9957 | -0.029613 | 0.99566 | -0.029906 | 8.3798
10 | 0.16096 | 0.040709 | -0.16062 | -0.040581 | 0.00033409 | 0.00012801 | 0.24067 | 0.24067 | 0.24067 | 0.9957 | -0.029613 | 0.99357 | -0.044364 | 44.5693
11 | 0.015139 | 0.0037943 | -0.015138 | -0.0037938 | 1.4937e-06 | 5.1368e-07 | 0.022625 | 0.022625 | 0.022625 | 0.99566 | -0.029906 | 0.99556 | -0.030619 | 8.3798
12 | 0.10853 | 0.027401 | -0.10789 | -0.027157 | 0.00063831 | 0.00024351 | 0.16261 | 0.16261 | 0.16261 | 0.99357 | -0.044364 | 0.98754 | -0.086477 | 30.1128
13 | 0.052096 | 0.01318 | -0.051794 | -0.013068 | 0.00030277 | 0.00011235 | 0.078066 | 0.078067 | 0.078067 | 0.99357 | -0.044364 | 0.98761 | -0.08579 | 14.4569
14 | 0.0015452 | 0.00038688 | -0.0015451 | -0.00038724 | 1.0399e-07 | -3.5333e-07 | 0.0023281 | 0.0023283 | 0.0023283 | 0.98754 | -0.086477 | 0.98747 | -0.086963 | 0.86233
15 | 0.10634 | 0.026771 | -0.10602 | -0.026645 | 0.00032852 | 0.00012531 | 0.16028 | 0.16028 | 0.16028 | 0.98754 | -0.086477 | 0.9844 | -0.10867 | 29.6818
16 | 0.043987 | 0.011111 | -0.043854 | -0.011063 | 0.00013281 | 4.861e-05 | 0.066306 | 0.066307 | 0.066307 | 0.98761 | -0.08579 | 0.98454 | -0.10732 | 12.279
17 | -0.024013 | -0.0060247 | 0.024059 | 0.0060419 | 4.6597e-05 | 1.7221e-05 | 0.036565 | 0.036564 | 0.036565 | 0.97727 | -0.15929 | 0.97923 | -0.14533 | 13.5424
18 | 0.024013 | 0.0060247 | -0.023977 | -0.0060115 | 3.5702e-05 | 1.3196e-05 | 0.036565 | 0.036565 | 0.036565 | 0.97727 | -0.15929 | 0.97577 | -0.17002 | 13.5425
19 | -0.038551 | -0.0096769 | 0.038558 | 0.0096797 | 7.4921e-06 | 2.8375e-06 | 0.058587 | 0.058587 | 0.058587 | 0.97923 | -0.14533 | 0.97943 | -0.14393 | 21.6988
20 | 0.014492 | 0.0036349 | -0.01446 | -0.0036239 | 3.1973e-05 | 1.0971e-05 | 0.022022 | 0.022023 | 0.022023 | 0.97923 | -0.14533 | 0.977 | -0.16127 | 8.1566
21 | 0.020755 | 0.0052039 | -0.020734 | -0.0051965 | 2.0445e-05 | 7.4555e-06 | 0.031651 | 0.031651 | 0.031651 | 0.97577 | -0.17002 | 0.97478 | -0.17714 | 11.7226
22 | 0.087309 | 0.021957 | -0.087159 | -0.0219 | 0.00014954 | 5.6816e-05 | 0.132 | 0.132 | 0.132 | 0.9844 | -0.10867 | 0.98266 | -0.12097 | 24.445
23 | 0.043854 | 0.011063 | -0.043299 | -0.010852 | 0.0005554 | 0.00021107 | 0.066307 | 0.066308 | 0.066308 | 0.98454 | -0.10732 | 0.97168 | -0.19879 | 24.5584
24 | -0.056535 | -0.014197 | 0.056549 | 0.014203 | 1.4131e-05 | 5.3963e-06 | 0.085903 | 0.085903 | 0.085903 | 0.97943 | -0.14393 | 0.97968 | -0.14213 | 31.8158
25 | 0.017977 | 0.0045177 | -0.017866 | -0.004478 | 0.00011103 | 3.9721e-05 | 0.027316 | 0.027317 | 0.027317 | 0.97943 | -0.14393 | 0.97319 | -0.18856 | 10.1175
26 | 0.073806 | 0.018553 | -0.073666 | -0.0185 | 0.00014026 | 5.3037e-05 | 0.11178 | 0.11178 | 0.11178 | 0.98266 | -0.12097 | 0.98073 | -0.13465 | 20.7006
27 | 0.0594 | 0.014925 | -0.059339 | -0.014902 | 6.1827e-05 | 2.3165e-05 | 0.090139 | 0.090139 | 0.090139 | 0.98073 | -0.13465 | 0.97968 | -0.14213 | 16.6924

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.19872 | 0.050072

## res_load
| p_mw | q_mvar
0 | 0.0024846 | 0.0006227
1 | 0.0027932 | 0.00070004
2 | 0.0030988 | 0.00077664
3 | 0.0031749 | 0.00079569
4 | 0.0028823 | 0.00072238
5 | 0.003404 | 0.00085312
6 | 0.021087 | 0.005285
7 | 0.015138 | 0.0037938
8 | 0.0078063 | 0.0019564
9 | 0.0032223 | 0.00080757
10 | 0.01446 | 0.0036239
11 | 0.0015451 | 0.00038724
12 | 0.018708 | 0.0046886
13 | 0.020734 | 0.0051965
14 | 0.013353 | 0.0033466
15 | 0.014265 | 0.0035753
16 | 0.0027892 | 0.00069904
17 | 0.043299 | 0.010852

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1