## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1128-10_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1128-10_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1128-10_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1128-10_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1128-10_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1128-10_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1128-10_0_3_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1128-10_0_3_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_1128-10_0_3_node_21 | 0.4 | n |  | TRUE
9 | bus_LV_1128-10_0_3_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1128-10_0_3_node_25 | 0.4 | n |  | TRUE
11 | bus_LV_1128-10_0_3_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1128-10_0_3_node_6 | 0.4 | n |  | TRUE
13 | bus_LV_1128-10_0_3_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1128-10_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1128-10_0_3_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1128-10_0_3_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1128-10_0_3_node_23 | 0.4 | n |  | TRUE
18 | bus_LV_1128-10_0_3_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1128-10_0_3_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1128-10_0_3_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_1128-10_0_3_node_47 | 0.4 | n |  | TRUE
22 | bus_LV_1128-10_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1128-10_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1128-10_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1128-10_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1128-10_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1128-10_0_3_node_44 | 0.4 | n |  | TRUE
28 | bus_LV_1128-10_0_3_node_35 | 0.4 | n |  | TRUE
29 | bus_LV_1128-10_0_3_node_43 | 0.4 | n |  | TRUE
30 | bus_LV_1128-10_0_3_node_36 | 0.4 | n |  | TRUE
31 | bus_LV_1128-10_0_3_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1128-10_0_3_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1128-10_0_3_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_1128-10_0_3_node_49 | 0.4 | n |  | TRUE
35 | bus_LV_1128-10_0_3_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_1128-10_0_3_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1128-10_0_3_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1128-10_0_3_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1128-10_0_3_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_1128-10_0_3_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_1128-10_0_3_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_1128-10_0_3_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_1128-10_0_3_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_1128-10_0_3_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_1128-10_0_3_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_1128-10_0_3_node_48 | 0.4 | n |  | TRUE
47 | bus_LV_1128-10_0_3_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_1128-10_0_3_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_1128-10_0_3_node_51 | 0.4 | n |  | TRUE
50 | bus_LV_1128-10_0_3_node_45 | 0.4 | n |  | TRUE
51 | bus_MV_128_0_node_44 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1128-10_0_3_load_0 | 0 | 0.0042266 | 0.0010593 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1128-10_0_3_load_1 | 1 | 0.006205 | 0.0015551 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1128-10_0_3_load_3 | 3 | 0.00068267 | 0.00017109 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1128-10_0_3_load_4 | 4 | 0.0034513 | 0.00086499 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1128-10_0_3_load_5 | 5 | 0.0027413 | 0.00068704 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1128-10_0_3_load_11 | 6 | 0.0014224 | 0.00035648 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1128-10_0_3_load_24 | 7 | 0.0080997 | 0.00203 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1128-10_0_3_load_21 | 8 | 0.00059616 | 0.00014941 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1128-10_0_3_load_12 | 9 | 0.00092475 | 0.00023176 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1128-10_0_3_load_25 | 10 | 0.00059532 | 0.0001492 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1128-10_0_3_load_6 | 12 | 0.0010585 | 0.0002653 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1128-10_0_3_load_7 | 13 | 0.0011582 | 0.00029027 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1128-10_0_3_load_9 | 15 | 0.0014719 | 0.0003689 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1128-10_0_3_load_10 | 16 | 0.00083335 | 0.00020886 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1128-10_0_3_load_23 | 17 | 0.0014453 | 0.00036224 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1128-10_0_3_load_18 | 18 | 0.00058852 | 0.0001475 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1128-10_0_3_load_29 | 19 | 0.00050508 | 0.00012659 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1128-10_0_3_load_13 | 22 | 0.0012731 | 0.00031906 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1128-10_0_3_load_14 | 23 | 0.00027078 | 6.7863e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1128-10_0_3_load_17 | 26 | 0.00065998 | 0.00016541 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1128-10_0_3_load_44 | 27 | 0.0018515 | 0.00046403 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1128-10_0_3_load_35 | 28 | 0.040565 | 0.010167 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1128-10_0_3_load_43 | 29 | 0.0007514 | 0.00018832 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1128-10_0_3_load_36 | 30 | 0.014108 | 0.0035358 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1128-10_0_3_load_20 | 31 | 0.00083565 | 0.00020943 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1128-10_0_3_load_22 | 32 | 0.00075994 | 0.00019046 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1128-10_0_3_load_27 | 33 | 0.00088712 | 0.00022233 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1128-10_0_3_load_49 | 34 | 0.00059616 | 0.00014941 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1128-10_0_3_load_50 | 35 | 0.00057816 | 0.0001449 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1128-10_0_3_load_26 | 36 | 0.00083526 | 0.00020934 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1128-10_0_3_load_28 | 37 | 0.0011969 | 0.00029996 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1128-10_0_3_load_30 | 38 | 0.014521 | 0.0036392 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1128-10_0_3_load_31 | 39 | 0.004822 | 0.0012085 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1128-10_0_3_load_32 | 40 | 0.012249 | 0.00307 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1128-10_0_3_load_33 | 41 | 0.00057837 | 0.00014495 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1128-10_0_3_load_34 | 42 | 0.00082586 | 0.00020698 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1128-10_0_3_load_42 | 43 | 0.00057811 | 0.00014489 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1128-10_0_3_load_37 | 44 | 0.0070205 | 0.0017595 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1128-10_0_3_load_38 | 45 | 0.0070231 | 0.0017601 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1128-10_0_3_load_48 | 46 | 0.015237 | 0.0038187 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1128-10_0_3_load_40 | 47 | 0.00095681 | 0.0002398 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1128-10_0_3_load_51 | 49 | 0.0012981 | 0.00032534 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1128-10_0_3_load_45 | 50 | 0.0005204 | 0.00013042 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 39 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1128-10_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0011834 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1128-10_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.028284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1128-10_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0057818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1128-10_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.013792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1128-10_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.0065892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1128-10_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.027322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1128-10_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.014985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1128-10_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.03873 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1128-10_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.009008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1128-10_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.023723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1128-10_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.041238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1128-10_0_3_line_11 | NAYY 4x150 SE | 9 | 20 | 0.085626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1128-10_0_3_line_12 | NAYY 4x150 SE | 10 | 34 | 0.0064507 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1128-10_0_3_line_13 | NAYY 4x150 SE | 11 | 31 | 0.024449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1128-10_0_3_line_14 | NAYY 4x150 SE | 11 | 32 | 0.02277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1128-10_0_3_line_15 | NAYY 4x150 SE | 11 | 18 | 0.017379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1128-10_0_3_line_16 | NAYY 4x150 SE | 12 | 13 | 0.02171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1128-10_0_3_line_17 | NAYY 4x150 SE | 12 | 14 | 0.016372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1128-10_0_3_line_18 | NAYY 4x150 SE | 13 | 15 | 0.0020803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1128-10_0_3_line_19 | NAYY 4x150 SE | 14 | 16 | 0.01788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1128-10_0_3_line_20 | NAYY 4x150 SE | 15 | 17 | 0.019132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1128-10_0_3_line_21 | NAYY 4x150 SE | 16 | 18 | 0.00046612 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1128-10_0_3_line_22 | NAYY 4x150 SE | 17 | 19 | 0.00034414 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1128-10_0_3_line_23 | NAYY 4x150 SE | 19 | 33 | 0.011285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1128-10_0_3_line_24 | NAYY 4x150 SE | 20 | 21 | 0.045788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1128-10_0_3_line_25 | NAYY 4x150 SE | 21 | 49 | 0.048137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1128-10_0_3_line_26 | NAYY 4x150 SE | 22 | 23 | 0.023627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1128-10_0_3_line_27 | NAYY 4x150 SE | 22 | 24 | 0.032987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1128-10_0_3_line_28 | NAYY 4x150 SE | 23 | 25 | 0.080831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
29 | LV_1128-10_0_3_line_29 | NAYY 4x150 SE | 24 | 26 | 0.057053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
30 | LV_1128-10_0_3_line_30 | NAYY 4x150 SE | 25 | 27 | 0.035871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
31 | LV_1128-10_0_3_line_31 | NAYY 4x150 SE | 26 | 28 | 0.033014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1128-10_0_3_line_32 | NAYY 4x150 SE | 27 | 29 | 0.045419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
33 | LV_1128-10_0_3_line_33 | NAYY 4x150 SE | 28 | 30 | 0.0014107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1128-10_0_3_line_34 | NAYY 4x150 SE | 29 | 50 | 0.017657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
35 | LV_1128-10_0_3_line_35 | NAYY 4x150 SE | 30 | 46 | 0.018207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1128-10_0_3_line_36 | NAYY 4x150 SE | 33 | 36 | 0.009193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1128-10_0_3_line_37 | NAYY 4x150 SE | 34 | 35 | 0.012966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1128-10_0_3_line_38 | NAYY 4x150 SE | 35 | 43 | 0.0069984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1128-10_0_3_line_39 | NAYY 4x150 SE | 36 | 37 | 0.020346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1128-10_0_3_line_40 | NAYY 4x150 SE | 38 | 39 | 0.02522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_1128-10_0_3_line_41 | NAYY 4x150 SE | 38 | 40 | 0.0018334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1128-10_0_3_line_42 | NAYY 4x150 SE | 39 | 41 | 0.00024575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1128-10_0_3_line_43 | NAYY 4x150 SE | 40 | 42 | 0.0094972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
44 | LV_1128-10_0_3_line_44 | NAYY 4x150 SE | 41 | 43 | 0.0062931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1128-10_0_3_line_45 | NAYY 4x150 SE | 42 | 44 | 0.012369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
46 | LV_1128-10_0_3_line_46 | NAYY 4x150 SE | 44 | 45 | 0.021811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_1128-10_0_3_line_47 | NAYY 4x150 SE | 45 | 47 | 0.0038653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_1128-10_0_3_line_48 | NAYY 4x150 SE | 47 | 48 | 0.02495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1128-10_0_3_line_49 | NAYY 4x150 SE | 48 | 50 | 0.036497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1128-10_0_3_trafo_31 | 0.25 MVA 20/0.4 kV | 51 | 39 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2643711.3623 | 1222620.9789 | 2643710.9725 | 1222622.0962
1 | 2643722.1404 | 1222594.9094 | 2643717.1719 | 1222604.3231 | 2643711.3623 | 1222620.9789
2 | 2643709.0683 | 1222627.5554 | 2643710.9725 | 1222622.0962
3 | 2643722.1404 | 1222594.9094 | 2643726.9312 | 1222581.9758
4 | 2643722.1404 | 1222594.9094 | 2643722.9847 | 1222588.3745
5 | 2643705.2067 | 1222654.6031 | 2643707.2296 | 1222640.4164 | 2643709.0683 | 1222627.5554 | 2643709.0683 | 1222627.5554
6 | 2643733.1035 | 1222568.3609 | 2643729.4756 | 1222575.1068 | 2643726.9312 | 1222581.9758
7 | 2643720.1652 | 1222550.7861 | 2643724.4847 | 1222560.7059 | 2643725.5659 | 1222568.3962 | 2643722.9847 | 1222588.3745
8 | 2643705.2067 | 1222654.6031 | 2643703.9351 | 1222663.5208
9 | 2643733.1035 | 1222568.3609 | 2643736.0268 | 1222562.9252 | 2643746.7189 | 1222549.0067
10 | 2643707.151 | 1222512.6385 | 2643708.2574 | 1222527.2333 | 2643711.1591 | 1222535.9265 | 2643718.2196 | 1222546.3179 | 2643720.1652 | 1222550.7861
11 | 2643701.5671 | 1222748.5514 | 2643699.5763 | 1222734.595 | 2643697.9493 | 1222716.55 | 2643699.0608 | 1222697.3687 | 2643699.9556 | 1222691.1827 | 2643701.9925 | 1222677.1447 | 2643703.9351 | 1222663.5208
12 | 2643750.6487 | 1222543.8911 | 2643746.7189 | 1222549.0067
13 | 2643707.151 | 1222512.6385 | 2643705.4214 | 1222488.2507
14 | 2643729.1226 | 1222518.8479 | 2643707.151 | 1222512.6385
15 | 2643707.151 | 1222512.6385 | 2643690.223 | 1222508.7068
16 | 2643667.6943 | 1222520.2513 | 2643661.5165 | 1222541.0643
17 | 2643672.3529 | 1222504.5563 | 2643667.6943 | 1222520.2513
18 | 2643660.9245 | 1222543.0586 | 2643661.5165 | 1222541.0643
19 | 2643672.3529 | 1222504.5563 | 2643689.769 | 1222508.6014
20 | 2643660.9245 | 1222543.0586 | 2643660.0507 | 1222546.0024 | 2643657.0444 | 1222554.6856 | 2643652.3921 | 1222559.7442
21 | 2643689.769 | 1222508.6014 | 2643690.223 | 1222508.7068
22 | 2643652.1591 | 1222559.9975 | 2643652.1591 | 1222559.9975 | 2643652.3921 | 1222559.7442
23 | 2643652.1591 | 1222559.9975 | 2643642.8895 | 1222566.4335
24 | 2643701.5671 | 1222748.5514 | 2643708.4375 | 1222764.1557 | 2643713.5056 | 1222772.1422 | 2643720.1632 | 1222782.6196 | 2643722.5759 | 1222785.5835 | 2643724.119 | 1222788.2075
25 | 2643724.119 | 1222788.2075 | 2643751.9965 | 1222827.4503
26 | 2643885.6391 | 1222429.8455 | 2643884.784 | 1222431.1502 | 2643880.0622 | 1222441.0103 | 2643878.8127 | 1222452.0745
27 | 2643898.6949 | 1222477.3139 | 2643889.2541 | 1222468.8393 | 2643881.5839 | 1222460.9447 | 2643878.8127 | 1222452.0745
28 | 2643900.8096 | 1222365.3396 | 2643913.5085 | 1222378.3743 | 2643916.1075 | 1222386.932 | 2643914.4213 | 1222395.5025 | 2643893.5363 | 1222417.7955 | 2643885.6391 | 1222429.8455
29 | 2643898.6949 | 1222477.3139 | 2643872.0837 | 1222508.926 | 2643871.8844 | 1222524.6563 | 2643871.8844 | 1222524.6563
30 | 2643900.8096 | 1222365.3396 | 2643885.244 | 1222383.1357 | 2643875.5871 | 1222390.6365
31 | 2643871.8844 | 1222524.6563 | 2643896.5221 | 1222546.6307
32 | 2643840.7925 | 1222419.7999 | 2643862.047 | 1222401.1536 | 2643875.5871 | 1222390.6365
33 | 2643896.5221 | 1222546.6307 | 2643897.5749 | 1222547.5698
34 | 2643840.7925 | 1222419.7999 | 2643837.3519 | 1222422.8183 | 2643828.8262 | 1222426.0131 | 2643824.8939 | 1222426.5937
35 | 2643911.1629 | 1222559.689 | 2643897.5749 | 1222547.5698
36 | 2643642.8895 | 1222566.4335 | 2643637.7673 | 1222574.0672
37 | 2643758.5473 | 1222533.6091 | 2643750.6487 | 1222543.8911
38 | 2643758.5473 | 1222533.6091 | 2643760.6302 | 1222530.8976 | 2643762.6508 | 1222527.9434
39 | 2643633.3877 | 1222593.8894 | 2643635.5859 | 1222580.9332 | 2643637.7673 | 1222574.0672 | 2643637.7673 | 1222574.0672
40 | 2643766.3423 | 1222522.5462 | 2643777.9416 | 1222505.5872 | 2643780.1486 | 1222501.4679
41 | 2643781.0144 | 1222499.8518 | 2643780.1486 | 1222501.4679
42 | 2643766.3423 | 1222522.5462 | 2643766.2035 | 1222522.749
43 | 2643785.4995 | 1222491.4804 | 2643781.0144 | 1222499.8518
44 | 2643766.2035 | 1222522.749 | 2643762.6508 | 1222527.9434
45 | 2643785.4995 | 1222491.4804 | 2643785.5776 | 1222491.3347 | 2643791.3198 | 1222480.5669
46 | 2643791.6178 | 1222459.8809 | 2643793.279 | 1222463.0297 | 2643794.5995 | 1222470.1326 | 2643792.9834 | 1222477.4474 | 2643791.3198 | 1222480.5669
47 | 2643791.6178 | 1222459.8809 | 2643789.8143 | 1222456.4622
48 | 2643789.5266 | 1222433.8845 | 2643785.4719 | 1222439.6805 | 2643785.3949 | 1222448.085 | 2643789.8143 | 1222456.4622
49 | 2643789.5266 | 1222433.8845 | 2643795.1546 | 1222433.837 | 2643800.0818 | 1222431.1049 | 2643811.4694 | 1222428.5759 | 2643824.8939 | 1222426.5937

## bus_geodata
| x | y | coords
0 | 2643711.3623 | 1222620.9789
1 | 2643710.9725 | 1222622.0962
2 | 2643722.1404 | 1222594.9094
3 | 2643709.0683 | 1222627.5554
4 | 2643726.9312 | 1222581.9758
5 | 2643722.9847 | 1222588.3745
6 | 2643705.2067 | 1222654.6031
7 | 2643733.1035 | 1222568.3609
8 | 2643720.1652 | 1222550.7861
9 | 2643703.9351 | 1222663.5208
10 | 2643746.7189 | 1222549.0067
11 | 2643707.151 | 1222512.6385
12 | 2643667.6942 | 1222520.2513
13 | 2643661.5165 | 1222541.0643
14 | 2643672.3529 | 1222504.5563
15 | 2643660.9245 | 1222543.0586
16 | 2643689.769 | 1222508.6014
17 | 2643652.3921 | 1222559.7442
18 | 2643690.223 | 1222508.7068
19 | 2643652.1591 | 1222559.9975
20 | 2643701.5671 | 1222748.5514
21 | 2643724.119 | 1222788.2075
22 | 2643878.8127 | 1222452.0745
23 | 2643885.6391 | 1222429.8455
24 | 2643898.6949 | 1222477.3139
25 | 2643900.8096 | 1222365.3396
26 | 2643871.8844 | 1222524.6563
27 | 2643875.5871 | 1222390.6365
28 | 2643896.5221 | 1222546.6307
29 | 2643840.7925 | 1222419.7999
30 | 2643897.5749 | 1222547.5698
31 | 2643705.4214 | 1222488.2507
32 | 2643729.1226 | 1222518.8479
33 | 2643642.8895 | 1222566.4335
34 | 2643750.6487 | 1222543.8911
35 | 2643758.5473 | 1222533.6091
36 | 2643637.7673 | 1222574.0672
37 | 2643633.3877 | 1222593.8894
38 | 2643780.1486 | 1222501.4679
39 | 2643766.3423 | 1222522.5462
40 | 2643781.0144 | 1222499.8518
41 | 2643766.2035 | 1222522.749
42 | 2643785.4995 | 1222491.4804
43 | 2643762.6508 | 1222527.9434
44 | 2643791.3198 | 1222480.5669
45 | 2643791.6178 | 1222459.8809
46 | 2643911.1629 | 1222559.689
47 | 2643789.8143 | 1222456.4622
48 | 2643789.5266 | 1222433.8845
49 | 2643751.9965 | 1222827.4503
50 | 2643824.8939 | 1222426.5937
51 | 2643722.1404 | 1222594.9094

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99469 | -0.037245 | 0.0042266 | 0.0010593
1 | 0.99467 | -0.037371 | 0.006205 | 0.0015551
2 | 0.99529 | -0.03303 | 0 | 0
3 | 0.99463 | -0.037624 | 0.00068267 | 0.00017109
4 | 0.99587 | -0.028902 | 0.0034513 | 0.00086499
5 | 0.99515 | -0.034021 | 0.0027413 | 0.00068704
6 | 0.99449 | -0.038635 | 0.0014224 | 0.00035648
7 | 0.99658 | -0.023902 | 0.0080997 | 0.00203
8 | 0.99447 | -0.038785 | 0.00059616 | 0.00014941
9 | 0.99446 | -0.038838 | 0.00092475 | 0.00023176
10 | 0.99799 | -0.014076 | 0.00059532 | 0.0001492
11 | 0.99378 | -0.043614 | 0 | 0
12 | 0.99311 | -0.048382 | 0.0010585 | 0.0002653
13 | 0.99287 | -0.050031 | 0.0011582 | 0.00029027
14 | 0.99331 | -0.046963 | 0 | 0
15 | 0.99285 | -0.050165 | 0.0014719 | 0.0003689
16 | 0.99353 | -0.045413 | 0.00083335 | 0.00020886
17 | 0.99272 | -0.051109 | 0.0014453 | 0.00036224
18 | 0.99353 | -0.045369 | 0.00058852 | 0.0001475
19 | 0.99272 | -0.051121 | 0.00050508 | 0.00012659
20 | 0.9943 | -0.039972 | 0 | 0
21 | 0.99422 | -0.040575 | 0 | 0
22 | 0.98049 | -0.13581 | 0.0012731 | 0.00031906
23 | 0.98173 | -0.12701 | 0.00027078 | 6.7863e-05
24 | 0.97878 | -0.14792 | 0 | 0
25 | 0.98601 | -0.096942 | 0 | 0
26 | 0.97583 | -0.16895 | 0.00065998 | 0.00016541
27 | 0.9879 | -0.083682 | 0.0018515 | 0.00046403
28 | 0.97245 | -0.19323 | 0.040565 | 0.010167
29 | 0.99036 | -0.066535 | 0.0007514 | 0.00018832
30 | 0.97239 | -0.19367 | 0.014108 | 0.0035358
31 | 0.99375 | -0.04382 | 0.00083565 | 0.00020943
32 | 0.99376 | -0.043789 | 0.00075994 | 0.00019046
33 | 0.99267 | -0.051455 | 0.00088712 | 0.00022233
34 | 0.99837 | -0.01137 | 0.00059616 | 0.00014941
35 | 0.99916 | -0.0058606 | 0.00057816 | 0.0001449
36 | 0.99265 | -0.051645 | 0.00083526 | 0.00020934
37 | 0.99261 | -0.051892 | 0.0011969 | 0.00029996
38 | 0.99784 | -0.014872 | 0.014521 | 0.0036392
39 | 1 | 0 | -0.16513 | -0.04148
40 | 0.9977 | -0.015822 | 0.012249 | 0.00307
41 | 0.99998 | -0.00010843 | 0.00057837 | 0.00014495
42 | 0.99707 | -0.020164 | 0.00082586 | 0.00020698
43 | 0.99959 | -0.0028499 | 0.00057811 | 0.00014489
44 | 0.99626 | -0.025776 | 0.0070205 | 0.0017595
45 | 0.99493 | -0.034922 | 0.0070231 | 0.0017601
46 | 0.97198 | -0.1966 | 0.015237 | 0.0038187
47 | 0.99472 | -0.036408 | 0.00095681 | 0.0002398
48 | 0.99334 | -0.045897 | 0 | 0
49 | 0.99413 | -0.041207 | 0.0012981 | 0.00032534
50 | 0.99133 | -0.059824 | 0.0005204 | 0.00013042
51 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.010534 | 0.0026374 | -0.010534 | -0.0026374 | 1.8336e-07 | 5.5163e-08 | 0.015758 | 0.015758 | 0.015758 | 0.99469 | -0.037245 | 0.99467 | -0.037371 | 5.8363
1 | -0.014761 | -0.0036967 | 0.014769 | 0.0036997 | 8.6051e-06 | 2.9423e-06 | 0.022081 | 0.022081 | 0.022081 | 0.99469 | -0.037245 | 0.99529 | -0.03303 | 8.1781
2 | 0.0043291 | 0.0010822 | -0.0043289 | -0.0010823 | 1.5127e-07 | -1.6861e-08 | 0.0064753 | 0.0064753 | 0.0064753 | 0.99467 | -0.037371 | 0.99463 | -0.037624 | 2.3983
3 | -0.029709 | -0.007444 | 0.029726 | 0.0074503 | 1.6979e-05 | 6.351e-06 | 0.044417 | 0.044417 | 0.044417 | 0.99529 | -0.03303 | 0.99587 | -0.028902 | 16.4506
4 | 0.01494 | 0.0037443 | -0.014938 | -0.0037436 | 2.0513e-06 | 7.0334e-07 | 0.022336 | 0.022336 | 0.022336 | 0.99529 | -0.03303 | 0.99515 | -0.034021 | 8.2726
5 | 0.0036462 | 0.00091117 | -0.0036457 | -0.00091133 | 5.0715e-07 | -1.595e-07 | 0.005454 | 0.0054541 | 0.0054541 | 0.99463 | -0.037624 | 0.99449 | -0.038635 | 2.02
6 | -0.033178 | -0.0083153 | 0.033201 | 0.008324 | 2.2979e-05 | 8.6429e-06 | 0.049573 | 0.049573 | 0.049573 | 0.99587 | -0.028902 | 0.99658 | -0.023902 | 18.3605
7 | 0.012196 | 0.0030566 | -0.012188 | -0.003054 | 8.0379e-06 | 2.5886e-06 | 0.018237 | 0.018237 | 0.018237 | 0.99515 | -0.034021 | 0.99447 | -0.038785 | 6.7545
8 | 0.0022233 | 0.00055484 | -0.0022233 | -0.00055494 | 6.2176e-08 | -9.2963e-08 | 0.0033259 | 0.0033259 | 0.0033259 | 0.99449 | -0.038635 | 0.99446 | -0.038838 | 1.2318
9 | -0.0413 | -0.010354 | 0.041357 | 0.010375 | 5.6294e-05 | 2.1342e-05 | 0.061667 | 0.061667 | 0.061667 | 0.99658 | -0.023902 | 0.99799 | -0.014076 | 22.8397
10 | 0.011592 | 0.0029046 | -0.011585 | -0.0029022 | 7.7418e-06 | 2.4429e-06 | 0.017345 | 0.017345 | 0.017345 | 0.99447 | -0.038785 | 0.99378 | -0.043614 | 6.4242
11 | 0.0012985 | 0.00032317 | -0.0012983 | -0.00032421 | 2.0159e-07 | -1.0332e-06 | 0.0019422 | 0.0019426 | 0.0019426 | 0.99446 | -0.038838 | 0.9943 | -0.039972 | 0.71948
12 | -0.041952 | -0.010524 | 0.041968 | 0.01053 | 1.5751e-05 | 5.9738e-06 | 0.062555 | 0.062555 | 0.062555 | 0.99799 | -0.014076 | 0.99837 | -0.01137 | 23.1684
13 | 0.00083568 | 0.00020913 | -0.00083565 | -0.00020943 | 2.3885e-08 | -3.0758e-07 | 0.0012512 | 0.0012513 | 0.0012513 | 0.99378 | -0.043614 | 0.99375 | -0.04382 | 0.46344
14 | 0.00075996 | 0.00019017 | -0.00075994 | -0.00019046 | 1.8396e-08 | -2.8794e-07 | 0.0011378 | 0.0011379 | 0.0011379 | 0.99378 | -0.043614 | 0.99376 | -0.043789 | 0.42145
15 | 0.0099889 | 0.0025029 | -0.0099865 | -0.0025021 | 2.4258e-06 | 7.0789e-07 | 0.014956 | 0.014956 | 0.014956 | 0.99378 | -0.043614 | 0.99353 | -0.045369 | 5.5394
16 | 0.0075025 | 0.0018796 | -0.0075008 | -0.0018792 | 1.7119e-06 | 3.7756e-07 | 0.011241 | 0.011241 | 0.011241 | 0.99311 | -0.048382 | 0.99287 | -0.050031 | 4.1634
17 | -0.008561 | -0.0021449 | 0.0085627 | 0.0021453 | 1.6809e-06 | 4.3461e-07 | 0.012827 | 0.012827 | 0.012827 | 0.99311 | -0.048382 | 0.99331 | -0.046963 | 4.7508
18 | 0.0063426 | 0.0015889 | -0.0063425 | -0.0015889 | 1.1729e-07 | 1.8206e-08 | 0.0095054 | 0.0095054 | 0.0095054 | 0.99287 | -0.050031 | 0.99285 | -0.050165 | 3.5205
19 | -0.0085627 | -0.0021453 | 0.0085645 | 0.0021458 | 1.8357e-06 | 4.7453e-07 | 0.012827 | 0.012827 | 0.012827 | 0.99331 | -0.046963 | 0.99353 | -0.045413 | 4.7507
20 | 0.0048706 | 0.00122 | -0.0048699 | -0.00122 | 6.3611e-07 | -2.7389e-09 | 0.0072994 | 0.0072995 | 0.0072995 | 0.99285 | -0.050165 | 0.99272 | -0.051109 | 2.7035
21 | -0.0093979 | -0.0023546 | 0.0093979 | 0.0023546 | 5.7621e-08 | 1.6126e-08 | 0.014075 | 0.014075 | 0.014075 | 0.99353 | -0.045413 | 0.99353 | -0.045369 | 5.213
22 | 0.0034246 | 0.00085778 | -0.0034246 | -0.00085778 | 5.6581e-09 | -2.2732e-09 | 0.005133 | 0.005133 | 0.005133 | 0.99272 | -0.051109 | 0.99272 | -0.051121 | 1.9011
23 | 0.0029195 | 0.00073119 | -0.0029193 | -0.00073129 | 1.3484e-07 | -9.4032e-08 | 0.0043759 | 0.004376 | 0.004376 | 0.99272 | -0.051121 | 0.99267 | -0.051455 | 1.6207
24 | 0.0012983 | 0.00032421 | -0.0012982 | -0.00032476 | 1.0783e-07 | -5.5236e-07 | 0.0019426 | 0.0019428 | 0.0019428 | 0.9943 | -0.039972 | 0.99422 | -0.040575 | 0.71956
25 | 0.0012982 | 0.00032476 | -0.0012981 | -0.00032534 | 1.1339e-07 | -5.8057e-07 | 0.0019428 | 0.001943 | 0.001943 | 0.99422 | -0.040575 | 0.99413 | -0.041207 | 0.71964
26 | -0.072414 | -0.018222 | 0.072503 | 0.018256 | 8.9073e-05 | 3.3662e-05 | 0.10992 | 0.10992 | 0.10992 | 0.98049 | -0.13581 | 0.98173 | -0.12701 | 20.3563
27 | 0.071141 | 0.017903 | -0.071021 | -0.017858 | 0.00012003 | 4.5333e-05 | 0.10799 | 0.10799 | 0.10799 | 0.98049 | -0.13581 | 0.97878 | -0.14792 | 19.9986
28 | -0.072774 | -0.018324 | 0.073081 | 0.01844 | 0.00030701 | 0.00011603 | 0.11033 | 0.11033 | 0.11033 | 0.98173 | -0.12701 | 0.98601 | -0.096942 | 20.4323
29 | 0.071021 | 0.017858 | -0.070814 | -0.01778 | 0.0002076 | 7.8415e-05 | 0.10799 | 0.10799 | 0.10799 | 0.97878 | -0.14792 | 0.97583 | -0.16895 | 19.9987
30 | -0.073081 | -0.01844 | 0.073217 | 0.018491 | 0.00013624 | 5.1484e-05 | 0.11033 | 0.11033 | 0.11033 | 0.98601 | -0.096942 | 0.9879 | -0.083682 | 20.4321
31 | 0.070154 | 0.017614 | -0.069918 | -0.017524 | 0.0002358 | 9.028e-05 | 0.10699 | 0.10699 | 0.10699 | 0.97583 | -0.16895 | 0.97245 | -0.19323 | 39.6247
32 | -0.075069 | -0.018955 | 0.07525 | 0.019024 | 0.00018134 | 6.8579e-05 | 0.11312 | 0.11312 | 0.11312 | 0.9879 | -0.083682 | 0.99036 | -0.066535 | 20.9485
33 | 0.029353 | 0.0073574 | -0.029351 | -0.0073567 | 1.7759e-06 | 6.6553e-07 | 0.044915 | 0.044915 | 0.044915 | 0.97245 | -0.19323 | 0.97239 | -0.19367 | 16.6353
34 | -0.076002 | -0.019212 | 0.076074 | 0.01924 | 7.1908e-05 | 2.7202e-05 | 0.11425 | 0.11425 | 0.11425 | 0.99036 | -0.066535 | 0.99133 | -0.059824 | 21.1575
35 | 0.015243 | 0.0038208 | -0.015237 | -0.0038187 | 6.1818e-06 | 2.1518e-06 | 0.023326 | 0.023326 | 0.023326 | 0.97239 | -0.19367 | 0.97198 | -0.1966 | 8.6393
36 | 0.0020322 | 0.00050896 | -0.0020322 | -0.00050905 | 5.323e-08 | -9.8368e-08 | 0.0030462 | 0.0030462 | 0.0030462 | 0.99267 | -0.051455 | 0.99265 | -0.051645 | 1.1282
37 | -0.042564 | -0.01068 | 0.042596 | 0.010692 | 3.2565e-05 | 1.2355e-05 | 0.063443 | 0.063443 | 0.063443 | 0.99837 | -0.01137 | 0.99916 | -0.0058606 | 23.4975
38 | -0.043174 | -0.010837 | 0.043193 | 0.010844 | 1.8058e-05 | 6.8535e-06 | 0.064304 | 0.064304 | 0.064304 | 0.99916 | -0.0058606 | 0.99959 | -0.0028499 | 23.8163
39 | 0.0011969 | 0.00029972 | -0.0011969 | -0.00029996 | 4.0868e-08 | -2.4728e-07 | 0.0017941 | 0.0017942 | 0.0017942 | 0.99265 | -0.051645 | 0.99261 | -0.051892 | 0.66453
40 | -0.11971 | -0.030244 | 0.11996 | 0.03034 | 0.00025101 | 9.5881e-05 | 0.17861 | 0.17861 | 0.17861 | 0.99784 | -0.014872 | 1 | 0 | 33.0752
41 | 0.10519 | 0.026605 | -0.10518 | -0.0266 | 1.4091e-05 | 5.3719e-06 | 0.15695 | 0.15695 | 0.15695 | 0.99784 | -0.014872 | 0.9977 | -0.015822 | 29.0653
42 | 0.044366 | 0.01114 | -0.044366 | -0.01114 | 6.6849e-07 | 2.5389e-07 | 0.066025 | 0.066025 | 0.066025 | 1 | 0 | 0.99998 | -0.00010843 | 24.4538
43 | 0.09293 | 0.02353 | -0.092873 | -0.023508 | 5.699e-05 | 2.1671e-05 | 0.13868 | 0.13868 | 0.13868 | 0.9977 | -0.015822 | 0.99707 | -0.020164 | 25.6822
44 | 0.043787 | 0.010995 | -0.043771 | -0.010989 | 1.6675e-05 | 6.331e-06 | 0.065165 | 0.065165 | 0.065165 | 0.99998 | -0.00010843 | 0.99959 | -0.0028499 | 24.1351
45 | 0.092047 | 0.023301 | -0.091974 | -0.023273 | 7.2907e-05 | 2.7719e-05 | 0.13745 | 0.13745 | 0.13745 | 0.99707 | -0.020164 | 0.99626 | -0.025776 | 25.454
46 | 0.084954 | 0.021514 | -0.084844 | -0.021472 | 0.0001097 | 4.1625e-05 | 0.12697 | 0.12697 | 0.12697 | 0.99626 | -0.025776 | 0.99493 | -0.034922 | 23.5122
47 | 0.077821 | 0.019712 | -0.077804 | -0.019706 | 1.6357e-05 | 6.1908e-06 | 0.11646 | 0.11646 | 0.11646 | 0.99493 | -0.034922 | 0.99472 | -0.036408 | 21.5671
48 | 0.076848 | 0.019466 | -0.076745 | -0.019427 | 0.000103 | 3.897e-05 | 0.11503 | 0.11503 | 0.11503 | 0.99472 | -0.036408 | 0.99334 | -0.045897 | 21.3021
49 | 0.076745 | 0.019427 | -0.076594 | -0.01937 | 0.00015068 | 5.701e-05 | 0.11503 | 0.11503 | 0.11503 | 0.99334 | -0.045897 | 0.99133 | -0.059824 | 21.3021

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16995 | 0.042689

## res_load
| p_mw | q_mvar
0 | 0.0042266 | 0.0010593
1 | 0.006205 | 0.0015551
2 | 0.00068267 | 0.00017109
3 | 0.0034513 | 0.00086499
4 | 0.0027413 | 0.00068704
5 | 0.0014224 | 0.00035648
6 | 0.0080997 | 0.00203
7 | 0.00059616 | 0.00014941
8 | 0.00092475 | 0.00023176
9 | 0.00059532 | 0.0001492
10 | 0.0010585 | 0.0002653
11 | 0.0011582 | 0.00029027
12 | 0.0014719 | 0.0003689
13 | 0.00083335 | 0.00020886
14 | 0.0014453 | 0.00036224
15 | 0.00058852 | 0.0001475
16 | 0.00050508 | 0.00012659
17 | 0.0012731 | 0.00031906
18 | 0.00027078 | 6.7863e-05
19 | 0.00065998 | 0.00016541
20 | 0.0018515 | 0.00046403
21 | 0.040565 | 0.010167
22 | 0.0007514 | 0.00018832
23 | 0.014108 | 0.0035358
24 | 0.00083565 | 0.00020943
25 | 0.00075994 | 0.00019046
26 | 0.00088712 | 0.00022233
27 | 0.00059616 | 0.00014941
28 | 0.00057816 | 0.0001449
29 | 0.00083526 | 0.00020934
30 | 0.0011969 | 0.00029996
31 | 0.014521 | 0.0036392
32 | 0.004822 | 0.0012085
33 | 0.012249 | 0.00307
34 | 0.00057837 | 0.00014495
35 | 0.00082586 | 0.00020698
36 | 0.00057811 | 0.00014489
37 | 0.0070205 | 0.0017595
38 | 0.0070231 | 0.0017601
39 | 0.015237 | 0.0038187
40 | 0.00095681 | 0.0002398
41 | 0.0012981 | 0.00032534
42 | 0.0005204 | 0.00013042

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1