## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1129-2_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1129-2_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1129-2_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1129-2_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1129-2_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1129-2_0_2_node_54 | 0.4 | n |  | TRUE
6 | bus_LV_1129-2_0_2_node_31 | 0.4 | n |  | TRUE
7 | bus_LV_1129-2_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1129-2_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1129-2_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1129-2_0_2_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_1129-2_0_2_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_1129-2_0_2_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1129-2_0_2_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1129-2_0_2_node_38 | 0.4 | n |  | TRUE
15 | bus_LV_1129-2_0_2_node_77 | 0.4 | n |  | TRUE
16 | bus_LV_1129-2_0_2_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_1129-2_0_2_node_74 | 0.4 | n |  | TRUE
18 | bus_LV_1129-2_0_2_node_40 | 0.4 | n |  | TRUE
19 | bus_LV_1129-2_0_2_node_41 | 0.4 | n |  | TRUE
20 | bus_LV_1129-2_0_2_node_73 | 0.4 | n |  | TRUE
21 | bus_LV_1129-2_0_2_node_50 | 0.4 | n |  | TRUE
22 | bus_LV_1129-2_0_2_node_51 | 0.4 | n |  | TRUE
23 | bus_LV_1129-2_0_2_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_1129-2_0_2_node_65 | 0.4 | n |  | TRUE
25 | bus_LV_1129-2_0_2_node_66 | 0.4 | n |  | TRUE
26 | bus_LV_1129-2_0_2_node_67 | 0.4 | n |  | TRUE
27 | bus_LV_1129-2_0_2_node_68 | 0.4 | n |  | TRUE
28 | bus_LV_1129-2_0_2_node_76 | 0.4 | n |  | TRUE
29 | bus_MV_0_node_41 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1129-2_0_2_load_0 | 0 | 0.00036839 | 9.2328e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1129-2_0_2_load_1 | 1 | 0.00070508 | 0.00017671 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1129-2_0_2_load_2 | 2 | 0.0004145 | 0.00010388 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1129-2_0_2_load_3 | 3 | 0.00058889 | 0.00014759 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1129-2_0_2_load_4 | 4 | 0.00023369 | 5.8569e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1129-2_0_2_load_54 | 5 | 0.0010459 | 0.00026212 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1129-2_0_2_load_31 | 6 | 0.0021436 | 0.00053723 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1129-2_0_2_load_5 | 7 | 0.00015512 | 3.8876e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1129-2_0_2_load_7 | 9 | 0.00082035 | 0.0002056 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1129-2_0_2_load_27 | 11 | 0.0001633 | 4.0926e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1129-2_0_2_load_28 | 12 | 0.0013937 | 0.00034929 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1129-2_0_2_load_29 | 13 | 0.00014801 | 3.7094e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1129-2_0_2_load_38 | 14 | 0.00043086 | 0.00010798 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1129-2_0_2_load_77 | 15 | 7.9493e-05 | 1.9923e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1129-2_0_2_load_40 | 18 | 0.00025364 | 6.3567e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1129-2_0_2_load_41 | 19 | 0.0017319 | 0.00043405 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1129-2_0_2_load_73 | 20 | 0.00025361 | 6.3561e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1129-2_0_2_load_50 | 21 | 0.0003236 | 8.1102e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1129-2_0_2_load_51 | 22 | 0.0035618 | 0.00089267 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1129-2_0_2_load_53 | 23 | 0.00069846 | 0.00017505 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1129-2_0_2_load_65 | 24 | 0.00027181 | 6.8121e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1129-2_0_2_load_66 | 25 | 0.00023611 | 5.9174e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1129-2_0_2_load_67 | 26 | 0.00090549 | 0.00022694 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1129-2_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.005197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1129-2_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.0030451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1129-2_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.02378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1129-2_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.020041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1129-2_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.015772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1129-2_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0094271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1129-2_0_2_line_6 | NAYY 4x150 SE | 5 | 23 | 0.0080394 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1129-2_0_2_line_7 | NAYY 4x150 SE | 6 | 16 | 0.0069176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1129-2_0_2_line_8 | NAYY 4x150 SE | 7 | 8 | 0.090792 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1129-2_0_2_line_9 | NAYY 4x150 SE | 7 | 9 | 0.012701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1129-2_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.50797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1129-2_0_2_line_11 | NAYY 4x150 SE | 10 | 14 | 0.021162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1129-2_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.030681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1129-2_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.032409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1129-2_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.23133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1129-2_0_2_line_15 | NAYY 4x150 SE | 13 | 15 | 0.30865 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1129-2_0_2_line_16 | NAYY 4x150 SE | 14 | 18 | 0.26331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1129-2_0_2_line_17 | NAYY 4x150 SE | 15 | 28 | 0.042655 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1129-2_0_2_line_18 | NAYY 4x150 SE | 16 | 17 | 0.26274 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1129-2_0_2_line_19 | NAYY 4x150 SE | 17 | 20 | 0.0010704 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1129-2_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.062949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1129-2_0_2_line_21 | NAYY 4x150 SE | 19 | 20 | 0.026723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1129-2_0_2_line_22 | NAYY 4x150 SE | 21 | 22 | 0.030082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1129-2_0_2_line_23 | NAYY 4x150 SE | 22 | 23 | 0.020996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1129-2_0_2_line_24 | NAYY 4x150 SE | 24 | 25 | 0.006733 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1129-2_0_2_line_25 | NAYY 4x150 SE | 24 | 26 | 0.0056444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1129-2_0_2_line_26 | NAYY 4x150 SE | 25 | 27 | 0.02874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1129-2_0_2_line_27 | NAYY 4x150 SE | 27 | 28 | 0.064577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1129-2_0_2_trafo_41 | 0.25 MVA 20/0.4 kV | 29 | 19 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2634563.8465 | 1220707.8953 | 2634566.1307 | 1220703.2271
1 | 2634563.8465 | 1220707.8953 | 2634562.5082 | 1220710.6305 | 2634562.5082 | 1220710.6305
2 | 2634566.1307 | 1220703.2271 | 2634569.1261 | 1220697.1053 | 2634578.5718 | 1220683.0135
3 | 2634560.5574 | 1220730.2975 | 2634560.2804 | 1220729.8067 | 2634559.8918 | 1220722.2444 | 2634562.5082 | 1220710.6305
4 | 2634584.099 | 1220668.6642 | 2634582.9928 | 1220676.4179 | 2634578.5718 | 1220683.0135
5 | 2634560.5574 | 1220730.2975 | 2634565.1914 | 1220738.507 | 2634565.1914 | 1220738.507
6 | 2634584.099 | 1220668.6642 | 2634584.5744 | 1220665.3316 | 2634582.943 | 1220660.9527
7 | 2634570.4455 | 1220743.0067 | 2634565.1914 | 1220738.507
8 | 2635183.8312 | 1221505.8459 | 2635199.7649 | 1221499.9809 | 2635208.177 | 1221492.3038 | 2635217.1693 | 1221481.4282 | 2635223.5582 | 1221468.2804 | 2635226.895 | 1221454.3029 | 2635226.5897 | 1221440.4929 | 2635225.0142 | 1221435.2119
9 | 2635221.383 | 1221423.0407 | 2635225.0142 | 1221435.2119
10 | 2635183.8312 | 1221505.8459 | 2634711.2979 | 1221319.4438
11 | 2634711.2979 | 1221319.4438 | 2634699.0819 | 1221302.1638
12 | 2634407.9727 | 1221291.5686 | 2634418.6522 | 1221296.8452 | 2634436.5146 | 1221302.6077
13 | 2634467.8832 | 1221310.045 | 2634455.8135 | 1221308.8336 | 2634436.5146 | 1221302.6077
14 | 2634467.8832 | 1221310.045 | 2634699.0819 | 1221302.1638
15 | 2634467.8832 | 1221310.045 | 2634513.4053 | 1221615.3147
16 | 2634699.0819 | 1221302.1638 | 2634609.5552 | 1221054.5449
17 | 2634502.3087 | 1221654.2738 | 2634501.4775 | 1221644.5632 | 2634502.3501 | 1221634.0287 | 2634512.5968 | 1221621.1025 | 2634513.4053 | 1221615.3147
18 | 2634570.4455 | 1220743.0067 | 2634548.8995 | 1221004.8589
19 | 2634548.8995 | 1221004.8589 | 2634549.9657 | 1221004.9524
20 | 2634576.5382 | 1221007.7443 | 2634581.2566 | 1221008.3374 | 2634591.4044 | 1221012.6544 | 2634600.3079 | 1221022.245 | 2634602.8936 | 1221031.5878 | 2634602.8476 | 1221039.5033 | 2634609.5552 | 1221054.5449
21 | 2634576.5382 | 1221007.7443 | 2634564.3823 | 1221006.2161 | 2634549.9657 | 1221004.9524
22 | 2634541.6397 | 1220633.6462 | 2634543.155 | 1220634.7402 | 2634568.5826 | 1220646.9635
23 | 2634568.5826 | 1220646.9635 | 2634576.163 | 1220650.6075 | 2634581.1456 | 1220656.1285 | 2634582.943 | 1220660.9527
24 | 2634563.8107 | 1221637.8206 | 2634562.113 | 1221644.336
25 | 2634565.234 | 1221632.3585 | 2634563.8107 | 1221637.8206
26 | 2634564.6179 | 1221671.8895 | 2634561.6068 | 1221666.6134 | 2634559.9774 | 1221661.134 | 2634561.6964 | 1221645.935 | 2634562.113 | 1221644.336
27 | 2634564.6179 | 1221671.8895 | 2634517.493 | 1221658.4308 | 2634502.3087 | 1221654.2738

## bus_geodata
| x | y | coords
0 | 2634563.8465 | 1220707.8953
1 | 2634566.1307 | 1220703.2271
2 | 2634562.5082 | 1220710.6305
3 | 2634578.5718 | 1220683.0135
4 | 2634560.5574 | 1220730.2975
5 | 2634584.099 | 1220668.6642
6 | 2634565.1914 | 1220738.507
7 | 2635225.0142 | 1221435.2119
8 | 2635183.8312 | 1221505.8459
9 | 2635221.383 | 1221423.0407
10 | 2634711.2979 | 1221319.4438
11 | 2634436.5146 | 1221302.6077
12 | 2634407.9727 | 1221291.5686
13 | 2634467.8832 | 1221310.045
14 | 2634699.0819 | 1221302.1638
15 | 2634513.4053 | 1221615.3147
16 | 2634570.4455 | 1220743.0067
17 | 2634548.8995 | 1221004.8589
18 | 2634609.5552 | 1221054.5449
19 | 2634576.5382 | 1221007.7443
20 | 2634549.9657 | 1221004.9524
21 | 2634541.6397 | 1220633.6462
22 | 2634568.5826 | 1220646.9635
23 | 2634582.943 | 1220660.9527
24 | 2634563.8107 | 1221637.8206
25 | 2634562.113 | 1221644.336
26 | 2634565.234 | 1221632.3585
27 | 2634564.6179 | 1221671.8895
28 | 2634502.3087 | 1221654.2738
29 | 2634576.5382 | 1221007.7443

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99533 | -0.032752 | 0.00036839 | 9.2328e-05
1 | 0.99528 | -0.033115 | 0.00070508 | 0.00017671
2 | 0.99537 | -0.032528 | 0.0004145 | 0.00010388
3 | 0.99507 | -0.034607 | 0.00058889 | 0.00014759
4 | 0.99559 | -0.03097 | 0.00023369 | 5.8569e-05
5 | 0.99494 | -0.035503 | 0.0010459 | 0.00026212
6 | 0.99569 | -0.030215 | 0.0021436 | 0.00053723
7 | 0.99697 | -0.021938 | 0.00015512 | 3.8876e-05
8 | 0.9971 | -0.021043 | 0 | 0
9 | 0.99695 | -0.022042 | 0.00082035 | 0.0002056
10 | 0.9978 | -0.015895 | 0 | 0
11 | 0.9967 | -0.023751 | 0.0001633 | 4.0926e-05
12 | 0.99664 | -0.024181 | 0.0013937 | 0.00034929
13 | 0.99677 | -0.023242 | 0.00014801 | 3.7094e-05
14 | 0.99783 | -0.015676 | 0.00043086 | 0.00010798
15 | 0.99612 | -0.027965 | 7.9493e-05 | 1.9923e-05
16 | 0.99579 | -0.029512 | 0 | 0
17 | 0.99959 | -0.0028773 | 0 | 0
18 | 0.99956 | -0.003156 | 0.00025364 | 6.3567e-05
19 | 1 | 0 | -0.016059 | -0.0038049
20 | 0.9996 | -0.0027691 | 0.00025361 | 6.3561e-05
21 | 0.99476 | -0.036797 | 0.0003236 | 8.1102e-05
22 | 0.99477 | -0.036699 | 0.0035618 | 0.00089267
23 | 0.99489 | -0.035875 | 0.00069846 | 0.00017505
24 | 0.99583 | -0.029989 | 0.00027181 | 6.8121e-05
25 | 0.99584 | -0.029909 | 0.00023611 | 5.9174e-05
26 | 0.99582 | -0.03004 | 0.00090549 | 0.00022694
27 | 0.9959 | -0.0295 | 0 | 0
28 | 0.99603 | -0.028577 | 0 | 0
29 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0069267 | 0.001735 | -0.0069263 | -0.001735 | 3.4773e-07 | 6.6199e-08 | 0.010355 | 0.010355 | 0.010355 | 0.99533 | -0.032752 | 0.99528 | -0.033115 | 3.8352
1 | -0.0072951 | -0.0018274 | 0.0072953 | 0.0018274 | 2.26e-07 | 4.7342e-08 | 0.010906 | 0.010906 | 0.010906 | 0.99533 | -0.032752 | 0.99537 | -0.032528 | 4.0392
2 | 0.0062213 | 0.0015583 | -0.00622 | -0.0015581 | 1.2837e-06 | 1.8474e-07 | 0.0093009 | 0.009301 | 0.009301 | 0.99528 | -0.033115 | 0.99507 | -0.034607 | 3.4448
3 | -0.0077098 | -0.0019313 | 0.0077115 | 0.0019317 | 1.6612e-06 | 3.7836e-07 | 0.011525 | 0.011525 | 0.011525 | 0.99537 | -0.032528 | 0.99559 | -0.03097 | 4.2687
4 | 0.0056311 | 0.0014105 | -0.0056304 | -0.0014104 | 6.9783e-07 | 6.3535e-08 | 0.0084204 | 0.0084205 | 0.0084205 | 0.99507 | -0.034607 | 0.99494 | -0.035503 | 3.1187
5 | -0.0079452 | -0.0019903 | 0.007946 | 0.0019905 | 8.2946e-07 | 1.9642e-07 | 0.011875 | 0.011875 | 0.011875 | 0.99559 | -0.03097 | 0.99569 | -0.030215 | 4.398
6 | 0.0045845 | 0.0011483 | -0.0045843 | -0.0011483 | 2.3582e-07 | -1.37e-08 | 0.0068563 | 0.0068563 | 0.0068563 | 0.99494 | -0.035503 | 0.99489 | -0.035875 | 2.5394
7 | -0.01009 | -0.0025277 | 0.010091 | 0.002528 | 9.8136e-07 | 2.8746e-07 | 0.015078 | 0.015078 | 0.015078 | 0.99569 | -0.030215 | 0.99579 | -0.029512 | 5.5845
8 | -0.00097548 | -0.00024431 | 0.0009756 | 0.00024318 | 1.2005e-07 | -1.1379e-06 | 0.0014559 | 0.0014555 | 0.0014559 | 0.99697 | -0.021938 | 0.9971 | -0.021043 | 0.53921
9 | 0.00082036 | 0.00020544 | -0.00082035 | -0.0002056 | 1.1882e-08 | -1.6105e-07 | 0.0012244 | 0.0012244 | 0.0012244 | 0.99697 | -0.021938 | 0.99695 | -0.022042 | 0.45349
10 | -0.0009756 | -0.00024318 | 0.00097627 | 0.0002368 | 6.7041e-07 | -6.3724e-06 | 0.0014555 | 0.0014532 | 0.0014555 | 0.9971 | -0.021043 | 0.9978 | -0.015895 | 0.53906
11 | -0.00097627 | -0.0002368 | 0.00097629 | 0.00023654 | 2.7883e-08 | -2.6569e-07 | 0.0014532 | 0.0014531 | 0.0014532 | 0.9978 | -0.015895 | 0.99783 | -0.015676 | 0.53821
12 | 0.0013938 | 0.00034892 | -0.0013937 | -0.00034929 | 8.2886e-08 | -3.6796e-07 | 0.0020807 | 0.0020808 | 0.0020808 | 0.9967 | -0.023751 | 0.99664 | -0.024181 | 0.77067
13 | -0.0015571 | -0.00038985 | 0.0015572 | 0.00038947 | 1.0926e-07 | -3.8039e-07 | 0.0023245 | 0.0023243 | 0.0023245 | 0.9967 | -0.023751 | 0.99677 | -0.023242 | 0.86091
14 | -0.0031994 | -0.00079528 | 0.0032027 | 0.00079353 | 3.2891e-06 | -1.7536e-06 | 0.0047739 | 0.0047728 | 0.0047739 | 0.99677 | -0.023242 | 0.99783 | -0.015676 | 1.7681
15 | 0.0014942 | 0.00036872 | -0.0014933 | -0.00037238 | 9.5719e-07 | -3.6523e-06 | 0.0022286 | 0.00223 | 0.00223 | 0.99677 | -0.023242 | 0.99612 | -0.027965 | 0.82594
16 | -0.0046099 | -0.0011381 | 0.0046176 | 0.0011376 | 7.7497e-06 | -4.6476e-07 | 0.0068684 | 0.0068672 | 0.0068684 | 0.99783 | -0.015676 | 0.99956 | -0.003156 | 2.5439
17 | 0.0014138 | 0.00035245 | -0.0014137 | -0.00035296 | 1.1866e-07 | -5.0959e-07 | 0.0021113 | 0.0021115 | 0.0021115 | 0.99612 | -0.027965 | 0.99603 | -0.028577 | 0.78203
18 | -0.010091 | -0.002528 | 0.010128 | 0.0025389 | 3.727e-05 | 1.0904e-05 | 0.015078 | 0.015077 | 0.015078 | 0.99579 | -0.029512 | 0.99959 | -0.0028773 | 5.5844
19 | -0.010128 | -0.0025389 | 0.010128 | 0.0025389 | 1.5182e-07 | 4.4361e-08 | 0.015077 | 0.015077 | 0.015077 | 0.99959 | -0.0028773 | 0.9996 | -0.0027691 | 5.584
20 | -0.0048712 | -0.0012012 | 0.0048733 | 0.0012011 | 2.0616e-06 | -3.2554e-08 | 0.0072448 | 0.0072445 | 0.0072448 | 0.99956 | -0.003156 | 1 | 0 | 2.6833
21 | 0.010386 | 0.0026037 | -0.010382 | -0.0026025 | 3.9827e-06 | 1.1813e-06 | 0.015454 | 0.015454 | 0.015454 | 1 | 0 | 0.9996 | -0.0027691 | 5.7238
22 | -0.0003236 | -8.1102e-05 | 0.0003236 | 8.0713e-05 | 4.397e-09 | -3.8884e-07 | 0.00048406 | 0.00048392 | 0.00048406 | 0.99476 | -0.036797 | 0.99477 | -0.036699 | 0.17928
23 | -0.0038854 | -0.00097338 | 0.0038858 | 0.00097328 | 4.4251e-07 | -1.0241e-07 | 0.0058118 | 0.0058117 | 0.0058118 | 0.99477 | -0.036699 | 0.99489 | -0.035875 | 2.1525
24 | -0.0011773 | -0.00029499 | 0.0011773 | 0.0002949 | 1.3001e-08 | -8.2597e-08 | 0.0017592 | 0.0017591 | 0.0017592 | 0.99583 | -0.029989 | 0.99584 | -0.029909 | 0.65154
25 | 0.00090549 | 0.00022687 | -0.00090549 | -0.00022694 | 6.4478e-09 | -7.0954e-08 | 0.001353 | 0.001353 | 0.001353 | 0.99583 | -0.029989 | 0.99582 | -0.03004 | 0.50112
26 | -0.0014134 | -0.00035408 | 0.0014135 | 0.00035373 | 7.9982e-08 | -3.4317e-07 | 0.0021119 | 0.0021118 | 0.0021119 | 0.99584 | -0.029909 | 0.9959 | -0.0295 | 0.78219
27 | -0.0014135 | -0.00035373 | 0.0014137 | 0.00035296 | 1.7968e-07 | -7.7127e-07 | 0.0021118 | 0.0021115 | 0.0021118 | 0.9959 | -0.0295 | 0.99603 | -0.028577 | 0.78214

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.017791 | 0.0042389

## res_load
| p_mw | q_mvar
0 | 0.00036839 | 9.2328e-05
1 | 0.00070508 | 0.00017671
2 | 0.0004145 | 0.00010388
3 | 0.00058889 | 0.00014759
4 | 0.00023369 | 5.8569e-05
5 | 0.0010459 | 0.00026212
6 | 0.0021436 | 0.00053723
7 | 0.00015512 | 3.8876e-05
8 | 0.00082035 | 0.0002056
9 | 0.0001633 | 4.0926e-05
10 | 0.0013937 | 0.00034929
11 | 0.00014801 | 3.7094e-05
12 | 0.00043086 | 0.00010798
13 | 7.9493e-05 | 1.9923e-05
14 | 0.00025364 | 6.3567e-05
15 | 0.0017319 | 0.00043405
16 | 0.00025361 | 6.3561e-05
17 | 0.0003236 | 8.1102e-05
18 | 0.0035618 | 0.00089267
19 | 0.00069846 | 0.00017505
20 | 0.00027181 | 6.8121e-05
21 | 0.00023611 | 5.9174e-05
22 | 0.00090549 | 0.00022694

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1