## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1132-1_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1132-1_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1132-1_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1132-1_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1132-1_0_3_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1132-1_0_3_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1132-1_0_3_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1132-1_0_3_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1132-1_0_3_node_79 | 0.4 | n |  | TRUE
9 | bus_LV_1132-1_0_3_node_69 | 0.4 | n |  | TRUE
10 | bus_LV_1132-1_0_3_node_61 | 0.4 | n |  | TRUE
11 | bus_LV_1132-1_0_3_node_75 | 0.4 | n |  | TRUE
12 | bus_LV_1132-1_0_3_node_78 | 0.4 | n |  | TRUE
13 | bus_LV_1132-1_0_3_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1132-1_0_3_node_40 | 0.4 | n |  | TRUE
15 | bus_LV_1132-1_0_3_node_74 | 0.4 | n |  | TRUE
16 | bus_LV_1132-1_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1132-1_0_3_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_1132-1_0_3_node_73 | 0.4 | n |  | TRUE
19 | bus_LV_1132-1_0_3_node_77 | 0.4 | n |  | TRUE
20 | bus_LV_1132-1_0_3_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_1132-1_0_3_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_1132-1_0_3_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_1132-1_0_3_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_1132-1_0_3_node_38 | 0.4 | n |  | TRUE
25 | bus_LV_1132-1_0_3_node_39 | 0.4 | n |  | TRUE
26 | bus_LV_1132-1_0_3_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_1132-1_0_3_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_1132-1_0_3_node_59 | 0.4 | n |  | TRUE
29 | bus_LV_1132-1_0_3_node_60 | 0.4 | n |  | TRUE
30 | bus_LV_1132-1_0_3_node_76 | 0.4 | n |  | TRUE
31 | bus_MV_128_0_node_294 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1132-1_0_3_load_0 | 0 | 0.0343 | 0.0085964 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1132-1_0_3_load_6 | 4 | 0.010582 | 0.0026522 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1132-1_0_3_load_79 | 8 | 0.050207 | 0.012583 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1132-1_0_3_load_69 | 9 | 0.0040717 | 0.0010205 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1132-1_0_3_load_61 | 10 | 0.00059558 | 0.00014927 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1132-1_0_3_load_75 | 11 | 0.045181 | 0.011324 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1132-1_0_3_load_78 | 12 | 0.0073346 | 0.0018382 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1132-1_0_3_load_74 | 15 | 0.0059217 | 0.0014841 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1132-1_0_3_load_73 | 18 | 0.020426 | 0.0051193 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1132-1_0_3_load_77 | 19 | 0.013702 | 0.0034341 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1132-1_0_3_load_16 | 20 | 0.00068138 | 0.00017077 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1132-1_0_3_load_17 | 21 | 0.00017927 | 4.493e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1132-1_0_3_load_18 | 22 | 0.00021887 | 5.4853e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1132-1_0_3_load_38 | 24 | 0.0019261 | 0.00048274 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1132-1_0_3_load_41 | 26 | 0.00029447 | 7.3802e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1132-1_0_3_load_59 | 28 | 0.0027795 | 0.0006966 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1132-1_0_3_load_60 | 29 | 0.0023483 | 0.00058854 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1132-1_0_3_load_76 | 30 | 0.0023559 | 0.00059044 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1132-1_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.066178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1132-1_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.015238 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1132-1_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.065368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1132-1_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.01526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1132-1_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.040279 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1132-1_0_3_line_5 | NAYY 4x150 SE | 3 | 9 | 0.044024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1132-1_0_3_line_6 | NAYY 4x150 SE | 3 | 10 | 0.048404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1132-1_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.020473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1132-1_0_3_line_8 | NAYY 4x150 SE | 5 | 12 | 0.021184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1132-1_0_3_line_9 | NAYY 4x150 SE | 6 | 7 | 0.008129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1132-1_0_3_line_10 | NAYY 4x150 SE | 6 | 8 | 0.007572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1132-1_0_3_line_11 | NAYY 4x150 SE | 7 | 11 | 0.014237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1132-1_0_3_line_12 | NAYY 4x150 SE | 9 | 30 | 0.016117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1132-1_0_3_line_13 | NAYY 4x150 SE | 10 | 29 | 0.013162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1132-1_0_3_line_14 | NAYY 4x150 SE | 11 | 16 | 0.015854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1132-1_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.37854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1132-1_0_3_line_16 | NAYY 4x150 SE | 13 | 15 | 0.071187 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1132-1_0_3_line_17 | NAYY 4x150 SE | 14 | 24 | 0.057321 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1132-1_0_3_line_18 | NAYY 4x150 SE | 15 | 18 | 0.053146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1132-1_0_3_line_19 | NAYY 4x150 SE | 16 | 17 | 0.032898 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1132-1_0_3_line_20 | NAYY 4x150 SE | 16 | 18 | 0.051295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1132-1_0_3_line_21 | NAYY 4x150 SE | 17 | 19 | 0.026628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1132-1_0_3_line_22 | NAYY 4x150 SE | 20 | 21 | 0.023542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1132-1_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.03119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1132-1_0_3_line_24 | NAYY 4x150 SE | 22 | 23 | 0.12566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1132-1_0_3_line_25 | NAYY 4x150 SE | 23 | 27 | 0.14184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1132-1_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.020281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1132-1_0_3_line_27 | NAYY 4x150 SE | 25 | 26 | 0.013884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1132-1_0_3_line_28 | NAYY 4x150 SE | 27 | 28 | 0.26692 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1132-1_0_3_line_29 | NAYY 4x150 SE | 28 | 29 | 0.029653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1132-1_0_3_trafo_3 | 0.25 MVA 20/0.4 kV | 31 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24
0 | 2639517.049 | 1214983.6482 | 2639503.0178 | 1214952.3593 | 2639501.8594 | 1214950.6951 | 2639500.3907 | 1214950.0072 | 2639498.726 | 1214950.2519 | 2639473.9455 | 1214959.7961
1 | 2639459.2374 | 1214961.8196 | 2639464.9504 | 1214962.5912 | 2639467.5954 | 1214962.2418 | 2639473.9455 | 1214959.7961
2 | 2639517.049 | 1214983.6482 | 2639518.111 | 1214983.8109 | 2639518.7756 | 1214984.3712 | 2639520.0383 | 1214986.3474 | 2639523.3622 | 1214994.6854 | 2639523.6412 | 1214996.1325 | 2639523.5661 | 1214997.1548 | 2639523.0371 | 1214997.9184 | 2639522.4331 | 1214998.5259 | 2639521.2057 | 1214999.2627 | 2639510.4586 | 1215004.1277 | 2639509.0323 | 1215005.0632 | 2639508.4856 | 1215006.2047 | 2639508.6682 | 1215007.2954 | 2639509.4143 | 1215009.3127 | 2639536.7637 | 1215001.8005
3 | 2639459.2374 | 1214961.8196 | 2639460.2359 | 1214960.103 | 2639460.3137 | 1214957.5353 | 2639458.7241 | 1214946.9491
4 | 2639443.6323 | 1214985.8861 | 2639437.2167 | 1214970.7793 | 2639457.7561 | 1214963.0328 | 2639459.2374 | 1214961.8196
5 | 2639536.7637 | 1215001.8005 | 2639536.1224 | 1214998.8835 | 2639528.4836 | 1214969.0043 | 2639527.0573 | 1214958.907
6 | 2639536.7637 | 1215001.8005 | 2639543.9509 | 1215001.2812 | 2639580.4325 | 1214996.5536 | 2639584.7222 | 1214995.5259
7 | 2639443.6323 | 1214985.8861 | 2639451.012 | 1215004.983
8 | 2639443.6323 | 1214985.8861 | 2639424.5235 | 1214995.0294
9 | 2639453.7413 | 1215012.046 | 2639454.1286 | 1215014.3388 | 2639454.182 | 1215016.596 | 2639453.9714 | 1215018.5846 | 2639453.4454 | 1215020.0376
10 | 2639453.7413 | 1215012.046 | 2639451.012 | 1215004.983
11 | 2639453.4454 | 1215020.0376 | 2639452.4019 | 1215021.6761 | 2639450.878 | 1215023.5893 | 2639448.6332 | 1215025.4423 | 2639445.704 | 1215027.4352 | 2639442.7408 | 1215029.0916
12 | 2639527.0573 | 1214958.907 | 2639525.0019 | 1214944.3557 | 2639525.0895 | 1214942.9377
13 | 2639596.2935 | 1214989.4256 | 2639593.7024 | 1214991.4386 | 2639589.2447 | 1214993.7548 | 2639584.7222 | 1214995.5259 | 2639584.7222 | 1214995.5259
14 | 2639429.7176 | 1215038.0135 | 2639434.0634 | 1215034.24 | 2639436.3672 | 1215032.6543 | 2639442.7408 | 1215029.0916
15 | 2639508.7323 | 1215194.8055 | 2639523.2352 | 1215221.2726 | 2639539.7511 | 1215255.6354 | 2639543.7416 | 1215264.2113 | 2639547.8741 | 1215277.691 | 2639559.0952 | 1215307.7719 | 2639563.1891 | 1215316.771 | 2639566.3963 | 1215322.062 | 2639569.9575 | 1215326.655 | 2639574.932 | 1215332.2579 | 2639579.8299 | 1215336.8042 | 2639587.4753 | 1215342.7028 | 2639608.0896 | 1215356.6699 | 2639623.4554 | 1215367.4227 | 2639632.5973 | 1215370.9299 | 2639637.1233 | 1215373.1613 | 2639655.943 | 1215385.2045 | 2639664.3583 | 1215389.4851 | 2639672.6988 | 1215392.4534 | 2639683.093 | 1215394.8795 | 2639692.0377 | 1215396.0619 | 2639703.3419 | 1215396.3928 | 2639730.6666 | 1215395.7855 | 2639771.2475 | 1215401.1367 | 2639781.5949 | 1215402.6065
16 | 2639508.7323 | 1215194.8055 | 2639475.7232 | 1215131.6946
17 | 2639781.5949 | 1215402.6065 | 2639786.7596 | 1215406.9657 | 2639809.1874 | 1215434.6871 | 2639818.1689 | 1215446.5819
18 | 2639475.7232 | 1215131.6946 | 2639464.9555 | 1215111.0224 | 2639452.044 | 1215087.2565 | 2639450.7953 | 1215084.7607
19 | 2639405.1858 | 1215050.1141 | 2639408.1098 | 1215054.6472 | 2639418.2855 | 1215047.7325 | 2639424.9891 | 1215043.3965 | 2639426.0959 | 1215042.5255 | 2639427.2502 | 1215041.3658 | 2639428.3006 | 1215039.8496 | 2639428.9068 | 1215038.8975 | 2639429.7176 | 1215038.0135
20 | 2639429.7176 | 1215038.0135 | 2639444.4594 | 1215072.0975 | 2639450.7953 | 1215084.7607
21 | 2639405.1858 | 1215050.1141 | 2639400.5155 | 1215043.2348 | 2639390.2511 | 1215028.0682
22 | 2639529.1885 | 1214449.5545 | 2639528.7041 | 1214444.1215 | 2639529.9602 | 1214426.0775
23 | 2639529.1885 | 1214449.5545 | 2639529.6443 | 1214454.6672 | 2639532.8514 | 1214464.6498 | 2639531.9725 | 1214472.3485 | 2639528.4784 | 1214479.3481
24 | 2639528.4784 | 1214479.3481 | 2639624.0749 | 1214560.8998
25 | 2639624.0749 | 1214560.8998 | 2639648.8154 | 1214700.5679
26 | 2639830.3901 | 1215462.7672 | 2639818.1689 | 1215446.5819
27 | 2639830.3901 | 1215462.7672 | 2639837.9712 | 1215474.3983
28 | 2639612.9503 | 1214965.0704 | 2639648.8154 | 1214700.5679
29 | 2639596.2935 | 1214989.4256 | 2639597.4198 | 1214988.5505 | 2639600.5405 | 1214985.1803 | 2639603.7932 | 1214980.2101 | 2639612.9503 | 1214965.0704

## bus_geodata
| x | y | coords
0 | 2639473.9455 | 1214959.7961
1 | 2639517.049 | 1214983.6482
2 | 2639459.2374 | 1214961.8196
3 | 2639536.7637 | 1215001.8005
4 | 2639458.7241 | 1214946.9491
5 | 2639443.6323 | 1214985.8861
6 | 2639453.7413 | 1215012.046
7 | 2639453.4455 | 1215020.0376
8 | 2639451.012 | 1215004.983
9 | 2639527.0573 | 1214958.907
10 | 2639584.7222 | 1214995.5259
11 | 2639442.7408 | 1215029.0916
12 | 2639424.5235 | 1214995.0294
13 | 2639508.7323 | 1215194.8055
14 | 2639781.5949 | 1215402.6065
15 | 2639475.7232 | 1215131.6946
16 | 2639429.7176 | 1215038.0135
17 | 2639405.1858 | 1215050.1141
18 | 2639450.7953 | 1215084.7607
19 | 2639390.2511 | 1215028.0682
20 | 2639529.1885 | 1214449.5545
21 | 2639529.9602 | 1214426.0775
22 | 2639528.4784 | 1214479.3481
23 | 2639624.0749 | 1214560.8998
24 | 2639818.1689 | 1215446.5819
25 | 2639830.3901 | 1215462.7672
26 | 2639837.9712 | 1215474.3983
27 | 2639648.8154 | 1214700.5679
28 | 2639612.9503 | 1214965.0704
29 | 2639596.2935 | 1214989.4256
30 | 2639525.0895 | 1214942.9377
31 | 2639453.4455 | 1215020.0376

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99305 | -0.048742 | 0.0343 | 0.0085964
1 | 0.99179 | -0.057669 | 0 | 0
2 | 0.99409 | -0.041407 | 0 | 0
3 | 0.99054 | -0.066504 | 0 | 0
4 | 0.99386 | -0.043038 | 0.010582 | 0.0026522
5 | 0.99745 | -0.017811 | 0 | 0
6 | 1 | 0 | -0.20474 | -0.051203
7 | 0.99898 | -0.007108 | 0 | 0
8 | 0.99937 | -0.0043764 | 0.050207 | 0.012583
9 | 0.99014 | -0.069385 | 0.0040717 | 0.0010205
10 | 0.99007 | -0.069886 | 0.00059558 | 0.00014927
11 | 0.9972 | -0.019592 | 0.045181 | 0.011324
12 | 0.99723 | -0.01937 | 0.0073346 | 0.0018382
13 | 0.99329 | -0.047169 | 0 | 0
14 | 0.99208 | -0.055786 | 0 | 0
15 | 0.99352 | -0.045535 | 0.0059217 | 0.0014841
16 | 0.99624 | -0.026335 | 0 | 0
17 | 0.99559 | -0.030872 | 0 | 0
18 | 0.99414 | -0.041133 | 0.020426 | 0.0051193
19 | 0.99507 | -0.034549 | 0.013702 | 0.0034341
20 | 0.98892 | -0.078234 | 0.00068138 | 0.00017077
21 | 0.98891 | -0.078277 | 0.00017927 | 4.493e-05
22 | 0.98896 | -0.077959 | 0.00021887 | 5.4853e-05
23 | 0.98915 | -0.076561 | 0 | 0
24 | 0.9919 | -0.057081 | 0.0019261 | 0.00048274
25 | 0.99189 | -0.057142 | 0 | 0
26 | 0.99189 | -0.057183 | 0.00029447 | 7.3802e-05
27 | 0.98937 | -0.074964 | 0 | 0
28 | 0.98979 | -0.071909 | 0.0027795 | 0.0006966
29 | 0.98995 | -0.070726 | 0.0023483 | 0.00058854
30 | 0.99008 | -0.069772 | 0.0023559 | 0.00059044
31 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.013271 | 0.0033202 | -0.013255 | -0.0033148 | 1.6327e-05 | 5.4244e-06 | 0.019884 | 0.019884 | 0.019884 | 0.99305 | -0.048742 | 0.99179 | -0.057669 | 7.3644
1 | -0.047571 | -0.011917 | 0.047619 | 0.011935 | 4.831e-05 | 1.8383e-05 | 0.07128 | 0.07128 | 0.07128 | 0.99305 | -0.048742 | 0.99409 | -0.041407 | 26.3999
2 | 0.013255 | 0.0033148 | -0.013239 | -0.0033095 | 1.6127e-05 | 5.3603e-06 | 0.019884 | 0.019884 | 0.019884 | 0.99179 | -0.057669 | 0.99054 | -0.066504 | 7.3645
3 | 0.010585 | 0.0026529 | -0.010582 | -0.0026522 | 2.3904e-06 | 7.2158e-07 | 0.015844 | 0.015844 | 0.015844 | 0.99409 | -0.041407 | 0.99386 | -0.043038 | 5.8682
4 | -0.058204 | -0.014588 | 0.058395 | 0.014661 | 0.00019078 | 7.2853e-05 | 0.087124 | 0.087124 | 0.087124 | 0.99409 | -0.041407 | 0.99745 | -0.017811 | 32.2681
5 | 0.0064302 | 0.0016112 | -0.0064277 | -0.0016107 | 2.5633e-06 | 4.1941e-07 | 0.0096595 | 0.0096597 | 0.0096597 | 0.99054 | -0.066504 | 0.99014 | -0.069385 | 3.5777
6 | 0.0068083 | 0.0016983 | -0.0068051 | -0.0016977 | 3.1578e-06 | 5.9175e-07 | 0.010225 | 0.010225 | 0.010225 | 0.99054 | -0.066504 | 0.99007 | -0.069886 | 3.787
7 | -0.065731 | -0.016499 | 0.065854 | 0.016546 | 0.00012286 | 4.6987e-05 | 0.098068 | 0.098068 | 0.098068 | 0.99745 | -0.017811 | 0.99937 | -0.0043764 | 36.3214
8 | 0.0073361 | 0.0018385 | -0.0073346 | -0.0018382 | 1.5833e-06 | 3.3251e-07 | 0.010944 | 0.010944 | 0.010944 | 0.99745 | -0.017811 | 0.99723 | -0.01937 | 4.0534
9 | 0.087813 | 0.022047 | -0.087726 | -0.022013 | 8.6625e-05 | 3.3211e-05 | 0.13068 | 0.13068 | 0.13068 | 1 | 0 | 0.99898 | -0.007108 | 48.4002
10 | 0.11613 | 0.029156 | -0.11606 | -0.029129 | 7.0562e-05 | 2.6941e-05 | 0.17282 | 0.17282 | 0.17282 | 1 | 0 | 0.99937 | -0.0043764 | 32.0043
11 | 0.087726 | 0.022013 | -0.087574 | -0.021955 | 0.00015171 | 5.8165e-05 | 0.13068 | 0.13068 | 0.13068 | 0.99898 | -0.007108 | 0.9972 | -0.019592 | 48.4002
12 | 0.002356 | 0.00059028 | -0.0023559 | -0.00059044 | 1.2608e-07 | -1.5878e-07 | 0.0035406 | 0.0035407 | 0.0035407 | 0.99014 | -0.069385 | 0.99008 | -0.069772 | 1.3114
13 | 0.0062096 | 0.0015485 | -0.0062089 | -0.0015483 | 7.149e-07 | 1.0572e-07 | 0.0093299 | 0.0093299 | 0.0093299 | 0.99007 | -0.069886 | 0.98995 | -0.070726 | 3.4555
14 | 0.042393 | 0.010632 | -0.042353 | -0.010617 | 3.9591e-05 | 1.5021e-05 | 0.063261 | 0.063261 | 0.063261 | 0.9972 | -0.019592 | 0.99624 | -0.026335 | 23.43
15 | 0.0022236 | 0.00055162 | -0.002221 | -0.00055551 | 2.6193e-06 | -3.8863e-06 | 0.0033292 | 0.0033309 | 0.0033309 | 0.99329 | -0.047169 | 0.99208 | -0.055786 | 1.2337
16 | -0.0022236 | -0.00055162 | 0.0022241 | 0.00055089 | 4.9228e-07 | -7.323e-07 | 0.0033292 | 0.0033288 | 0.0033292 | 0.99329 | -0.047169 | 0.99352 | -0.045535 | 1.233
17 | 0.002221 | 0.00055551 | -0.0022206 | -0.0005561 | 3.9687e-07 | -5.8737e-07 | 0.0033309 | 0.0033311 | 0.0033311 | 0.99208 | -0.055786 | 0.9919 | -0.057081 | 1.2338
18 | -0.0081459 | -0.002035 | 0.0081508 | 0.0020362 | 4.9342e-06 | 1.2091e-06 | 0.012198 | 0.012198 | 0.012198 | 0.99352 | -0.045535 | 0.99414 | -0.041133 | 4.5178
19 | 0.013718 | 0.0034394 | -0.013709 | -0.0034365 | 8.6187e-06 | 2.8868e-06 | 0.02049 | 0.02049 | 0.02049 | 0.99624 | -0.026335 | 0.99559 | -0.030872 | 7.589
20 | 0.028635 | 0.0071774 | -0.028577 | -0.0071555 | 5.8555e-05 | 2.1855e-05 | 0.042771 | 0.042771 | 0.042771 | 0.99624 | -0.026335 | 0.99414 | -0.041133 | 15.8412
21 | 0.013709 | 0.0034365 | -0.013702 | -0.0034341 | 6.9762e-06 | 2.3371e-06 | 0.02049 | 0.02049 | 0.02049 | 0.99559 | -0.030872 | 0.99507 | -0.034549 | 7.589
22 | 0.00017927 | 4.4629e-05 | -0.00017927 | -4.493e-05 | 1.0685e-09 | -3.0164e-07 | 0.00026965 | 0.00026975 | 0.00026975 | 0.98892 | -0.078234 | 0.98891 | -0.078277 | 0.099909
23 | -0.00086065 | -0.0002154 | 0.00086069 | 0.00021501 | 3.2631e-08 | -3.8764e-07 | 0.0012949 | 0.0012948 | 0.0012949 | 0.98892 | -0.078234 | 0.98896 | -0.077959 | 0.4796
24 | -0.0010796 | -0.00026986 | 0.0010798 | 0.00026833 | 2.0674e-07 | -1.5331e-06 | 0.0016241 | 0.0016235 | 0.0016241 | 0.98896 | -0.077959 | 0.98915 | -0.076561 | 0.60151
25 | -0.0010798 | -0.00026833 | 0.00108 | 0.0002666 | 2.332e-07 | -1.7314e-06 | 0.0016235 | 0.0016229 | 0.0016235 | 0.98915 | -0.076561 | 0.98937 | -0.074964 | 0.6013
26 | 0.00029448 | 7.3362e-05 | -0.00029447 | -7.3623e-05 | 2.4685e-09 | -2.6083e-07 | 0.00044161 | 0.0004417 | 0.0004417 | 0.9919 | -0.057081 | 0.99189 | -0.057142 | 0.16359
27 | 0.00029447 | 7.3623e-05 | -0.00029447 | -7.3802e-05 | 1.6905e-09 | -1.7855e-07 | 0.0004417 | 0.00044176 | 0.00044176 | 0.99189 | -0.057142 | 0.99189 | -0.057183 | 0.16362
28 | -0.00108 | -0.0002666 | 0.0010804 | 0.00026334 | 4.3835e-07 | -3.2606e-06 | 0.0016229 | 0.0016217 | 0.0016229 | 0.98937 | -0.074964 | 0.98979 | -0.071909 | 0.60107
29 | -0.0038599 | -0.00095994 | 0.0038605 | 0.0009598 | 6.225e-07 | -1.4176e-07 | 0.0058003 | 0.0058001 | 0.0058003 | 0.98979 | -0.071909 | 0.98995 | -0.070726 | 2.1482

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20474 | 0.051203

## res_load
| p_mw | q_mvar
0 | 0.0343 | 0.0085964
1 | 0.010582 | 0.0026522
2 | 0.050207 | 0.012583
3 | 0.0040717 | 0.0010205
4 | 0.00059558 | 0.00014927
5 | 0.045181 | 0.011324
6 | 0.0073346 | 0.0018382
7 | 0.0059217 | 0.0014841
8 | 0.020426 | 0.0051193
9 | 0.013702 | 0.0034341
10 | 0.00068138 | 0.00017077
11 | 0.00017927 | 4.493e-05
12 | 0.00021887 | 5.4853e-05
13 | 0.0019261 | 0.00048274
14 | 0.00029447 | 7.3802e-05
15 | 0.0027795 | 0.0006966
16 | 0.0023483 | 0.00058854
17 | 0.0023559 | 0.00059044

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1