## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1132-5_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1132-5_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1132-5_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1132-5_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1132-5_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1132-5_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1132-5_0_5_node_22 | 0.4 | n |  | TRUE
7 | bus_LV_1132-5_0_5_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1132-5_0_5_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1132-5_0_5_node_47 | 0.4 | n |  | TRUE
10 | bus_LV_1132-5_0_5_node_48 | 0.4 | n |  | TRUE
11 | bus_LV_1132-5_0_5_node_40 | 0.4 | n |  | TRUE
12 | bus_LV_1132-5_0_5_node_46 | 0.4 | n |  | TRUE
13 | bus_LV_1132-5_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1132-5_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1132-5_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1132-5_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1132-5_0_5_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1132-5_0_5_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_1132-5_0_5_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_1132-5_0_5_node_105 | 0.4 | n |  | TRUE
21 | bus_LV_1132-5_0_5_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_1132-5_0_5_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_1132-5_0_5_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1132-5_0_5_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_1132-5_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_1132-5_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1132-5_0_5_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1132-5_0_5_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_1132-5_0_5_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1132-5_0_5_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_1132-5_0_5_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_1132-5_0_5_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1132-5_0_5_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_1132-5_0_5_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_1132-5_0_5_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1132-5_0_5_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_1132-5_0_5_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_1132-5_0_5_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_1132-5_0_5_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_1132-5_0_5_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_1132-5_0_5_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_1132-5_0_5_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_1132-5_0_5_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_1132-5_0_5_node_33 | 0.4 | n |  | TRUE
45 | bus_LV_1132-5_0_5_node_104 | 0.4 | n |  | TRUE
46 | bus_LV_1132-5_0_5_node_44 | 0.4 | n |  | TRUE
47 | bus_LV_1132-5_0_5_node_108 | 0.4 | n |  | TRUE
48 | bus_LV_1132-5_0_5_node_43 | 0.4 | n |  | TRUE
49 | bus_LV_1132-5_0_5_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_1132-5_0_5_node_51 | 0.4 | n |  | TRUE
51 | bus_LV_1132-5_0_5_node_83 | 0.4 | n |  | TRUE
52 | bus_LV_1132-5_0_5_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_1132-5_0_5_node_73 | 0.4 | n |  | TRUE
54 | bus_LV_1132-5_0_5_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_1132-5_0_5_node_81 | 0.4 | n |  | TRUE
56 | bus_LV_1132-5_0_5_node_72 | 0.4 | n |  | TRUE
57 | bus_LV_1132-5_0_5_node_52 | 0.4 | n |  | TRUE
58 | bus_LV_1132-5_0_5_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_1132-5_0_5_node_54 | 0.4 | n |  | TRUE
60 | bus_LV_1132-5_0_5_node_55 | 0.4 | n |  | TRUE
61 | bus_LV_1132-5_0_5_node_56 | 0.4 | n |  | TRUE
62 | bus_LV_1132-5_0_5_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_1132-5_0_5_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_1132-5_0_5_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_1132-5_0_5_node_60 | 0.4 | n |  | TRUE
66 | bus_LV_1132-5_0_5_node_93 | 0.4 | n |  | TRUE
67 | bus_LV_1132-5_0_5_node_89 | 0.4 | n |  | TRUE
68 | bus_LV_1132-5_0_5_node_94 | 0.4 | n |  | TRUE
69 | bus_LV_1132-5_0_5_node_91 | 0.4 | n |  | TRUE
70 | bus_LV_1132-5_0_5_node_90 | 0.4 | n |  | TRUE
71 | bus_LV_1132-5_0_5_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_1132-5_0_5_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_1132-5_0_5_node_63 | 0.4 | n |  | TRUE
74 | bus_LV_1132-5_0_5_node_64 | 0.4 | n |  | TRUE
75 | bus_LV_1132-5_0_5_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_1132-5_0_5_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_1132-5_0_5_node_106 | 0.4 | n |  | TRUE
78 | bus_LV_1132-5_0_5_node_78 | 0.4 | n |  | TRUE
79 | bus_LV_1132-5_0_5_node_86 | 0.4 | n |  | TRUE
80 | bus_LV_1132-5_0_5_node_107 | 0.4 | n |  | TRUE
81 | bus_LV_1132-5_0_5_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_1132-5_0_5_node_88 | 0.4 | n |  | TRUE
83 | bus_LV_1132-5_0_5_node_84 | 0.4 | n |  | TRUE
84 | bus_LV_1132-5_0_5_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_1132-5_0_5_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_1132-5_0_5_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_1132-5_0_5_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_1132-5_0_5_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_1132-5_0_5_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_1132-5_0_5_node_79 | 0.4 | n |  | TRUE
91 | bus_LV_1132-5_0_5_node_74 | 0.4 | n |  | TRUE
92 | bus_LV_1132-5_0_5_node_80 | 0.4 | n |  | TRUE
93 | bus_LV_1132-5_0_5_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_1132-5_0_5_node_92 | 0.4 | n |  | TRUE
95 | bus_LV_1132-5_0_5_node_82 | 0.4 | n |  | TRUE
96 | bus_LV_1132-5_0_5_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_1132-5_0_5_node_87 | 0.4 | n |  | TRUE
98 | bus_LV_1132-5_0_5_node_103 | 0.4 | n |  | TRUE
99 | bus_LV_1132-5_0_5_node_95 | 0.4 | n |  | TRUE
100 | bus_LV_1132-5_0_5_node_96 | 0.4 | n |  | TRUE
101 | bus_LV_1132-5_0_5_node_100 | 0.4 | n |  | TRUE
102 | bus_LV_1132-5_0_5_node_99 | 0.4 | n |  | TRUE
103 | bus_LV_1132-5_0_5_node_102 | 0.4 | n |  | TRUE
104 | bus_LV_1132-5_0_5_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_1132-5_0_5_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_1132-5_0_5_node_101 | 0.4 | n |  | TRUE
107 | bus_MV_128_0_node_298 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1132-5_0_5_load_0 | 0 | 0.00032931 | 8.2534e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1132-5_0_5_load_1 | 1 | 0.0011556 | 0.00028962 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1132-5_0_5_load_3 | 3 | 0.00035342 | 8.8575e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1132-5_0_5_load_4 | 4 | 0.00030334 | 7.6024e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1132-5_0_5_load_5 | 5 | 0.000847 | 0.00021228 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1132-5_0_5_load_28 | 7 | 0.0021971 | 0.00055064 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1132-5_0_5_load_18 | 8 | 0.0035714 | 0.00089509 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1132-5_0_5_load_46 | 12 | 0.002969 | 0.00074411 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1132-5_0_5_load_6 | 13 | 0.001955 | 0.00048997 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1132-5_0_5_load_7 | 14 | 0.0003571 | 8.9498e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1132-5_0_5_load_8 | 15 | 0.00063718 | 0.00015969 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1132-5_0_5_load_105 | 20 | 0.00053426 | 0.0001339 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1132-5_0_5_load_32 | 22 | 0.00014714 | 3.6877e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1132-5_0_5_load_12 | 23 | 0.00025502 | 6.3913e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1132-5_0_5_load_15 | 26 | 0.00058384 | 0.00014632 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1132-5_0_5_load_16 | 27 | 0.00030796 | 7.7182e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1132-5_0_5_load_17 | 28 | 0.00020773 | 5.2063e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1132-5_0_5_load_34 | 30 | 0.00019788 | 4.9593e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1132-5_0_5_load_23 | 31 | 0.0012454 | 0.00031213 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1132-5_0_5_load_24 | 34 | 0.0011701 | 0.00029325 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1132-5_0_5_load_36 | 38 | 0.0017972 | 0.00045042 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1132-5_0_5_load_27 | 39 | 0.0013865 | 0.00034748 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1132-5_0_5_load_38 | 41 | 0.00021042 | 5.2737e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1132-5_0_5_load_45 | 42 | 0.00018117 | 4.5405e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1132-5_0_5_load_37 | 43 | 0.00027554 | 6.9058e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1132-5_0_5_load_33 | 44 | 0.0011669 | 0.00029246 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1132-5_0_5_load_104 | 45 | 0.00044465 | 0.00011144 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1132-5_0_5_load_108 | 47 | 0.00206 | 0.00051627 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1132-5_0_5_load_43 | 48 | 0.0029473 | 0.00073867 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1132-5_0_5_load_42 | 49 | 0.0038764 | 0.00097153 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1132-5_0_5_load_51 | 50 | 0.0016865 | 0.00042267 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1132-5_0_5_load_73 | 53 | 0.0024718 | 0.0006195 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1132-5_0_5_load_50 | 54 | 0.0022432 | 0.0005622 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1132-5_0_5_load_81 | 55 | 0.0037984 | 0.00095197 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1132-5_0_5_load_72 | 56 | 0.0013296 | 0.00033323 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1132-5_0_5_load_52 | 57 | 0.0016948 | 0.00042477 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1132-5_0_5_load_53 | 58 | 0.0018485 | 0.00046328 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1132-5_0_5_load_54 | 59 | 0.0027818 | 0.00069718 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1132-5_0_5_load_55 | 60 | 0.0016746 | 0.00041969 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1132-5_0_5_load_56 | 61 | 0.0030808 | 0.00077213 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1132-5_0_5_load_57 | 62 | 0.0027456 | 0.00068812 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1132-5_0_5_load_60 | 65 | 0.0021017 | 0.00052674 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1132-5_0_5_load_89 | 67 | 0.002472 | 0.00061955 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1132-5_0_5_load_94 | 68 | 0.0023801 | 0.0005965 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1132-5_0_5_load_91 | 69 | 0.0039109 | 0.00098016 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1132-5_0_5_load_90 | 70 | 0.0015904 | 0.00039858 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1132-5_0_5_load_61 | 71 | 0.0012784 | 0.0003204 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1132-5_0_5_load_62 | 72 | 0.0012795 | 0.00032066 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1132-5_0_5_load_64 | 74 | 0.0012797 | 0.00032073 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1132-5_0_5_load_65 | 75 | 0.0038223 | 0.00095796 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1132-5_0_5_load_66 | 76 | 0.0020221 | 0.00050678 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1132-5_0_5_load_106 | 77 | 0.001279 | 0.00032055 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1132-5_0_5_load_78 | 78 | 0.0052365 | 0.0013124 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1132-5_0_5_load_107 | 80 | 0.0019285 | 0.00048333 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1132-5_0_5_load_77 | 81 | 0.0025292 | 0.00063387 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1132-5_0_5_load_88 | 82 | 0.0020093 | 0.00050357 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1132-5_0_5_load_84 | 83 | 0.0029794 | 0.0007467 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1132-5_0_5_load_67 | 84 | 0.0033776 | 0.0008465 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1132-5_0_5_load_68 | 85 | 0.0023093 | 0.00057876 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1132-5_0_5_load_69 | 86 | 0.0016183 | 0.00040558 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1132-5_0_5_load_71 | 88 | 0.003344 | 0.00083809 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1132-5_0_5_load_76 | 89 | 0.0030961 | 0.00077595 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1132-5_0_5_load_79 | 90 | 0.002675 | 0.00067041 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1132-5_0_5_load_80 | 92 | 0.0036207 | 0.00090744 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1132-5_0_5_load_75 | 93 | 0.00123 | 0.00030826 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1132-5_0_5_load_92 | 94 | 0.002355 | 0.00059023 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1132-5_0_5_load_82 | 95 | 0.0051114 | 0.001281 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1132-5_0_5_load_85 | 96 | 0.0042764 | 0.0010718 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1132-5_0_5_load_103 | 98 | 0.0035381 | 0.00088674 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1132-5_0_5_load_95 | 99 | 0.001833 | 0.00045939 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1132-5_0_5_load_96 | 100 | 0.0027372 | 0.00068602 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1132-5_0_5_load_100 | 101 | 0.0018845 | 0.0004723 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1132-5_0_5_load_99 | 102 | 0.002664 | 0.00066766 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1132-5_0_5_load_102 | 103 | 0.0038383 | 0.00096198 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1132-5_0_5_load_97 | 104 | 0.0018226 | 0.00045679 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1132-5_0_5_load_98 | 105 | 0.0026876 | 0.00067358 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1132-5_0_5_load_101 | 106 | 0.002906 | 0.00072832 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1132-5_0_5_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0043501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1132-5_0_5_line_1 | NAYY 4x150 SE | 0 | 2 | 0.034018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1132-5_0_5_line_2 | NAYY 4x150 SE | 1 | 3 | 0.042599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1132-5_0_5_line_3 | NAYY 4x150 SE | 2 | 4 | 0.015014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1132-5_0_5_line_4 | NAYY 4x150 SE | 2 | 5 | 0.017297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1132-5_0_5_line_5 | NAYY 4x150 SE | 4 | 13 | 0.32567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1132-5_0_5_line_6 | NAYY 4x150 SE | 5 | 8 | 0.017194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1132-5_0_5_line_7 | NAYY 4x150 SE | 6 | 7 | 0.17266 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1132-5_0_5_line_8 | NAYY 4x150 SE | 6 | 8 | 0.22313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1132-5_0_5_line_9 | NAYY 4x150 SE | 7 | 39 | 0.023633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1132-5_0_5_line_10 | NAYY 4x150 SE | 9 | 10 | 0.049923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
11 | LV_1132-5_0_5_line_11 | NAYY 4x150 SE | 9 | 11 | 0.5941 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1132-5_0_5_line_12 | NAYY 4x150 SE | 9 | 12 | 0.050493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1132-5_0_5_line_13 | NAYY 4x150 SE | 10 | 50 | 0.062915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1132-5_0_5_line_14 | NAYY 4x150 SE | 10 | 51 | 0.037062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1132-5_0_5_line_15 | NAYY 4x150 SE | 11 | 42 | 0.10819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1132-5_0_5_line_16 | NAYY 4x150 SE | 11 | 40 | 0.004042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1132-5_0_5_line_17 | NAYY 4x150 SE | 14 | 15 | 0.001837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1132-5_0_5_line_18 | NAYY 4x150 SE | 15 | 16 | 0.053456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1132-5_0_5_line_19 | NAYY 4x150 SE | 16 | 17 | 0.2906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1132-5_0_5_line_20 | NAYY 4x150 SE | 17 | 18 | 0.27521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1132-5_0_5_line_21 | NAYY 4x150 SE | 18 | 22 | 0.0094383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1132-5_0_5_line_22 | NAYY 4x150 SE | 18 | 21 | 0.024069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1132-5_0_5_line_23 | NAYY 4x150 SE | 19 | 20 | 0.058222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
24 | LV_1132-5_0_5_line_24 | NAYY 4x150 SE | 19 | 21 | 0.013396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
25 | LV_1132-5_0_5_line_25 | NAYY 4x150 SE | 20 | 35 | 0.12695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
26 | LV_1132-5_0_5_line_26 | NAYY 4x150 SE | 21 | 39 | 0.012318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1132-5_0_5_line_27 | NAYY 4x150 SE | 22 | 44 | 0.022028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1132-5_0_5_line_28 | NAYY 4x150 SE | 23 | 24 | 0.17105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1132-5_0_5_line_29 | NAYY 4x150 SE | 23 | 25 | 0.24446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1132-5_0_5_line_30 | NAYY 4x150 SE | 24 | 26 | 0.1928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1132-5_0_5_line_31 | NAYY 4x150 SE | 25 | 27 | 0.068444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1132-5_0_5_line_32 | NAYY 4x150 SE | 25 | 28 | 0.11563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1132-5_0_5_line_33 | NAYY 4x150 SE | 27 | 29 | 0.086002 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1132-5_0_5_line_34 | NAYY 4x150 SE | 28 | 30 | 0.016837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1132-5_0_5_line_35 | NAYY 4x150 SE | 29 | 31 | 0.12928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1132-5_0_5_line_36 | NAYY 4x150 SE | 31 | 34 | 0.066852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1132-5_0_5_line_37 | NAYY 4x150 SE | 32 | 33 | 0.29675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1132-5_0_5_line_38 | NAYY 4x150 SE | 32 | 34 | 0.20556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1132-5_0_5_line_39 | NAYY 4x150 SE | 33 | 36 | 0.011248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1132-5_0_5_line_40 | NAYY 4x150 SE | 33 | 37 | 0.35697 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1132-5_0_5_line_41 | NAYY 4x150 SE | 33 | 38 | 0.015032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1132-5_0_5_line_42 | NAYY 4x150 SE | 33 | 35 | 0.29285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_1132-5_0_5_line_43 | NAYY 4x150 SE | 36 | 45 | 0.19875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1132-5_0_5_line_44 | NAYY 4x150 SE | 37 | 46 | 0.066275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1132-5_0_5_line_45 | NAYY 4x150 SE | 37 | 47 | 0.029629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1132-5_0_5_line_46 | NAYY 4x150 SE | 38 | 43 | 0.026976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
47 | LV_1132-5_0_5_line_47 | NAYY 4x150 SE | 40 | 41 | 0.2513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_1132-5_0_5_line_48 | NAYY 4x150 SE | 41 | 43 | 0.021338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
49 | LV_1132-5_0_5_line_49 | NAYY 4x150 SE | 46 | 48 | 0.0069785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1132-5_0_5_line_50 | NAYY 4x150 SE | 48 | 49 | 0.029223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1132-5_0_5_line_51 | NAYY 4x150 SE | 50 | 54 | 0.015113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1132-5_0_5_line_52 | NAYY 4x150 SE | 51 | 55 | 0.041666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1132-5_0_5_line_53 | NAYY 4x150 SE | 51 | 52 | 0.079092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1132-5_0_5_line_54 | NAYY 4x150 SE | 52 | 53 | 0.092166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
55 | LV_1132-5_0_5_line_55 | NAYY 4x150 SE | 53 | 56 | 0.0044275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
56 | LV_1132-5_0_5_line_56 | NAYY 4x150 SE | 54 | 57 | 0.014791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1132-5_0_5_line_57 | NAYY 4x150 SE | 55 | 95 | 0.042469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1132-5_0_5_line_58 | NAYY 4x150 SE | 56 | 91 | 0.01149 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
59 | LV_1132-5_0_5_line_59 | NAYY 4x150 SE | 57 | 58 | 0.0085455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1132-5_0_5_line_60 | NAYY 4x150 SE | 58 | 59 | 0.0050384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1132-5_0_5_line_61 | NAYY 4x150 SE | 59 | 60 | 0.01105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1132-5_0_5_line_62 | NAYY 4x150 SE | 61 | 62 | 0.035694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1132-5_0_5_line_63 | NAYY 4x150 SE | 61 | 63 | 0.056316 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1132-5_0_5_line_64 | NAYY 4x150 SE | 62 | 64 | 0.0042854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1132-5_0_5_line_65 | NAYY 4x150 SE | 63 | 65 | 0.089264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1132-5_0_5_line_66 | NAYY 4x150 SE | 64 | 66 | 0.030496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1132-5_0_5_line_67 | NAYY 4x150 SE | 65 | 67 | 0.0015609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1132-5_0_5_line_68 | NAYY 4x150 SE | 66 | 68 | 0.019072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1132-5_0_5_line_69 | NAYY 4x150 SE | 66 | 69 | 0.016313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1132-5_0_5_line_70 | NAYY 4x150 SE | 67 | 70 | 0.020484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1132-5_0_5_line_71 | NAYY 4x150 SE | 68 | 103 | 0.017176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1132-5_0_5_line_72 | NAYY 4x150 SE | 69 | 94 | 0.024148 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1132-5_0_5_line_73 | NAYY 4x150 SE | 70 | 101 | 0.020643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1132-5_0_5_line_74 | NAYY 4x150 SE | 71 | 72 | 0.0042418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1132-5_0_5_line_75 | NAYY 4x150 SE | 71 | 73 | 0.015199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1132-5_0_5_line_76 | NAYY 4x150 SE | 72 | 74 | 0.0053458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1132-5_0_5_line_77 | NAYY 4x150 SE | 73 | 75 | 0.0037069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1132-5_0_5_line_78 | NAYY 4x150 SE | 73 | 76 | 0.01528 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1132-5_0_5_line_79 | NAYY 4x150 SE | 74 | 77 | 0.0068415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1132-5_0_5_line_80 | NAYY 4x150 SE | 75 | 78 | 0.016352 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1132-5_0_5_line_81 | NAYY 4x150 SE | 76 | 79 | 0.010625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1132-5_0_5_line_82 | NAYY 4x150 SE | 77 | 80 | 0.01372 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1132-5_0_5_line_83 | NAYY 4x150 SE | 78 | 81 | 0.020024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
84 | LV_1132-5_0_5_line_84 | NAYY 4x150 SE | 79 | 82 | 0.010669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1132-5_0_5_line_85 | NAYY 4x150 SE | 79 | 83 | 0.027907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1132-5_0_5_line_86 | NAYY 4x150 SE | 81 | 88 | 0.0080728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
87 | LV_1132-5_0_5_line_87 | NAYY 4x150 SE | 82 | 99 | 0.022196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1132-5_0_5_line_88 | NAYY 4x150 SE | 83 | 96 | 0.026935 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1132-5_0_5_line_89 | NAYY 4x150 SE | 84 | 85 | 0.023599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
90 | LV_1132-5_0_5_line_90 | NAYY 4x150 SE | 84 | 86 | 0.017361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
91 | LV_1132-5_0_5_line_91 | NAYY 4x150 SE | 85 | 87 | 0.0086484 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
92 | LV_1132-5_0_5_line_92 | NAYY 4x150 SE | 86 | 88 | 0.0078564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
93 | LV_1132-5_0_5_line_93 | NAYY 4x150 SE | 87 | 89 | 0.022723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
94 | LV_1132-5_0_5_line_94 | NAYY 4x150 SE | 87 | 90 | 0.017196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1132-5_0_5_line_95 | NAYY 4x150 SE | 89 | 91 | 0.021249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
96 | LV_1132-5_0_5_line_96 | NAYY 4x150 SE | 90 | 92 | 0.006263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1132-5_0_5_line_97 | NAYY 4x150 SE | 91 | 93 | 0.032567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1132-5_0_5_line_98 | NAYY 4x150 SE | 93 | 94 | 0.024619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1132-5_0_5_line_99 | NAYY 4x150 SE | 96 | 97 | 0.090386 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1132-5_0_5_line_100 | NAYY 4x150 SE | 97 | 98 | 0.062007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1132-5_0_5_line_101 | NAYY 4x150 SE | 99 | 100 | 0.002098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1132-5_0_5_line_102 | NAYY 4x150 SE | 100 | 104 | 0.012448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1132-5_0_5_line_103 | NAYY 4x150 SE | 101 | 102 | 0.019471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1132-5_0_5_line_104 | NAYY 4x150 SE | 104 | 105 | 0.012244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1132-5_0_5_line_105 | NAYY 4x150 SE | 105 | 106 | 0.0040893 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1132-5_0_5_trafo_47 | 0.25 MVA 20/0.4 kV | 107 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30
0 | 2640205.7349 | 1216288.3944 | 2640207.2229 | 1216284.3068
1 | 2640200.5755 | 1216321.9984 | 2640205.3889 | 1216289.345 | 2640205.7349 | 1216288.3944
2 | 2640244.501 | 1216275.7783 | 2640228.9158 | 1216272.6493 | 2640220.767 | 1216273.0057 | 2640214.4404 | 1216275.5979 | 2640208.7074 | 1216280.2287 | 2640207.2229 | 1216284.3068
3 | 2640200.5755 | 1216321.9984 | 2640212.1038 | 1216319.2412 | 2640215.2457 | 1216318.9024
4 | 2640200.5755 | 1216321.9984 | 2640184.6824 | 1216325.7936 | 2640183.7258 | 1216325.7872
5 | 2640510.7585 | 1216408.1916 | 2640501.087 | 1216405.8468 | 2640492.9804 | 1216401.1223 | 2640459.1611 | 1216372.6761 | 2640410.3221 | 1216337.8358 | 2640383.3441 | 1216322.6331 | 2640361.5247 | 1216313.5912 | 2640339.1571 | 1216308.159 | 2640321.6545 | 1216307.4291 | 2640215.2457 | 1216318.9024
6 | 2640183.7258 | 1216325.7872 | 2640175.5191 | 1216325.7319 | 2640166.9544 | 1216323.0082
7 | 2639945.737 | 1216293.8703 | 2639938.1748 | 1216295.0648 | 2639926.1515 | 1216295.7959 | 2639850.473 | 1216285.5506 | 2639836.2346 | 1216282.6094 | 2639820.9896 | 1216278.0494 | 2639790.1393 | 1216262.6123 | 2639779.0221 | 1216259.1455
8 | 2639945.737 | 1216293.8703 | 2640166.9544 | 1216323.0082
9 | 2639755.5967 | 1216261.5979 | 2639769.1126 | 1216259.7927 | 2639778.1534 | 1216258.8746 | 2639779.0221 | 1216259.1455
10 | 2639252.4755 | 1214998.2441 | 2639256.1143 | 1215003.7935 | 2639256.9602 | 1215005.6446 | 2639257.8252 | 1215009.219 | 2639259.1478 | 1215018.2552 | 2639260.9429 | 1215046.6392
11 | 2639260.9429 | 1215046.6392 | 2639652.925 | 1215493.0809
12 | 2639260.9429 | 1215046.6392 | 2639258.1359 | 1215039.3164 | 2639253.9677 | 1215033.43 | 2639249.8495 | 1215030.3233 | 2639228.7133 | 1215022.6688 | 2639221.1679 | 1215020.6938
13 | 2639252.4755 | 1214998.2441 | 2639251.0131 | 1215000.0577 | 2639250.0454 | 1215000.5628 | 2639246.5716 | 1215001.0736 | 2639203.0799 | 1214996.7741 | 2639195.4806 | 1214996.4462 | 2639190.8078 | 1214996.4533
14 | 2639252.4755 | 1214998.2441 | 2639253.0213 | 1214996.0686 | 2639252.5742 | 1214993.6198 | 2639251.2306 | 1214991.2429 | 2639249.1125 | 1214989.9949 | 2639246.9561 | 1214989.9696 | 2639241.7041 | 1214991.8251 | 2639237.2651 | 1214992.474 | 2639235.3544 | 1214992.0279 | 2639233.6836 | 1214990.894 | 2639232.1018 | 1214987.7818 | 2639232.0776 | 1214985.6804 | 2639233.3943 | 1214982.9208 | 2639235.5196 | 1214981.9119
15 | 2639652.925 | 1215493.0809 | 2639648.0639 | 1215496.7285 | 2639645.1269 | 1215499.922 | 2639644.137 | 1215506.0412 | 2639645.1208 | 1215511.1174 | 2639661.726 | 1215545.5145 | 2639673.6325 | 1215572.8319 | 2639676.9232 | 1215587.24 | 2639677.3492 | 1215590.8415
16 | 2639656.1682 | 1215490.6566 | 2639652.925 | 1215493.0809
17 | 2639921.2729 | 1216659.3325 | 2639921.2729 | 1216659.3325 | 2639921.6221 | 1216661.136
18 | 2639902.0001 | 1216611.3087 | 2639906.7732 | 1216616.1546 | 2639912.8753 | 1216624.3447 | 2639915.3678 | 1216629.6645 | 2639919.3729 | 1216639.2302 | 2639920.5271 | 1216649.3884 | 2639921.2729 | 1216659.3325
19 | 2639759.2937 | 1216548.1856 | 2639763.1213 | 1216545.7096 | 2639769.641 | 1216561.907 | 2639779.5339 | 1216586.8321 | 2639785.0783 | 1216602.3893 | 2639788.102 | 1216612.3042 | 2639790.0125 | 1216619.5212 | 2639791.647 | 1216627.1477 | 2639793.5732 | 1216638.8341 | 2639795.2704 | 1216654.1322 | 2639796.2475 | 1216665.8344 | 2639797.3873 | 1216691.8351 | 2639806.2016 | 1216689.5037 | 2639808.7591 | 1216688.4979 | 2639811.609 | 1216686.916 | 2639814.336 | 1216684.3994 | 2639815.4296 | 1216683.1949 | 2639819.1208 | 1216678.4056 | 2639834.0974 | 1216657.0708 | 2639845.3966 | 1216647.574 | 2639884.4693 | 1216624.0101 | 2639902.0001 | 1216611.3087
20 | 2639747.3446 | 1216286.1631 | 2639745.1773 | 1216291.2517 | 2639740.37 | 1216298.3015 | 2639729.7808 | 1216311.6945 | 2639729.4142 | 1216363.3112 | 2639729.0703 | 1216424.0335 | 2639729.6152 | 1216433.4204 | 2639730.5628 | 1216442.7433 | 2639732.491 | 1216456.442 | 2639734.5336 | 1216466.6394 | 2639736.9178 | 1216475.705 | 2639739.9993 | 1216486.0761 | 2639745.1301 | 1216501.0746 | 2639763.1213 | 1216545.7096 | 2639759.2937 | 1216548.1856
21 | 2639747.3446 | 1216286.1631 | 2639752.2903 | 1216290.2429 | 2639754.4478 | 1216292.366
22 | 2639743.3334 | 1216262.6226 | 2639747.7269 | 1216281.2072 | 2639747.3446 | 1216286.1631
23 | 2639730.1545 | 1216260.1667 | 2639730.8745 | 1216243.2727 | 2639732.1099 | 1216225.3481 | 2639734.0592 | 1216207.4173 | 2639734.6782 | 1216202.1446
24 | 2639743.3334 | 1216262.6226 | 2639738.8927 | 1216261.37 | 2639730.1545 | 1216260.1667
25 | 2639749.4815 | 1216076.0651 | 2639734.6782 | 1216202.1446
26 | 2639743.3334 | 1216262.6226 | 2639750.2444 | 1216262.3129 | 2639755.5967 | 1216261.5979
27 | 2639757.89 | 1216313.5161 | 2639757.9095 | 1216300.3418 | 2639757.2845 | 1216297.2914 | 2639756.3805 | 1216295.0841 | 2639755.1112 | 1216293.0189 | 2639754.4478 | 1216292.366
28 | 2640083.0024 | 1215861.3702 | 2640076.0069 | 1215849.3273 | 2640073.5433 | 1215843.0737 | 2640071.4168 | 1215832.9869 | 2640070.7897 | 1215822.3542 | 2640071.0879 | 1215814.1403 | 2640074.8182 | 1215800.2461 | 2640092.0619 | 1215752.734 | 2640094.6771 | 1215743.2238 | 2640097.3286 | 1215723.7858 | 2640098.5917 | 1215712.0985 | 2640098.5421 | 1215704.7939 | 2640098.0123 | 1215700.0209 | 2640097.0669 | 1215697.2242
29 | 2639922.7051 | 1215585.7562 | 2639927.0484 | 1215590.2879 | 2639932.7996 | 1215594.3288 | 2639940.7036 | 1215598.9177 | 2639945.0367 | 1215602.6934 | 2639947.9674 | 1215606.1261 | 2639950.4928 | 1215610.0008 | 2639952.6328 | 1215614.7179 | 2639964.1364 | 1215646.4135 | 2639971.0706 | 1215662.0025 | 2639978.8645 | 1215676.2074 | 2639982.2075 | 1215681.5552 | 2639984.7235 | 1215684.5405 | 2639988.3242 | 1215687.6887 | 2639997.9254 | 1215693.9233 | 2640006.8491 | 1215698.1523 | 2640013.6987 | 1215700.2995 | 2640020.3212 | 1215701.2111 | 2640027.2365 | 1215701.4799 | 2640033.9976 | 1215700.9694 | 2640040.7478 | 1215699.8251 | 2640045.1013 | 1215698.2868 | 2640051.2506 | 1215696.1712 | 2640074.5755 | 1215686.0886 | 2640078.8403 | 1215685.3168 | 2640082.7193 | 1215685.4651 | 2640087.1763 | 1215686.6069 | 2640090.8517 | 1215688.7995 | 2640093.8386 | 1215691.7546 | 2640096.4265 | 1215695.3297 | 2640097.0669 | 1215697.2242
30 | 2640083.0024 | 1215861.3702 | 2640092.8251 | 1215857.1893 | 2640097.3484 | 1215854.0957 | 2640100.7398 | 1215849.9605 | 2640103.5908 | 1215844.8878 | 2640106.218 | 1215836.9563 | 2640113.0795 | 1215798.9246 | 2640115.607 | 1215792.2933 | 2640118.3617 | 1215786.8641 | 2640128.4504 | 1215771.3896 | 2640154.4882 | 1215742.9036 | 2640171.2683 | 1215731.6544 | 2640178.2146 | 1215728.4437 | 2640197.7078 | 1215726.9852 | 2640198.5225 | 1215727.0813
31 | 2639922.7051 | 1215585.7562 | 2639913.9096 | 1215578.2263 | 2639904.6635 | 1215568.8145 | 2639890.5993 | 1215552.0551 | 2639877.3649 | 1215534.7411
32 | 2639922.7051 | 1215585.7562 | 2639933.1856 | 1215588.8504 | 2639956.4207 | 1215600.1236 | 2639961.3464 | 1215603.8588 | 2639965.3369 | 1215607.7656 | 2639967.932 | 1215611.4184 | 2639970.5249 | 1215616.5388 | 2639983.1987 | 1215639.0258 | 2639991.5494 | 1215650.5996 | 2639998.4081 | 1215658.1834 | 2640004.378 | 1215660.9426
33 | 2639830.3901 | 1215462.7672 | 2639840.0408 | 1215477.5737 | 2639867.9723 | 1215522.4532 | 2639877.3649 | 1215534.7411
34 | 2640020.1863 | 1215665.8673 | 2640011.6362 | 1215664.7982 | 2640005.145 | 1215661.297 | 2640004.378 | 1215660.9426
35 | 2639830.3901 | 1215462.7672 | 2639834.9558 | 1215485.1775 | 2639862.0168 | 1215581.8927 | 2639862.6913 | 1215587.7673 | 2639862.6494 | 1215587.8225
36 | 2639851.9779 | 1215640.5588 | 2639849.3725 | 1215637.8632 | 2639841.0038 | 1215624.3995 | 2639839.2249 | 1215613.3478 | 2639841.502 | 1215605.5251 | 2639845.6799 | 1215600.7168 | 2639852.4265 | 1215595.57 | 2639860.1327 | 1215591.1411 | 2639862.6494 | 1215587.8225
37 | 2639726.602 | 1215789.3668 | 2639729.254 | 1215798.1785 | 2639732.6947 | 1215808.2518 | 2639738.008 | 1215823.3182 | 2639743.2861 | 1215819.729 | 2639745.2751 | 1215817.4965 | 2639747.5574 | 1215813.3982 | 2639749.9414 | 1215806.5879 | 2639751.3639 | 1215805.052 | 2639753.6015 | 1215804.2442 | 2639756.1234 | 1215804.0943 | 2639761.3245 | 1215804.0733 | 2639808.4497 | 1215806.8336 | 2639861.0082 | 1215805.4948 | 2639890.5175 | 1215808.3381 | 2639907.6309 | 1215808.4415 | 2639955.9328 | 1215803.2839 | 2639967.3393 | 1215802.9601 | 2639970.2875 | 1215782.2455
38 | 2639970.2875 | 1215782.2455 | 2639965.119 | 1215756.985 | 2639950.0482 | 1215701.2958 | 2639942.0846 | 1215685.222 | 2639929.1919 | 1215672.7395 | 2639915.754 | 1215663.4219 | 2639901.1187 | 1215659.4328 | 2639884.718 | 1215658.278 | 2639873.0202 | 1215655.5649 | 2639860.4801 | 1215649.3553 | 2639851.9779 | 1215640.5588
39 | 2639726.602 | 1215789.3668 | 2639724.0083 | 1215800.3115
40 | 2639544.8911 | 1215903.8936 | 2639558.826 | 1215921.852 | 2639576.8343 | 1215939.2261 | 2639599.1325 | 1215955.4169 | 2639612.1015 | 1215964.4305 | 2639624.9122 | 1215967.5618 | 2639647.5035 | 1215969.3351 | 2639657.5034 | 1215966.9668 | 2639667.5174 | 1215961.3523 | 2639674.0775 | 1215954.4919 | 2639680.3392 | 1215945.684 | 2639686.1221 | 1215933.5375 | 2639693.4094 | 1215925.7926 | 2639702.8229 | 1215919.1513 | 2639714.692 | 1215910.9032 | 2639721.6635 | 1215903.8455 | 2639723.9586 | 1215895.5448 | 2639723.9105 | 1215885.672 | 2639718.8065 | 1215857.4215 | 2639707.9863 | 1215816.4588 | 2639707.4425 | 1215806.9162 | 2639708.8054 | 1215799.4987 | 2639712.8196 | 1215794.1556 | 2639718.4323 | 1215791.6359 | 2639722.3797 | 1215790.6172 | 2639726.602 | 1215789.3668
41 | 2639726.602 | 1215789.3668 | 2639724.3571 | 1215781.0025 | 2639723.0854 | 1215774.759
42 | 2639726.602 | 1215789.3668 | 2639729.254 | 1215798.1785 | 2639732.6947 | 1215808.2518 | 2639738.008 | 1215823.3182 | 2639745.5169 | 1215845.0143 | 2639753.3038 | 1215870.5478 | 2639756.4821 | 1215883.5432 | 2639758.791 | 1215894.8208 | 2639761.295 | 1215909.8574 | 2639763.1273 | 1215927.7023 | 2639763.7779 | 1215939.4469 | 2639764.0077 | 1215948.2536 | 2639763.8598 | 1215957.9027 | 2639763.5343 | 1215966.8724 | 2639761.8481 | 1215984.0491 | 2639758.7181 | 1216008.2424 | 2639749.4815 | 1216076.0651
43 | 2639724.0083 | 1215800.3115 | 2639724.0712 | 1215802.2686 | 2639724.9772 | 1215807.6 | 2639729.6689 | 1215821.3726 | 2639732.4332 | 1215828.1283 | 2639737.6224 | 1215837.8797 | 2639741.5092 | 1215845.9548 | 2639747.6592 | 1215865.3404 | 2639752.4239 | 1215882.9492 | 2639756.2304 | 1215903.0752 | 2639758.6277 | 1215922.725 | 2639759.736 | 1215939.8424 | 2639759.6763 | 1215962.4664 | 2639758.0656 | 1215983.1233 | 2639756.5357 | 1215993.1753
44 | 2639501.484 | 1215908.4754 | 2639507.3128 | 1215920.2876 | 2639512.3709 | 1215925.8021 | 2639519.8849 | 1215928.4979 | 2639528.0167 | 1215927.34 | 2639535.5721 | 1215921.5088 | 2639539.5004 | 1215915.3424 | 2639544.8911 | 1215903.8936
45 | 2639532.8541 | 1215876.8091 | 2639544.8911 | 1215903.8936
46 | 2639723.0854 | 1215774.759 | 2639722.9014 | 1215773.8553 | 2639721.6392 | 1215764.9972 | 2639720.4941 | 1215753.3939 | 2639720.0451 | 1215747.9656
47 | 2639656.1682 | 1215490.6566 | 2639695.6764 | 1215555.5462 | 2639703.9034 | 1215569.8204 | 2639707.3714 | 1215576.9587 | 2639710.2122 | 1215583.6593 | 2639712.2333 | 1215590.2989 | 2639713.2097 | 1215595.3195 | 2639713.9207 | 1215602.5729 | 2639714.3597 | 1215613.0486 | 2639714.2747 | 1215628.0902 | 2639714.0295 | 1215648.9452 | 2639714.0149 | 1215663.6871 | 2639714.7159 | 1215681.5689 | 2639718.3205 | 1215726.6977
48 | 2639720.0451 | 1215747.9656 | 2639719.5806 | 1215742.348 | 2639719.2294 | 1215738.0765 | 2639718.3205 | 1215726.6977
49 | 2639501.484 | 1215908.4754 | 2639500.5123 | 1215901.565 | 2639500.5123 | 1215901.565
50 | 2639488.6399 | 1215874.9067 | 2639490.3578 | 1215880.263 | 2639500.5123 | 1215901.565
51 | 2639175.6952 | 1214996.476 | 2639190.8078 | 1214996.4533
52 | 2639235.5196 | 1214981.9119 | 2639232.4022 | 1214979.0453 | 2639229.2802 | 1214976.8791 | 2639226.3343 | 1214975.6479 | 2639215.4093 | 1214972.9634 | 2639202.2268 | 1214970.5977 | 2639196.4486 | 1214970.1543
53 | 2639306.0437 | 1214959.9743 | 2639301.3048 | 1214966.9472 | 2639295.9351 | 1214975.1388 | 2639289.7528 | 1214976.4322 | 2639253.8611 | 1214980.3983 | 2639239.3901 | 1214981.1147 | 2639235.5196 | 1214981.9119
54 | 2639306.0437 | 1214959.9743 | 2639303.4203 | 1214959.3567 | 2639300.8009 | 1214958.1276 | 2639298.9408 | 1214956.9257 | 2639273.7143 | 1214934.958 | 2639265.9003 | 1214929.1809 | 2639258.7172 | 1214924.4643 | 2639253.0177 | 1214921.614 | 2639248.5489 | 1214919.8502 | 2639242.5836 | 1214918.1656 | 2639227.706 | 1214914.9261
55 | 2639223.3799 | 1214913.9841 | 2639227.706 | 1214914.9261
56 | 2639175.6952 | 1214996.476 | 2639160.9046 | 1214996.4983
57 | 2639196.4486 | 1214970.1543 | 2639186.3788 | 1214969.3818 | 2639179.1364 | 1214969.0674 | 2639170.9584 | 1214968.9803 | 2639163.1271 | 1214969.2957 | 2639156.4769 | 1214970.1415 | 2639154.1332 | 1214970.6624
58 | 2639212.1529 | 1214911.5395 | 2639223.3799 | 1214913.9841
59 | 2639152.3592 | 1214996.5112 | 2639160.9046 | 1214996.4983
60 | 2639147.3207 | 1214996.5188 | 2639152.3592 | 1214996.5112
61 | 2639136.2712 | 1214996.5355 | 2639147.3207 | 1214996.5188
62 | 2639132.0504 | 1214767.53 | 2639133.7022 | 1214770.0308 | 2639136.6315 | 1214774.964 | 2639139.5331 | 1214780.6419 | 2639147.5965 | 1214797.0711 | 2639148.6439 | 1214799.0981
63 | 2639107.9145 | 1214718.7875 | 2639108.2354 | 1214727.7615 | 2639108.2937 | 1214732.7648 | 2639108.8033 | 1214734.9583 | 2639109.9717 | 1214737.434 | 2639112.0091 | 1214740.5826 | 2639129.0853 | 1214763.0409 | 2639132.0504 | 1214767.53
64 | 2639150.6111 | 1214802.9054 | 2639148.6439 | 1214799.0981
65 | 2639107.9145 | 1214718.7875 | 2639058.195 | 1214767.5792 | 2639056.778 | 1214769.4377 | 2639055.9324 | 1214770.9998 | 2639055.45 | 1214772.7643 | 2639055.3989 | 1214774.7762 | 2639055.6889 | 1214776.8682 | 2639056.2115 | 1214778.2391 | 2639056.9322 | 1214779.5224 | 2639061.0627 | 1214784.6666
66 | 2639150.6111 | 1214802.9054 | 2639168.1259 | 1214827.9015
67 | 2639061.0627 | 1214784.6666 | 2639062.04 | 1214785.8837
68 | 2639168.1259 | 1214827.9015 | 2639152.8355 | 1214839.3012
69 | 2639168.1259 | 1214827.9015 | 2639177.9516 | 1214840.9238
70 | 2639062.04 | 1214785.8837 | 2639074.865 | 1214801.8561
71 | 2639137.6245 | 1214845.8341 | 2639141.9069 | 1214845.9289 | 2639144.4868 | 1214845.0898 | 2639146.5444 | 1214843.9916 | 2639152.8355 | 1214839.3012
72 | 2639177.9516 | 1214840.9238 | 2639192.496 | 1214860.1998
73 | 2639087.7893 | 1214817.9523 | 2639074.865 | 1214801.8561
74 | 2639072.9431 | 1214846.043 | 2639072.5233 | 1214844.3734 | 2639071.5893 | 1214842.0326 | 2639071.5893 | 1214842.0326
75 | 2639075.9842 | 1214860.8946 | 2639075.819 | 1214858.292 | 2639075.5503 | 1214856.4113 | 2639072.9431 | 1214846.043
76 | 2639068.6066 | 1214837.6075 | 2639070.3277 | 1214839.8786 | 2639071.5893 | 1214842.0326
77 | 2639075.9842 | 1214860.8946 | 2639079.5968 | 1214861.7253
78 | 2639075.9842 | 1214860.8946 | 2639072.199 | 1214860.2472 | 2639069.9372 | 1214860.0767 | 2639067.8941 | 1214860.1189 | 2639066.0846 | 1214860.4406 | 2639064.2353 | 1214861.0511 | 2639062.8099 | 1214861.8645 | 2639061.456 | 1214862.8955
79 | 2639064.4746 | 1214832.1547 | 2639068.6066 | 1214837.6075
80 | 2639079.5968 | 1214861.7253 | 2639081.9062 | 1214862.2564 | 2639085.875 | 1214863.85 | 2639089.0963 | 1214865.9389 | 2639092.8867 | 1214869.2546 | 2639093.4909 | 1214869.8241
81 | 2639056.6601 | 1214872.0969 | 2639057.1874 | 1214869.2764 | 2639058.3961 | 1214866.7718 | 2639059.7008 | 1214864.668 | 2639061.1309 | 1214863.1431 | 2639061.456 | 1214862.8955
82 | 2639056.1883 | 1214821.2196 | 2639064.4746 | 1214832.1547
83 | 2639108.0617 | 1214883.5588 | 2639093.4909 | 1214869.8241
84 | 2639056.6601 | 1214872.0969 | 2639054.3555 | 1214871.4925 | 2639052.1736 | 1214870.7111 | 2639050.1986 | 1214869.6309 | 2639048.2882 | 1214867.973 | 2639047.5418 | 1214867.0488
85 | 2639056.6601 | 1214872.0969 | 2639056.692 | 1214874.1872 | 2639057.1161 | 1214876.6803 | 2639063.5538 | 1214899.0601
86 | 2639108.0617 | 1214883.5588 | 2639111.8305 | 1214887.1114 | 2639114.1952 | 1214888.7789
87 | 2639047.5418 | 1214867.0488 | 2639033.5959 | 1214849.7815
88 | 2639063.5538 | 1214899.0601 | 2639067.7857 | 1214913.7718 | 2639069.206 | 1214920.6962 | 2639069.6686 | 1214925.2304
89 | 2639136.9805 | 1214898.9526 | 2639144.2237 | 1214900.2203 | 2639160.2479 | 1214902.8938
90 | 2639136.9805 | 1214898.9526 | 2639134.5222 | 1214898.5223 | 2639129.6178 | 1214897.1783 | 2639124.1267 | 1214894.9632 | 2639120.76 | 1214893.0777
91 | 2639168.7783 | 1214904.3171 | 2639160.2479 | 1214902.8938
92 | 2639120.76 | 1214893.0777 | 2639118.4824 | 1214891.8021 | 2639114.1952 | 1214888.7789
93 | 2639168.7783 | 1214904.3171 | 2639191.1922 | 1214908.0493
94 | 2639168.7783 | 1214904.3171 | 2639168.5099 | 1214913.9765 | 2639168.6425 | 1214921.5081
95 | 2639212.1529 | 1214911.5395 | 2639191.1922 | 1214908.0493
96 | 2639168.6425 | 1214921.5081 | 2639168.7528 | 1214927.7701
97 | 2639212.1529 | 1214911.5395 | 2639213.211 | 1214905.3762 | 2639213.6695 | 1214901.4658 | 2639213.3779 | 1214897.317 | 2639212.3192 | 1214893.1632 | 2639209.518 | 1214887.2524 | 2639205.8882 | 1214880.8156
98 | 2639192.496 | 1214860.1998 | 2639197.3287 | 1214866.6047 | 2639202.3193 | 1214874.4866 | 2639205.8882 | 1214880.8156
99 | 2638997.2698 | 1214969.3542 | 2639014.8412 | 1214964.8219 | 2639028.106 | 1214960.4283 | 2639037.7594 | 1214956.7004 | 2639046.7617 | 1214952.668 | 2639052.539 | 1214949.4373 | 2639058.7108 | 1214945.1085 | 2639062.5061 | 1214941.887 | 2639065.6934 | 1214938.7282 | 2639067.8479 | 1214935.5849 | 2639068.6888 | 1214933.567 | 2639069.2889 | 1214931.214 | 2639069.5533 | 1214929.1145 | 2639069.7055 | 1214925.5912 | 2639069.6686 | 1214925.2304
100 | 2638997.2698 | 1214969.3542 | 2638996.8419 | 1214963.9593 | 2638996.835 | 1214961.5356 | 2638997.3934 | 1214959.7494 | 2638998.9452 | 1214958.1808 | 2639001.5082 | 1214956.4187 | 2639028.5823 | 1214946.8235 | 2639033.421 | 1214944.287 | 2639044.6035 | 1214937.823
101 | 2639032.2777 | 1214848.1493 | 2639033.5959 | 1214849.7815
102 | 2639032.2777 | 1214848.1493 | 2639024.4566 | 1214838.4654
103 | 2639099.9797 | 1214833.1344 | 2639087.7893 | 1214817.9523
104 | 2639016.7634 | 1214828.94 | 2639024.4566 | 1214838.4654
105 | 2639014.1941 | 1214825.7587 | 2639016.7634 | 1214828.94

## bus_geodata
| x | y | coords
0 | 2640205.7349 | 1216288.3944
1 | 2640207.2229 | 1216284.3068
2 | 2640200.5755 | 1216321.9984
3 | 2640244.501 | 1216275.7783
4 | 2640215.2457 | 1216318.9024
5 | 2640183.7258 | 1216325.7872
6 | 2639945.737 | 1216293.8703
7 | 2639779.0221 | 1216259.1455
8 | 2640166.9544 | 1216323.0082
9 | 2639260.9429 | 1215046.6392
10 | 2639252.4755 | 1214998.2441
11 | 2639652.925 | 1215493.0809
12 | 2639221.1679 | 1215020.6938
13 | 2640510.7585 | 1216408.1916
14 | 2639921.6221 | 1216661.136
15 | 2639921.2729 | 1216659.3325
16 | 2639902.0001 | 1216611.3087
17 | 2639759.2937 | 1216548.1856
18 | 2639747.3446 | 1216286.1631
19 | 2639730.1545 | 1216260.1667
20 | 2639734.6782 | 1216202.1446
21 | 2639743.3334 | 1216262.6226
22 | 2639754.4478 | 1216292.366
23 | 2640097.0669 | 1215697.2242
24 | 2640083.0024 | 1215861.3702
25 | 2639922.7051 | 1215585.7562
26 | 2640198.5225 | 1215727.0813
27 | 2639877.3649 | 1215534.7411
28 | 2640004.378 | 1215660.9426
29 | 2639830.3901 | 1215462.7672
30 | 2640020.1863 | 1215665.8673
31 | 2639862.6494 | 1215587.8225
32 | 2639970.2875 | 1215782.2455
33 | 2639726.602 | 1215789.3668
34 | 2639851.9779 | 1215640.5588
35 | 2639749.4815 | 1216076.0651
36 | 2639724.0083 | 1215800.3115
37 | 2639544.8911 | 1215903.8936
38 | 2639723.0854 | 1215774.759
39 | 2639755.5967 | 1216261.5979
40 | 2639656.1682 | 1215490.6566
41 | 2639718.3205 | 1215726.6977
42 | 2639677.3492 | 1215590.8415
43 | 2639720.0451 | 1215747.9656
44 | 2639757.89 | 1216313.5161
45 | 2639756.5357 | 1215993.1753
46 | 2639501.484 | 1215908.4754
47 | 2639532.8541 | 1215876.8091
48 | 2639500.5123 | 1215901.565
49 | 2639488.6399 | 1215874.9067
50 | 2639190.8078 | 1214996.4533
51 | 2639235.5196 | 1214981.9119
52 | 2639306.0437 | 1214959.9743
53 | 2639227.706 | 1214914.9261
54 | 2639175.6952 | 1214996.476
55 | 2639196.4486 | 1214970.1543
56 | 2639223.3799 | 1214913.9841
57 | 2639160.9046 | 1214996.4983
58 | 2639152.3592 | 1214996.5112
59 | 2639147.3207 | 1214996.5188
60 | 2639136.2712 | 1214996.5355
61 | 2639132.0504 | 1214767.53
62 | 2639148.6439 | 1214799.0981
63 | 2639107.9145 | 1214718.7875
64 | 2639150.6111 | 1214802.9054
65 | 2639061.0627 | 1214784.6666
66 | 2639168.1259 | 1214827.9015
67 | 2639062.04 | 1214785.8837
68 | 2639152.8355 | 1214839.3012
69 | 2639177.9516 | 1214840.9238
70 | 2639074.865 | 1214801.8561
71 | 2639072.9431 | 1214846.043
72 | 2639071.5893 | 1214842.0326
73 | 2639075.9842 | 1214860.8946
74 | 2639068.6066 | 1214837.6075
75 | 2639079.5968 | 1214861.7253
76 | 2639061.456 | 1214862.8955
77 | 2639064.4746 | 1214832.1547
78 | 2639093.4909 | 1214869.8241
79 | 2639056.6601 | 1214872.0969
80 | 2639056.1883 | 1214821.2196
81 | 2639108.0617 | 1214883.5588
82 | 2639047.5418 | 1214867.0488
83 | 2639063.5538 | 1214899.0601
84 | 2639136.9805 | 1214898.9526
85 | 2639160.2479 | 1214902.8938
86 | 2639120.76 | 1214893.0777
87 | 2639168.7783 | 1214904.3171
88 | 2639114.1952 | 1214888.7789
89 | 2639191.1922 | 1214908.0493
90 | 2639168.6425 | 1214921.5081
91 | 2639212.1529 | 1214911.5395
92 | 2639168.7528 | 1214927.7701
93 | 2639205.8882 | 1214880.8156
94 | 2639192.496 | 1214860.1998
95 | 2639154.1332 | 1214970.6624
96 | 2639069.6686 | 1214925.2304
97 | 2638997.2698 | 1214969.3542
98 | 2639044.6035 | 1214937.823
99 | 2639033.5959 | 1214849.7815
100 | 2639032.2777 | 1214848.1493
101 | 2639087.7893 | 1214817.9523
102 | 2639099.9797 | 1214833.1344
103 | 2639137.6245 | 1214845.8341
104 | 2639024.4566 | 1214838.4654
105 | 2639016.7634 | 1214828.94
106 | 2639014.1941 | 1214825.7587
107 | 2639252.4755 | 1214998.2441

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97115 | -0.2061 | 0.00032931 | 8.2534e-05
1 | 0.97114 | -0.20617 | 0.0011556 | 0.00028962
2 | 0.97125 | -0.20544 | 0 | 0
3 | 0.97112 | -0.20633 | 0.00035342 | 8.8575e-05
4 | 0.9712 | -0.2058 | 0.00030334 | 7.6024e-05
5 | 0.97135 | -0.20468 | 0.000847 | 0.00021228
6 | 0.97287 | -0.19367 | 0 | 0
7 | 0.97395 | -0.18584 | 0.0021971 | 0.00055064
8 | 0.97147 | -0.20378 | 0.0035714 | 0.00089509
9 | 1 | 0 | -0.15838 | -0.039854
10 | 0.99562 | -0.030163 | 0 | 0
11 | 0.98666 | -0.094109 | 0 | 0
12 | 0.99979 | -0.0014978 | 0.002969 | 0.00074411
13 | 0.97026 | -0.2126 | 0.001955 | 0.00048997
14 | 0.97326 | -0.19098 | 0.0003571 | 8.9498e-05
15 | 0.97326 | -0.19097 | 0.00063718 | 0.00015969
16 | 0.97334 | -0.19041 | 0 | 0
17 | 0.97376 | -0.18731 | 0 | 0
18 | 0.97416 | -0.1843 | 0 | 0
19 | 0.97438 | -0.18267 | 0 | 0
20 | 0.975 | -0.17821 | 0.00053426 | 0.0001339
21 | 0.97424 | -0.1837 | 0 | 0
22 | 0.97414 | -0.18443 | 0.00014714 | 3.6877e-05
23 | 0.9755 | -0.17529 | 0.00025502 | 6.3913e-05
24 | 0.97536 | -0.17639 | 0 | 0
25 | 0.9758 | -0.17303 | 0 | 0
26 | 0.97519 | -0.17759 | 0.00058384 | 0.00014632
27 | 0.97593 | -0.17208 | 0.00030796 | 7.7182e-05
28 | 0.97573 | -0.17353 | 0.00020773 | 5.2063e-05
29 | 0.97612 | -0.17061 | 0 | 0
30 | 0.97573 | -0.17356 | 0.00019788 | 4.9593e-05
31 | 0.97641 | -0.16839 | 0.0012454 | 0.00031213
32 | 0.97787 | -0.1576 | 0 | 0
33 | 0.97959 | -0.14492 | 0 | 0
34 | 0.97669 | -0.16636 | 0.0011701 | 0.00029325
35 | 0.97639 | -0.16812 | 0 | 0
36 | 0.97958 | -0.14497 | 0 | 0
37 | 0.97495 | -0.17816 | 0 | 0
38 | 0.9799 | -0.14267 | 0.0017972 | 0.00045042
39 | 0.97413 | -0.18449 | 0.0013865 | 0.00034748
40 | 0.98657 | -0.094753 | 0 | 0
41 | 0.98097 | -0.13498 | 0.00021042 | 5.2737e-05
42 | 0.98664 | -0.094315 | 0.00018117 | 4.5405e-05
43 | 0.98049 | -0.13839 | 0.00027554 | 6.9058e-05
44 | 0.9741 | -0.1847 | 0.0011669 | 0.00029246
45 | 0.97946 | -0.14591 | 0.00044465 | 0.00011144
46 | 0.97429 | -0.18292 | 0 | 0
47 | 0.97486 | -0.1788 | 0.00206 | 0.00051627
48 | 0.97422 | -0.18342 | 0.0029473 | 0.00073867
49 | 0.97406 | -0.18461 | 0.0038764 | 0.00097153
50 | 0.99454 | -0.037733 | 0.0016865 | 0.00042267
51 | 0.99268 | -0.050484 | 0 | 0
52 | 0.98691 | -0.090637 | 0 | 0
53 | 0.9802 | -0.13801 | 0.0024718 | 0.0006195
54 | 0.99432 | -0.039296 | 0.0022432 | 0.0005622
55 | 0.99214 | -0.054249 | 0.0037984 | 0.00095197
56 | 0.97988 | -0.14025 | 0.0013296 | 0.00033323
57 | 0.99415 | -0.040491 | 0.0016948 | 0.00042477
58 | 0.99407 | -0.041035 | 0.0018485 | 0.00046328
59 | 0.99404 | -0.041262 | 0.0027818 | 0.00069718
60 | 0.99401 | -0.041449 | 0.0016746 | 0.00041969
61 | 0.97354 | -0.18563 | 0.0030808 | 0.00077213
62 | 0.97426 | -0.18045 | 0.0027456 | 0.00068812
63 | 0.97265 | -0.192 | 0 | 0
64 | 0.97436 | -0.1797 | 0 | 0
65 | 0.97125 | -0.20211 | 0.0021017 | 0.00052674
66 | 0.9751 | -0.17439 | 0 | 0
67 | 0.97123 | -0.20226 | 0.002472 | 0.00061955
68 | 0.97493 | -0.17564 | 0.0023801 | 0.0005965
69 | 0.97565 | -0.17049 | 0.0039109 | 0.00098016
70 | 0.97104 | -0.20359 | 0.0015904 | 0.00039858
71 | 0.97267 | -0.19184 | 0.0012784 | 0.0003204
72 | 0.97263 | -0.1921 | 0.0012795 | 0.00032066
73 | 0.97283 | -0.19071 | 0 | 0
74 | 0.9726 | -0.19235 | 0.0012797 | 0.00032073
75 | 0.97301 | -0.18939 | 0.0038223 | 0.00095796
76 | 0.97223 | -0.19504 | 0.0020221 | 0.00050678
77 | 0.97257 | -0.19259 | 0.001279 | 0.00032055
78 | 0.97391 | -0.18289 | 0.0052365 | 0.0013124
79 | 0.97184 | -0.19783 | 0 | 0
80 | 0.97253 | -0.19287 | 0.0019285 | 0.00048333
81 | 0.97454 | -0.17837 | 0.0025292 | 0.00063387
82 | 0.97162 | -0.1994 | 0.0020093 | 0.00050357
83 | 0.9714 | -0.20102 | 0.0029794 | 0.0007467
84 | 0.97574 | -0.16984 | 0.0033776 | 0.0008465
85 | 0.97667 | -0.16318 | 0.0023093 | 0.00057876
86 | 0.97509 | -0.17443 | 0.0016183 | 0.00040558
87 | 0.97702 | -0.16064 | 0 | 0
88 | 0.97481 | -0.17644 | 0.003344 | 0.00083809
89 | 0.97806 | -0.15323 | 0.0030961 | 0.00077595
90 | 0.97686 | -0.16178 | 0.002675 | 0.00067041
91 | 0.97908 | -0.14598 | 0 | 0
92 | 0.97683 | -0.16201 | 0.0036207 | 0.00090744
93 | 0.97764 | -0.15626 | 0.00123 | 0.00030826
94 | 0.97659 | -0.16374 | 0.002355 | 0.00059023
95 | 0.99183 | -0.056451 | 0.0051114 | 0.001281
96 | 0.97109 | -0.20325 | 0.0042764 | 0.0010718
97 | 0.97062 | -0.20664 | 0 | 0
98 | 0.9703 | -0.20897 | 0.0035381 | 0.00088674
99 | 0.97123 | -0.20222 | 0.001833 | 0.00045939
100 | 0.9712 | -0.20244 | 0.0027372 | 0.00068602
101 | 0.97091 | -0.20458 | 0.0018845 | 0.0004723
102 | 0.97083 | -0.20513 | 0.002664 | 0.00066766
103 | 0.97483 | -0.17633 | 0.0038383 | 0.00096198
104 | 0.97106 | -0.20342 | 0.0018226 | 0.00045679
105 | 0.97096 | -0.20415 | 0.0026876 | 0.00067358
106 | 0.97094 | -0.20427 | 0.002906 | 0.00072832
107 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.001509 | 0.00037762 | -0.001509 | -0.00037767 | 1.4509e-08 | -4.8244e-08 | 0.002312 | 0.002312 | 0.002312 | 0.97115 | -0.2061 | 0.97114 | -0.20617 | 0.85629
1 | -0.0018383 | -0.00046016 | 0.0018385 | 0.0004598 | 1.6838e-07 | -3.5619e-07 | 0.0028165 | 0.0028164 | 0.0028165 | 0.97115 | -0.2061 | 0.97125 | -0.20544 | 1.0432
2 | 0.00035343 | 8.8051e-05 | -0.00035342 | -8.8575e-05 | 7.7926e-09 | -5.2408e-07 | 0.00054134 | 0.00054153 | 0.00054153 | 0.97114 | -0.20617 | 0.97112 | -0.20633 | 0.20057
3 | 0.0022603 | 0.00056253 | -0.0022602 | -0.00056267 | 1.1225e-07 | -1.4262e-07 | 0.0034615 | 0.0034616 | 0.0034616 | 0.97125 | -0.20544 | 0.9712 | -0.2058 | 1.2821
4 | -0.0040988 | -0.0010223 | 0.0040992 | 0.0010223 | 4.2537e-07 | -5.0476e-08 | 0.0062779 | 0.0062778 | 0.0062779 | 0.97125 | -0.20544 | 0.97135 | -0.20468 | 2.3251
5 | 0.0019568 | 0.00048665 | -0.001955 | -0.00048997 | 1.8259e-06 | -3.3238e-06 | 0.0029968 | 0.0029983 | 0.0029983 | 0.9712 | -0.2058 | 0.97026 | -0.2126 | 1.1105
6 | -0.0049462 | -0.0012346 | 0.0049468 | 0.0012346 | 6.157e-07 | 2.3942e-08 | 0.0075753 | 0.0075752 | 0.0075753 | 0.97135 | -0.20468 | 0.97147 | -0.20378 | 2.8057
7 | -0.0085301 | -0.0021287 | 0.0085393 | 0.0021279 | 9.1644e-06 | -7.6793e-07 | 0.013044 | 0.013042 | 0.013044 | 0.97287 | -0.19367 | 0.97395 | -0.18584 | 2.4155
8 | 0.0085301 | 0.0021287 | -0.0085183 | -0.0021297 | 1.1846e-05 | -9.7706e-07 | 0.013044 | 0.013046 | 0.013046 | 0.97287 | -0.19367 | 0.97147 | -0.20378 | 2.4159
9 | -0.010736 | -0.0026786 | 0.010738 | 0.0026787 | 1.9829e-06 | 1.7433e-07 | 0.016399 | 0.016399 | 0.016399 | 0.97395 | -0.18584 | 0.97413 | -0.18449 | 3.0368
10 | 0.12312 | 0.031202 | -0.1226 | -0.031002 | 0.00052351 | 0.00020005 | 0.18333 | 0.18333 | 0.18333 | 1 | 0 | 0.99562 | -0.030163 | 33.9503
11 | 0.031491 | 0.0079075 | -0.031084 | -0.0077663 | 0.00040715 | 0.00014121 | 0.046864 | 0.04687 | 0.04687 | 1 | 0 | 0.98666 | -0.094109 | 8.6796
12 | 0.0029697 | 0.00074369 | -0.002969 | -0.00074411 | 6.1521e-07 | -4.2567e-07 | 0.0044187 | 0.0044189 | 0.0044189 | 1 | 0 | 0.99979 | -0.0014978 | 1.6366
13 | 0.011946 | 0.0029947 | -0.011934 | -0.0029907 | 1.2515e-05 | 3.9963e-06 | 0.017855 | 0.017855 | 0.017855 | 0.99562 | -0.030163 | 0.99454 | -0.037733 | 6.6129
14 | 0.11065 | 0.028008 | -0.11034 | -0.027887 | 0.00031664 | 0.00012082 | 0.16548 | 0.16548 | 0.16548 | 0.99562 | -0.030163 | 0.99268 | -0.050484 | 30.644
15 | 0.00018117 | 4.4026e-05 | -0.00018117 | -4.5405e-05 | 5.031e-09 | -1.3797e-06 | 0.00027275 | 0.00027323 | 0.00027323 | 0.98666 | -0.094109 | 0.98664 | -0.094315 | 0.1012
16 | 0.030903 | 0.0077223 | -0.0309 | -0.0077213 | 2.7382e-06 | 9.4993e-07 | 0.046597 | 0.046597 | 0.046597 | 0.98666 | -0.094109 | 0.98657 | -0.094753 | 8.6291
17 | -0.0003571 | -8.9498e-05 | 0.0003571 | 8.9475e-05 | 3.4172e-10 | -2.2697e-08 | 0.00054597 | 0.00054597 | 0.00054597 | 0.97326 | -0.19098 | 0.97326 | -0.19097 | 0.20221
18 | -0.00099428 | -0.00024917 | 0.00099436 | 0.00024853 | 7.707e-08 | -6.3471e-07 | 0.0015201 | 0.0015199 | 0.0015201 | 0.97326 | -0.19097 | 0.97334 | -0.19041 | 0.56302
19 | -0.00099436 | -0.00024853 | 0.00099478 | 0.00024508 | 4.1855e-07 | -3.4525e-06 | 0.0015199 | 0.0015186 | 0.0015199 | 0.97334 | -0.19041 | 0.97376 | -0.18731 | 0.56293
20 | -0.00099478 | -0.00024508 | 0.00099517 | 0.00024181 | 3.9574e-07 | -3.2728e-06 | 0.0015186 | 0.0015174 | 0.0015186 | 0.97376 | -0.18731 | 0.97416 | -0.1843 | 0.56245
21 | 0.0013142 | 0.00032897 | -0.0013141 | -0.00032908 | 2.3729e-08 | -1.0838e-07 | 0.0020072 | 0.0020073 | 0.0020073 | 0.97416 | -0.1843 | 0.97414 | -0.18443 | 0.74343
22 | -0.0023093 | -0.00057078 | 0.0023095 | 0.00057055 | 1.8657e-07 | -2.2793e-07 | 0.0035246 | 0.0035245 | 0.0035246 | 0.97416 | -0.1843 | 0.97424 | -0.1837 | 1.3054
23 | -0.014438 | -0.0035974 | 0.014446 | 0.0035994 | 8.8244e-06 | 1.9427e-06 | 0.022041 | 0.02204 | 0.022041 | 0.97438 | -0.18267 | 0.975 | -0.17821 | 4.0816
24 | 0.014438 | 0.0035974 | -0.014436 | -0.003597 | 2.0304e-06 | 4.4726e-07 | 0.022041 | 0.022041 | 0.022041 | 0.97438 | -0.18267 | 0.97424 | -0.1837 | 4.0816
25 | -0.014981 | -0.0037333 | 0.015001 | 0.003738 | 2.0689e-05 | 4.7863e-06 | 0.022856 | 0.022854 | 0.022856 | 0.975 | -0.17821 | 0.97639 | -0.16812 | 4.2325
26 | 0.012126 | 0.0030264 | -0.012125 | -0.0030262 | 1.3177e-06 | 2.0006e-07 | 0.018516 | 0.018516 | 0.018516 | 0.97424 | -0.1837 | 0.97413 | -0.18449 | 3.429
27 | 0.001167 | 0.00029221 | -0.0011669 | -0.00029246 | 4.3676e-08 | -2.5743e-07 | 0.0017825 | 0.0017826 | 0.0017826 | 0.97414 | -0.18443 | 0.9741 | -0.1847 | 0.66022
28 | 0.00058402 | 0.00014185 | -0.00058394 | -0.00014396 | 8.4477e-08 | -2.1027e-06 | 0.00088925 | 0.00089001 | 0.00089001 | 0.9755 | -0.17529 | 0.97536 | -0.17639 | 0.32963
29 | -0.00083904 | -0.00020577 | 0.00083929 | 0.00020281 | 2.4904e-07 | -2.9571e-06 | 0.0012782 | 0.0012772 | 0.0012782 | 0.9755 | -0.17529 | 0.9758 | -0.17303 | 0.47342
30 | 0.00058394 | 0.00014396 | -0.00058384 | -0.00014632 | 9.5386e-08 | -2.3691e-06 | 0.00089001 | 0.00089086 | 0.00089086 | 0.97536 | -0.17639 | 0.97519 | -0.17759 | 0.32995
31 | -0.0012449 | -0.00030282 | 0.0012451 | 0.00030202 | 1.5337e-07 | -7.9612e-07 | 0.0018951 | 0.0018948 | 0.0018951 | 0.9758 | -0.17303 | 0.97593 | -0.17208 | 0.70191
32 | 0.00040564 | 0.00010001 | -0.00040561 | -0.00010145 | 2.7577e-08 | -1.4337e-06 | 0.00061798 | 0.00061849 | 0.00061849 | 0.9758 | -0.17303 | 0.97573 | -0.17353 | 0.22907
33 | -0.001553 | -0.00037921 | 0.0015533 | 0.00037825 | 2.9996e-07 | -9.5946e-07 | 0.0023644 | 0.002364 | 0.0023644 | 0.97593 | -0.17208 | 0.97612 | -0.17061 | 0.8757
34 | 0.00019788 | 4.9383e-05 | -0.00019788 | -4.9593e-05 | 9.5651e-10 | -2.0993e-07 | 0.00030169 | 0.00030177 | 0.00030177 | 0.97573 | -0.17353 | 0.97573 | -0.17356 | 0.11177
35 | -0.0015533 | -0.00037825 | 0.0015538 | 0.0003768 | 4.5073e-07 | -1.4432e-06 | 0.002364 | 0.0023634 | 0.002364 | 0.97612 | -0.17061 | 0.97641 | -0.16839 | 0.87556
36 | -0.0027992 | -0.00068893 | 0.0027999 | 0.00068838 | 7.5746e-07 | -5.4506e-07 | 0.0042614 | 0.0042611 | 0.0042614 | 0.97641 | -0.16839 | 0.97669 | -0.16636 | 1.5783
37 | -0.0039747 | -0.00098086 | 0.0039815 | 0.00097973 | 6.7603e-06 | -1.1293e-06 | 0.0060428 | 0.0060415 | 0.0060428 | 0.97787 | -0.1576 | 0.97959 | -0.14492 | 2.2381
38 | 0.0039747 | 0.00098086 | -0.00397 | -0.00098164 | 4.6845e-06 | -7.7389e-07 | 0.0060428 | 0.0060437 | 0.0060437 | 0.97787 | -0.1576 | 0.97669 | -0.16636 | 2.2384
39 | 0.00044471 | 0.00010882 | -0.00044471 | -0.00010896 | 3.1943e-09 | -1.4037e-07 | 0.00067459 | 0.00067464 | 0.00067464 | 0.97959 | -0.14492 | 0.97958 | -0.14497 | 0.24987
40 | 0.0089305 | 0.0022383 | -0.0088895 | -0.0022271 | 4.0996e-05 | 1.1295e-05 | 0.013566 | 0.013567 | 0.013567 | 0.97959 | -0.14492 | 0.97495 | -0.17816 | 5.0249
41 | -0.028406 | -0.0070759 | 0.028415 | 0.0070789 | 8.7257e-06 | 2.9774e-06 | 0.043134 | 0.043133 | 0.043134 | 0.97959 | -0.14492 | 0.9799 | -0.14267 | 7.9877
42 | 0.015049 | 0.003749 | -0.015001 | -0.003738 | 4.7719e-05 | 1.1004e-05 | 0.022852 | 0.022854 | 0.022854 | 0.97959 | -0.14492 | 0.97639 | -0.16812 | 4.2323
43 | 0.00044471 | 0.00010896 | -0.00044465 | -0.00011144 | 5.6519e-08 | -2.48e-06 | 0.00067464 | 0.00067553 | 0.00067553 | 0.97958 | -0.14497 | 0.97946 | -0.14591 | 0.2502
44 | 0.0068294 | 0.0017111 | -0.0068249 | -0.0017102 | 4.493e-06 | 9.0218e-07 | 0.010423 | 0.010423 | 0.010423 | 0.97495 | -0.17816 | 0.97429 | -0.18292 | 3.8605
45 | 0.0020601 | 0.00051598 | -0.00206 | -0.00051627 | 1.8278e-07 | -2.9915e-07 | 0.0031442 | 0.0031443 | 0.0031443 | 0.97495 | -0.17816 | 0.97486 | -0.1788 | 1.1646
46 | -0.030212 | -0.0075293 | 0.030229 | 0.0075355 | 1.7703e-05 | 6.1288e-06 | 0.045863 | 0.045862 | 0.045863 | 0.9799 | -0.14267 | 0.98049 | -0.13839 | 8.4931
47 | 0.0309 | 0.0077213 | -0.03073 | -0.0076622 | 0.00017025 | 5.9098e-05 | 0.046597 | 0.046599 | 0.046599 | 0.98657 | -0.094753 | 0.98097 | -0.13498 | 8.6295
48 | 0.030519 | 0.0076095 | -0.030505 | -0.0076045 | 1.4259e-05 | 4.9458e-06 | 0.04628 | 0.04628 | 0.04628 | 0.98097 | -0.13498 | 0.98049 | -0.13839 | 8.5704
49 | 0.0068249 | 0.0017102 | -0.0068244 | -0.0017101 | 4.7311e-07 | 9.5067e-08 | 0.010423 | 0.010423 | 0.010423 | 0.97429 | -0.18292 | 0.97422 | -0.18342 | 3.8605
50 | 0.0038771 | 0.00097141 | -0.0038764 | -0.00097153 | 6.3947e-07 | -1.1787e-07 | 0.0059217 | 0.0059218 | 0.0059218 | 0.97422 | -0.18342 | 0.97406 | -0.18461 | 2.1933
51 | 0.010247 | 0.002568 | -0.010245 | -0.0025674 | 2.2167e-06 | 6.565e-07 | 0.015332 | 0.015332 | 0.015332 | 0.99454 | -0.037733 | 0.99432 | -0.039296 | 5.6784
52 | 0.008916 | 0.0022343 | -0.0089113 | -0.0022331 | 4.6441e-06 | 1.2478e-06 | 0.013365 | 0.013365 | 0.013365 | 0.99268 | -0.050484 | 0.99214 | -0.054249 | 4.95
53 | 0.10142 | 0.025653 | -0.10085 | -0.025435 | 0.00057098 | 0.00021757 | 0.15211 | 0.15211 | 0.15211 | 0.99268 | -0.050484 | 0.98691 | -0.090637 | 28.1691
54 | 0.10085 | 0.025435 | -0.10018 | -0.025181 | 0.00066537 | 0.00025357 | 0.15211 | 0.15211 | 0.15211 | 0.98691 | -0.090637 | 0.9802 | -0.13801 | 28.1693
55 | 0.097713 | 0.024562 | -0.097682 | -0.02455 | 3.0406e-05 | 1.1583e-05 | 0.14836 | 0.14836 | 0.14836 | 0.9802 | -0.13801 | 0.97988 | -0.14025 | 27.4744
56 | 0.0080017 | 0.0020052 | -0.0080004 | -0.0020049 | 1.3234e-06 | 3.172e-07 | 0.011975 | 0.011975 | 0.011975 | 0.99432 | -0.039296 | 0.99415 | -0.040491 | 4.4351
57 | 0.0051129 | 0.0012811 | -0.0051114 | -0.001281 | 1.5584e-06 | 5.109e-08 | 0.0076683 | 0.0076685 | 0.0076685 | 0.99214 | -0.054249 | 0.99183 | -0.056451 | 2.8402
58 | 0.096353 | 0.024217 | -0.096276 | -0.024188 | 7.6775e-05 | 2.924e-05 | 0.14634 | 0.14634 | 0.14634 | 0.97988 | -0.14025 | 0.97908 | -0.14598 | 27.1005
59 | 0.0063056 | 0.0015801 | -0.0063051 | -0.00158 | 4.7498e-07 | 7.1891e-08 | 0.0094379 | 0.009438 | 0.009438 | 0.99415 | -0.040491 | 0.99407 | -0.041035 | 3.4955
60 | 0.0044566 | 0.0011167 | -0.0044564 | -0.0011167 | 1.3991e-07 | -1.1505e-08 | 0.0066709 | 0.006671 | 0.006671 | 0.99407 | -0.041035 | 0.99404 | -0.041262 | 2.4707
61 | 0.0016746 | 0.00041957 | -0.0016746 | -0.00041969 | 4.3329e-08 | -1.2657e-07 | 0.0025068 | 0.0025068 | 0.0025068 | 0.99404 | -0.041262 | 0.99401 | -0.041449 | 0.92846
62 | -0.01382 | -0.0034646 | 0.01383 | 0.003468 | 9.9383e-06 | 3.3783e-06 | 0.021124 | 0.021124 | 0.021124 | 0.97354 | -0.18563 | 0.97426 | -0.18045 | 7.8236
63 | 0.010739 | 0.0026925 | -0.01073 | -0.0026895 | 9.4688e-06 | 2.9422e-06 | 0.016415 | 0.016415 | 0.016415 | 0.97354 | -0.18563 | 0.97265 | -0.192 | 6.0796
64 | -0.016576 | -0.0041561 | 0.016577 | 0.0041567 | 1.714e-06 | 6.0585e-07 | 0.025317 | 0.025317 | 0.025317 | 0.97426 | -0.18045 | 0.97436 | -0.1797 | 9.3767
65 | 0.01073 | 0.0026895 | -0.010715 | -0.0026849 | 1.5009e-05 | 4.6665e-06 | 0.016415 | 0.016415 | 0.016415 | 0.97265 | -0.192 | 0.97125 | -0.20211 | 6.0798
66 | -0.016577 | -0.0041567 | 0.016589 | 0.004161 | 1.2197e-05 | 4.311e-06 | 0.025317 | 0.025317 | 0.025317 | 0.97436 | -0.1797 | 0.9751 | -0.17439 | 9.3767
67 | 0.008613 | 0.0021581 | -0.0086128 | -0.0021581 | 1.696e-07 | 4.5913e-08 | 0.013196 | 0.013196 | 0.013196 | 0.97125 | -0.20211 | 0.97123 | -0.20226 | 4.8872
68 | 0.0062199 | 0.0015586 | -0.0062188 | -0.0015584 | 1.0721e-06 | 1.745e-07 | 0.0094915 | 0.0094916 | 0.0094916 | 0.9751 | -0.17439 | 0.97493 | -0.17564 | 3.5154
69 | -0.022809 | -0.0057196 | 0.022822 | 0.0057241 | 1.2334e-05 | 4.5401e-06 | 0.034808 | 0.034808 | 0.034808 | 0.9751 | -0.17439 | 0.97565 | -0.17049 | 12.892
70 | 0.0061408 | 0.0015385 | -0.0061397 | -0.0015384 | 1.1314e-06 | 1.817e-07 | 0.0094081 | 0.0094082 | 0.0094082 | 0.97123 | -0.20226 | 0.97104 | -0.20359 | 3.4845
71 | 0.0038387 | 0.00096191 | -0.0038383 | -0.00096198 | 3.6791e-07 | -7.2654e-08 | 0.0058589 | 0.005859 | 0.005859 | 0.97493 | -0.17564 | 0.97483 | -0.17633 | 2.17
72 | -0.026733 | -0.0067043 | 0.026758 | 0.0067136 | 2.505e-05 | 9.3326e-06 | 0.040773 | 0.040773 | 0.040773 | 0.97565 | -0.17049 | 0.97659 | -0.16374 | 15.1011
73 | 0.0045493 | 0.0011398 | -0.0045487 | -0.0011398 | 6.2599e-07 | -1.4559e-08 | 0.0069712 | 0.0069713 | 0.0069713 | 0.97104 | -0.20359 | 0.97091 | -0.20458 | 2.582
74 | 0.0057673 | 0.0014451 | -0.0057671 | -0.0014451 | 2.0604e-07 | 2.6598e-08 | 0.0088228 | 0.0088228 | 0.0088228 | 0.97267 | -0.19184 | 0.97263 | -0.1921 | 3.2677
75 | -0.0070457 | -0.0017655 | 0.0070468 | 0.0017657 | 1.1018e-06 | 2.351e-07 | 0.010779 | 0.010778 | 0.010779 | 0.97267 | -0.19184 | 0.97283 | -0.19071 | 3.9921
76 | 0.0044876 | 0.0011244 | -0.0044874 | -0.0011244 | 1.5723e-07 | -5.8726e-09 | 0.0068654 | 0.0068654 | 0.0068654 | 0.97263 | -0.1921 | 0.9726 | -0.19235 | 2.5427
77 | -0.033904 | -0.0084992 | 0.03391 | 0.0085015 | 6.2208e-06 | 2.3466e-06 | 0.051859 | 0.051859 | 0.051859 | 0.97283 | -0.19071 | 0.97301 | -0.18939 | 19.2072
78 | 0.026857 | 0.0067334 | -0.026841 | -0.0067274 | 1.6091e-05 | 5.9994e-06 | 0.041081 | 0.041081 | 0.041081 | 0.97283 | -0.19071 | 0.97223 | -0.19504 | 15.2152
79 | 0.0032077 | 0.00080369 | -0.0032076 | -0.00080374 | 1.0282e-07 | -4.5357e-08 | 0.0049075 | 0.0049075 | 0.0049075 | 0.9726 | -0.19235 | 0.97257 | -0.19259 | 1.8176
80 | -0.037732 | -0.0094595 | 0.037766 | 0.0094723 | 3.3977e-05 | 1.2865e-05 | 0.057705 | 0.057705 | 0.057705 | 0.97301 | -0.18939 | 0.97391 | -0.18289 | 21.3721
81 | 0.024819 | 0.0062206 | -0.024809 | -0.0062171 | 9.5668e-06 | 3.5478e-06 | 0.037986 | 0.037986 | 0.037986 | 0.97223 | -0.19504 | 0.97184 | -0.19783 | 14.0689
82 | 0.0019286 | 0.00048319 | -0.0019285 | -0.00048333 | 7.4539e-08 | -1.4158e-07 | 0.0029507 | 0.0029507 | 0.0029507 | 0.97257 | -0.19259 | 0.97253 | -0.19287 | 1.0929
83 | -0.043003 | -0.010785 | 0.04303 | 0.010795 | 2.6971e-05 | 9.8749e-06 | 0.065705 | 0.065705 | 0.065705 | 0.97391 | -0.18289 | 0.97454 | -0.17837 | 12.1677
84 | 0.014005 | 0.0035106 | -0.014002 | -0.0035096 | 3.0614e-06 | 1.0453e-06 | 0.021444 | 0.021444 | 0.021444 | 0.97184 | -0.19783 | 0.97162 | -0.1994 | 7.9424
85 | 0.010804 | 0.0027065 | -0.010799 | -0.002705 | 4.765e-06 | 1.4871e-06 | 0.016542 | 0.016542 | 0.016542 | 0.97184 | -0.19783 | 0.9714 | -0.20102 | 6.1266
86 | -0.045559 | -0.011428 | 0.045571 | 0.011433 | 1.2189e-05 | 4.487e-06 | 0.069567 | 0.069567 | 0.069567 | 0.97454 | -0.17837 | 0.97481 | -0.17644 | 12.8828
87 | 0.011993 | 0.003006 | -0.011988 | -0.0030045 | 4.6725e-06 | 1.5223e-06 | 0.018367 | 0.018367 | 0.018367 | 0.97162 | -0.1994 | 0.97123 | -0.20222 | 6.8027
88 | 0.0078197 | 0.0019583 | -0.0078173 | -0.0019577 | 2.4114e-06 | 5.9412e-07 | 0.011978 | 0.011978 | 0.011978 | 0.9714 | -0.20102 | 0.97109 | -0.20325 | 4.4363
89 | -0.053957 | -0.01354 | 0.054007 | 0.013559 | 4.9861e-05 | 1.8587e-05 | 0.082292 | 0.082291 | 0.082292 | 0.97574 | -0.16984 | 0.97667 | -0.16318 | 15.2392
90 | 0.050579 | 0.012694 | -0.050547 | -0.012682 | 3.2232e-05 | 1.1964e-05 | 0.077141 | 0.077141 | 0.077141 | 0.97574 | -0.16984 | 0.97509 | -0.17443 | 14.2853
91 | -0.056316 | -0.014137 | 0.056336 | 0.014145 | 1.9868e-05 | 7.4251e-06 | 0.08581 | 0.08581 | 0.08581 | 0.97667 | -0.16318 | 0.97702 | -0.16064 | 15.8907
92 | 0.048929 | 0.012276 | -0.048915 | -0.012271 | 1.3667e-05 | 5.0608e-06 | 0.074671 | 0.074671 | 0.074671 | 0.97509 | -0.17443 | 0.97481 | -0.17644 | 13.828
93 | -0.062633 | -0.015723 | 0.062697 | 0.015747 | 6.4521e-05 | 2.4246e-05 | 0.0954 | 0.095399 | 0.0954 | 0.97702 | -0.16064 | 0.97806 | -0.15323 | 17.6666
94 | 0.0062968 | 0.001578 | -0.0062958 | -0.0015778 | 9.8686e-07 | 1.6425e-07 | 0.0095901 | 0.0095901 | 0.0095901 | 0.97702 | -0.16064 | 0.97686 | -0.16178 | 3.5519
95 | -0.065793 | -0.016523 | 0.06586 | 0.016548 | 6.6443e-05 | 2.5021e-05 | 0.10011 | 0.10011 | 0.10011 | 0.97806 | -0.15323 | 0.97908 | -0.14598 | 18.5389
96 | 0.0036208 | 0.00090741 | -0.0036207 | -0.00090744 | 1.1889e-07 | -3.268e-08 | 0.0055155 | 0.0055155 | 0.0055155 | 0.97686 | -0.16178 | 0.97683 | -0.16201 | 2.0428
97 | 0.030416 | 0.0076397 | -0.030373 | -0.0076235 | 4.3438e-05 | 1.6298e-05 | 0.046233 | 0.046233 | 0.046233 | 0.97908 | -0.14598 | 0.97764 | -0.15626 | 17.1234
98 | 0.029143 | 0.0073152 | -0.029113 | -0.0073039 | 3.0231e-05 | 1.1319e-05 | 0.044361 | 0.044361 | 0.044361 | 0.97764 | -0.15626 | 0.97659 | -0.16374 | 16.4301
99 | 0.0035409 | 0.00088593 | -0.0035393 | -0.00088641 | 1.6602e-06 | -4.7914e-07 | 0.0054253 | 0.0054257 | 0.0054257 | 0.97109 | -0.20325 | 0.97062 | -0.20664 | 2.0095
100 | 0.0035393 | 0.00088641 | -0.0035381 | -0.00088674 | 1.1391e-06 | -3.2802e-07 | 0.0054257 | 0.005426 | 0.005426 | 0.97062 | -0.20664 | 0.9703 | -0.20897 | 2.0096
101 | 0.010155 | 0.0025451 | -0.010155 | -0.002545 | 3.1693e-07 | 9.5933e-08 | 0.015559 | 0.015559 | 0.015559 | 0.97123 | -0.20222 | 0.9712 | -0.20244 | 5.7626
102 | 0.0074179 | 0.001859 | -0.0074169 | -0.0018587 | 1.0033e-06 | 2.3188e-07 | 0.011365 | 0.011365 | 0.011365 | 0.9712 | -0.20244 | 0.97106 | -0.20342 | 4.2094
103 | 0.0026642 | 0.0006675 | -0.002664 | -0.00066766 | 2.0256e-07 | -1.6287e-07 | 0.0040831 | 0.0040832 | 0.0040832 | 0.97091 | -0.20458 | 0.97083 | -0.20513 | 1.5123
104 | 0.0055943 | 0.0014019 | -0.0055937 | -0.0014019 | 5.6146e-07 | 6.449e-08 | 0.0085724 | 0.0085724 | 0.0085724 | 0.97106 | -0.20342 | 0.97096 | -0.20415 | 3.175
105 | 0.0029061 | 0.00072829 | -0.002906 | -0.00072832 | 5.0612e-08 | -3.1111e-08 | 0.0044536 | 0.0044536 | 0.0044536 | 0.97096 | -0.20415 | 0.97094 | -0.20427 | 1.6495

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.15838 | 0.039854

## res_load
| p_mw | q_mvar
0 | 0.00032931 | 8.2534e-05
1 | 0.0011556 | 0.00028962
2 | 0.00035342 | 8.8575e-05
3 | 0.00030334 | 7.6024e-05
4 | 0.000847 | 0.00021228
5 | 0.0021971 | 0.00055064
6 | 0.0035714 | 0.00089509
7 | 0.002969 | 0.00074411
8 | 0.001955 | 0.00048997
9 | 0.0003571 | 8.9498e-05
10 | 0.00063718 | 0.00015969
11 | 0.00053426 | 0.0001339
12 | 0.00014714 | 3.6877e-05
13 | 0.00025502 | 6.3913e-05
14 | 0.00058384 | 0.00014632
15 | 0.00030796 | 7.7182e-05
16 | 0.00020773 | 5.2063e-05
17 | 0.00019788 | 4.9593e-05
18 | 0.0012454 | 0.00031213
19 | 0.0011701 | 0.00029325
20 | 0.0017972 | 0.00045042
21 | 0.0013865 | 0.00034748
22 | 0.00021042 | 5.2737e-05
23 | 0.00018117 | 4.5405e-05
24 | 0.00027554 | 6.9058e-05
25 | 0.0011669 | 0.00029246
26 | 0.00044465 | 0.00011144
27 | 0.00206 | 0.00051627
28 | 0.0029473 | 0.00073867
29 | 0.0038764 | 0.00097153
30 | 0.0016865 | 0.00042267
31 | 0.0024718 | 0.0006195
32 | 0.0022432 | 0.0005622
33 | 0.0037984 | 0.00095197
34 | 0.0013296 | 0.00033323
35 | 0.0016948 | 0.00042477
36 | 0.0018485 | 0.00046328
37 | 0.0027818 | 0.00069718
38 | 0.0016746 | 0.00041969
39 | 0.0030808 | 0.00077213
40 | 0.0027456 | 0.00068812
41 | 0.0021017 | 0.00052674
42 | 0.002472 | 0.00061955
43 | 0.0023801 | 0.0005965
44 | 0.0039109 | 0.00098016
45 | 0.0015904 | 0.00039858
46 | 0.0012784 | 0.0003204
47 | 0.0012795 | 0.00032066
48 | 0.0012797 | 0.00032073
49 | 0.0038223 | 0.00095796
50 | 0.0020221 | 0.00050678
51 | 0.001279 | 0.00032055
52 | 0.0052365 | 0.0013124
53 | 0.0019285 | 0.00048333
54 | 0.0025292 | 0.00063387
55 | 0.0020093 | 0.00050357
56 | 0.0029794 | 0.0007467
57 | 0.0033776 | 0.0008465
58 | 0.0023093 | 0.00057876
59 | 0.0016183 | 0.00040558
60 | 0.003344 | 0.00083809
61 | 0.0030961 | 0.00077595
62 | 0.002675 | 0.00067041
63 | 0.0036207 | 0.00090744
64 | 0.00123 | 0.00030826
65 | 0.002355 | 0.00059023
66 | 0.0051114 | 0.001281
67 | 0.0042764 | 0.0010718
68 | 0.0035381 | 0.00088674
69 | 0.001833 | 0.00045939
70 | 0.0027372 | 0.00068602
71 | 0.0018845 | 0.0004723
72 | 0.002664 | 0.00066766
73 | 0.0038383 | 0.00096198
74 | 0.0018226 | 0.00045679
75 | 0.0026876 | 0.00067358
76 | 0.002906 | 0.00072832

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1