## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1132-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1132-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1132-6_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1132-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1132-6_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1132-6_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1132-6_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1132-6_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1132-6_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1132-6_0_3_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1132-6_0_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_1132-6_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1132-6_0_3_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_1132-6_0_3_node_42 | 0.4 | n |  | TRUE
14 | bus_LV_1132-6_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1132-6_0_3_node_14 | 0.4 | n |  | TRUE
16 | bus_LV_1132-6_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1132-6_0_3_node_35 | 0.4 | n |  | TRUE
18 | bus_LV_1132-6_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1132-6_0_3_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_1132-6_0_3_node_57 | 0.4 | n |  | TRUE
21 | bus_LV_1132-6_0_3_node_70 | 0.4 | n |  | TRUE
22 | bus_LV_1132-6_0_3_node_68 | 0.4 | n |  | TRUE
23 | bus_LV_1132-6_0_3_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_1132-6_0_3_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_1132-6_0_3_node_36 | 0.4 | n |  | TRUE
26 | bus_LV_1132-6_0_3_node_39 | 0.4 | n |  | TRUE
27 | bus_LV_1132-6_0_3_node_105 | 0.4 | n |  | TRUE
28 | bus_LV_1132-6_0_3_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1132-6_0_3_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_1132-6_0_3_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_1132-6_0_3_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_1132-6_0_3_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_1132-6_0_3_node_69 | 0.4 | n |  | TRUE
34 | bus_LV_1132-6_0_3_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_1132-6_0_3_node_19 | 0.4 | n |  | TRUE
36 | bus_LV_1132-6_0_3_node_17 | 0.4 | n |  | TRUE
37 | bus_LV_1132-6_0_3_node_18 | 0.4 | n |  | TRUE
38 | bus_LV_1132-6_0_3_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1132-6_0_3_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1132-6_0_3_node_26 | 0.4 | n |  | TRUE
41 | bus_LV_1132-6_0_3_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_1132-6_0_3_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_1132-6_0_3_node_54 | 0.4 | n |  | TRUE
44 | bus_LV_1132-6_0_3_node_52 | 0.4 | n |  | TRUE
45 | bus_LV_1132-6_0_3_node_53 | 0.4 | n |  | TRUE
46 | bus_LV_1132-6_0_3_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_1132-6_0_3_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_1132-6_0_3_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_1132-6_0_3_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_1132-6_0_3_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_1132-6_0_3_node_32 | 0.4 | n |  | TRUE
52 | bus_LV_1132-6_0_3_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_1132-6_0_3_node_34 | 0.4 | n |  | TRUE
54 | bus_LV_1132-6_0_3_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_1132-6_0_3_node_40 | 0.4 | n |  | TRUE
56 | bus_LV_1132-6_0_3_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_1132-6_0_3_node_107 | 0.4 | n |  | TRUE
58 | bus_LV_1132-6_0_3_node_86 | 0.4 | n |  | TRUE
59 | bus_LV_1132-6_0_3_node_106 | 0.4 | n |  | TRUE
60 | bus_LV_1132-6_0_3_node_104 | 0.4 | n |  | TRUE
61 | bus_LV_1132-6_0_3_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_1132-6_0_3_node_49 | 0.4 | n |  | TRUE
63 | bus_LV_1132-6_0_3_node_43 | 0.4 | n |  | TRUE
64 | bus_LV_1132-6_0_3_node_44 | 0.4 | n |  | TRUE
65 | bus_LV_1132-6_0_3_node_60 | 0.4 | n |  | TRUE
66 | bus_LV_1132-6_0_3_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_1132-6_0_3_node_64 | 0.4 | n |  | TRUE
68 | bus_LV_1132-6_0_3_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_1132-6_0_3_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_1132-6_0_3_node_103 | 0.4 | n |  | TRUE
71 | bus_LV_1132-6_0_3_node_85 | 0.4 | n |  | TRUE
72 | bus_LV_1132-6_0_3_node_55 | 0.4 | n |  | TRUE
73 | bus_LV_1132-6_0_3_node_61 | 0.4 | n |  | TRUE
74 | bus_LV_1132-6_0_3_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_1132-6_0_3_node_62 | 0.4 | n |  | TRUE
76 | bus_LV_1132-6_0_3_node_101 | 0.4 | n |  | TRUE
77 | bus_LV_1132-6_0_3_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_1132-6_0_3_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_1132-6_0_3_node_108 | 0.4 | n |  | TRUE
80 | bus_LV_1132-6_0_3_node_88 | 0.4 | n |  | TRUE
81 | bus_LV_1132-6_0_3_node_89 | 0.4 | n |  | TRUE
82 | bus_LV_1132-6_0_3_node_102 | 0.4 | n |  | TRUE
83 | bus_LV_1132-6_0_3_node_87 | 0.4 | n |  | TRUE
84 | bus_LV_1132-6_0_3_node_109 | 0.4 | n |  | TRUE
85 | bus_LV_1132-6_0_3_node_95 | 0.4 | n |  | TRUE
86 | bus_LV_1132-6_0_3_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_1132-6_0_3_node_72 | 0.4 | n |  | TRUE
88 | bus_LV_1132-6_0_3_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_1132-6_0_3_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_1132-6_0_3_node_90 | 0.4 | n |  | TRUE
91 | bus_LV_1132-6_0_3_node_91 | 0.4 | n |  | TRUE
92 | bus_LV_1132-6_0_3_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_1132-6_0_3_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_1132-6_0_3_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_1132-6_0_3_node_79 | 0.4 | n |  | TRUE
96 | bus_LV_1132-6_0_3_node_80 | 0.4 | n |  | TRUE
97 | bus_LV_1132-6_0_3_node_81 | 0.4 | n |  | TRUE
98 | bus_LV_1132-6_0_3_node_82 | 0.4 | n |  | TRUE
99 | bus_LV_1132-6_0_3_node_99 | 0.4 | n |  | TRUE
100 | bus_LV_1132-6_0_3_node_83 | 0.4 | n |  | TRUE
101 | bus_LV_1132-6_0_3_node_97 | 0.4 | n |  | TRUE
102 | bus_LV_1132-6_0_3_node_84 | 0.4 | n |  | TRUE
103 | bus_LV_1132-6_0_3_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_1132-6_0_3_node_92 | 0.4 | n |  | TRUE
105 | bus_LV_1132-6_0_3_node_96 | 0.4 | n |  | TRUE
106 | bus_LV_1132-6_0_3_node_98 | 0.4 | n |  | TRUE
107 | bus_LV_1132-6_0_3_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_1132-6_0_3_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_1132-6_0_3_node_111 | 0.4 | n |  | TRUE
110 | bus_LV_1132-6_0_3_node_112 | 0.4 | n |  | TRUE
111 | bus_MV_128_0_node_85 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1132-6_0_3_load_0 | 0 | 0.00015247 | 3.8213e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1132-6_0_3_load_1 | 1 | 0.00031168 | 7.8113e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1132-6_0_3_load_3 | 3 | 0.00015702 | 3.9353e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1132-6_0_3_load_5 | 5 | 0.00044603 | 0.00011179 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1132-6_0_3_load_6 | 6 | 0.00088108 | 0.00022082 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1132-6_0_3_load_7 | 7 | 0.00017982 | 4.5067e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1132-6_0_3_load_8 | 8 | 0.00018602 | 4.6622e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1132-6_0_3_load_15 | 9 | 0.00014976 | 3.7534e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1132-6_0_3_load_13 | 10 | 0.0015294 | 0.00038331 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1132-6_0_3_load_16 | 12 | 0.00015839 | 3.9695e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1132-6_0_3_load_42 | 13 | 0.0005619 | 0.00014083 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1132-6_0_3_load_10 | 14 | 0.00027808 | 6.9695e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1132-6_0_3_load_14 | 15 | 0.00035198 | 8.8214e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1132-6_0_3_load_35 | 17 | 0.00090791 | 0.00022754 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1132-6_0_3_load_57 | 20 | 0.0011039 | 0.00027666 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1132-6_0_3_load_70 | 21 | 0.0042858 | 0.0010741 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1132-6_0_3_load_68 | 22 | 0.0070715 | 0.0017723 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1132-6_0_3_load_41 | 24 | 0.00069874 | 0.00017512 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1132-6_0_3_load_31 | 28 | 0.00088233 | 0.00022113 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1132-6_0_3_load_27 | 29 | 0.00082673 | 0.0002072 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1132-6_0_3_load_56 | 30 | 0.0005342 | 0.00013388 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1132-6_0_3_load_73 | 31 | 0.0041718 | 0.0010456 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1132-6_0_3_load_37 | 32 | 0.00060906 | 0.00015264 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1132-6_0_3_load_19 | 35 | 0.0002252 | 5.644e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1132-6_0_3_load_17 | 36 | 0.0020861 | 0.00052284 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1132-6_0_3_load_18 | 37 | 0.006669 | 0.0016714 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1132-6_0_3_load_25 | 39 | 0.00086403 | 0.00021655 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1132-6_0_3_load_26 | 40 | 0.00095653 | 0.00023973 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1132-6_0_3_load_22 | 41 | 0.00064268 | 0.00016107 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1132-6_0_3_load_23 | 42 | 0.00017118 | 4.2903e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1132-6_0_3_load_54 | 43 | 0.0012255 | 0.00030715 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1132-6_0_3_load_52 | 44 | 0.00046967 | 0.00011771 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1132-6_0_3_load_53 | 45 | 0.002748 | 0.00068872 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1132-6_0_3_load_28 | 46 | 0.0011481 | 0.00028773 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1132-6_0_3_load_29 | 47 | 0.00060631 | 0.00015196 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1132-6_0_3_load_47 | 49 | 0.0013071 | 0.00032759 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1132-6_0_3_load_45 | 50 | 0.00044511 | 0.00011155 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1132-6_0_3_load_32 | 51 | 0.0013176 | 0.00033023 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1132-6_0_3_load_33 | 52 | 0.00090975 | 0.00022801 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1132-6_0_3_load_38 | 54 | 0.00045593 | 0.00011427 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1132-6_0_3_load_107 | 57 | 0.024821 | 0.0062206 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1132-6_0_3_load_106 | 59 | 0.007448 | 0.0018666 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1132-6_0_3_load_104 | 60 | 0.0024424 | 0.00061212 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1132-6_0_3_load_48 | 61 | 0.00065424 | 0.00016397 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1132-6_0_3_load_49 | 62 | 0.00059963 | 0.00015028 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1132-6_0_3_load_43 | 63 | 0.00049275 | 0.00012349 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1132-6_0_3_load_44 | 64 | 0.00044511 | 0.00011155 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1132-6_0_3_load_63 | 66 | 0.012437 | 0.003117 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1132-6_0_3_load_58 | 68 | 0.0046529 | 0.0011661 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1132-6_0_3_load_103 | 70 | 0.0028213 | 0.00070709 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1132-6_0_3_load_85 | 71 | 0.0019058 | 0.00047764 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1132-6_0_3_load_55 | 72 | 0.0006408 | 0.0001606 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1132-6_0_3_load_67 | 74 | 0.0094485 | 0.002368 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1132-6_0_3_load_101 | 76 | 0.010541 | 0.0026419 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1132-6_0_3_load_108 | 79 | 0.011687 | 0.0029289 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1132-6_0_3_load_102 | 82 | 0.0070934 | 0.0017778 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1132-6_0_3_load_87 | 83 | 0.014283 | 0.0035796 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1132-6_0_3_load_109 | 84 | 0.0035193 | 0.00088201 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1132-6_0_3_load_95 | 85 | 0.0014655 | 0.00036729 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1132-6_0_3_load_71 | 86 | 0.0021599 | 0.00054133 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1132-6_0_3_load_72 | 87 | 0.003803 | 0.00095313 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1132-6_0_3_load_74 | 88 | 0.0024995 | 0.00062642 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1132-6_0_3_load_75 | 89 | 0.001948 | 0.00048821 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1132-6_0_3_load_90 | 90 | 0.0024208 | 0.00060671 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1132-6_0_3_load_91 | 91 | 0.00062524 | 0.0001567 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1132-6_0_3_load_76 | 92 | 0.0022381 | 0.00056092 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1132-6_0_3_load_77 | 93 | 0.0026745 | 0.00067028 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1132-6_0_3_load_78 | 94 | 0.00168 | 0.00042104 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1132-6_0_3_load_79 | 95 | 0.0061101 | 0.0015313 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1132-6_0_3_load_80 | 96 | 0.001752 | 0.0004391 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1132-6_0_3_load_81 | 97 | 0.0020066 | 0.00050289 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1132-6_0_3_load_82 | 98 | 0.0022531 | 0.00056467 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1132-6_0_3_load_99 | 99 | 0.0026513 | 0.00066449 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1132-6_0_3_load_83 | 100 | 0.0016069 | 0.00040273 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1132-6_0_3_load_84 | 102 | 0.0052309 | 0.001311 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1132-6_0_3_load_93 | 103 | 0.0017362 | 0.00043514 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1132-6_0_3_load_92 | 104 | 0.0043164 | 0.0010818 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1132-6_0_3_load_96 | 105 | 0.0028055 | 0.00070313 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1132-6_0_3_load_98 | 106 | 0.0019537 | 0.00048965 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1132-6_0_3_load_100 | 107 | 0.0019411 | 0.0004865 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1132-6_0_3_load_110 | 108 | 0.0012432 | 0.00031157 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1132-6_0_3_load_111 | 109 | 0.001104 | 0.00027669 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1132-6_0_3_load_112 | 110 | 0.00072089 | 0.00018067 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 60 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1132-6_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1132-6_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.026521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1132-6_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0089888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1132-6_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.009767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1132-6_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.058421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1132-6_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0097229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1132-6_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.0029033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1132-6_0_3_line_7 | NAYY 4x150 SE | 4 | 8 | 0.019551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1132-6_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.022265 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1132-6_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.02361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1132-6_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.018702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1132-6_0_3_line_11 | NAYY 4x150 SE | 9 | 12 | 0.00018853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1132-6_0_3_line_12 | NAYY 4x150 SE | 10 | 13 | 0.011968 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1132-6_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.015225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1132-6_0_3_line_14 | NAYY 4x150 SE | 13 | 24 | 0.023239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1132-6_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.05485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1132-6_0_3_line_16 | NAYY 4x150 SE | 15 | 23 | 0.046188 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1132-6_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.031295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1132-6_0_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.039176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1132-6_0_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.014098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1132-6_0_3_line_20 | NAYY 4x150 SE | 17 | 24 | 0.028463 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1132-6_0_3_line_21 | NAYY 4x150 SE | 18 | 20 | 0.017084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1132-6_0_3_line_22 | NAYY 4x150 SE | 18 | 21 | 0.05195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1132-6_0_3_line_23 | NAYY 4x150 SE | 18 | 22 | 0.023868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1132-6_0_3_line_24 | NAYY 4x150 SE | 19 | 28 | 0.014145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1132-6_0_3_line_25 | NAYY 4x150 SE | 19 | 29 | 0.028184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1132-6_0_3_line_26 | NAYY 4x150 SE | 20 | 30 | 0.01944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1132-6_0_3_line_27 | NAYY 4x150 SE | 21 | 31 | 0.023734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1132-6_0_3_line_28 | NAYY 4x150 SE | 22 | 33 | 0.020765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1132-6_0_3_line_29 | NAYY 4x150 SE | 23 | 34 | 0.004042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1132-6_0_3_line_30 | NAYY 4x150 SE | 23 | 35 | 0.011204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1132-6_0_3_line_31 | NAYY 4x150 SE | 25 | 26 | 0.025577 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1132-6_0_3_line_32 | NAYY 4x150 SE | 25 | 27 | 0.036191 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1132-6_0_3_line_33 | NAYY 4x150 SE | 26 | 32 | 0.054206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1132-6_0_3_line_34 | NAYY 4x150 SE | 27 | 59 | 0.006852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1132-6_0_3_line_35 | NAYY 4x150 SE | 27 | 60 | 0.0030057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1132-6_0_3_line_36 | NAYY 4x150 SE | 28 | 51 | 0.026157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1132-6_0_3_line_37 | NAYY 4x150 SE | 29 | 38 | 0.029582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1132-6_0_3_line_38 | NAYY 4x150 SE | 30 | 72 | 0.018033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1132-6_0_3_line_39 | NAYY 4x150 SE | 32 | 53 | 0.017016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1132-6_0_3_line_40 | NAYY 4x150 SE | 33 | 86 | 0.015354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1132-6_0_3_line_41 | NAYY 4x150 SE | 33 | 87 | 0.042651 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1132-6_0_3_line_42 | NAYY 4x150 SE | 34 | 41 | 0.026746 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1132-6_0_3_line_43 | NAYY 4x150 SE | 34 | 42 | 0.053875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1132-6_0_3_line_44 | NAYY 4x150 SE | 36 | 37 | 0.024918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1132-6_0_3_line_45 | NAYY 4x150 SE | 37 | 38 | 0.020923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1132-6_0_3_line_46 | NAYY 4x150 SE | 38 | 39 | 0.01241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1132-6_0_3_line_47 | NAYY 4x150 SE | 38 | 40 | 0.032699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1132-6_0_3_line_48 | NAYY 4x150 SE | 39 | 46 | 0.0016855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1132-6_0_3_line_49 | NAYY 4x150 SE | 40 | 47 | 0.0014713 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1132-6_0_3_line_50 | NAYY 4x150 SE | 41 | 43 | 0.073535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1132-6_0_3_line_51 | NAYY 4x150 SE | 42 | 44 | 0.14186 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1132-6_0_3_line_52 | NAYY 4x150 SE | 44 | 45 | 0.046924 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1132-6_0_3_line_53 | NAYY 4x150 SE | 46 | 48 | 0.014769 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1132-6_0_3_line_54 | NAYY 4x150 SE | 48 | 49 | 0.013089 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1132-6_0_3_line_55 | NAYY 4x150 SE | 48 | 50 | 0.01293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1132-6_0_3_line_56 | NAYY 4x150 SE | 49 | 55 | 0.015185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1132-6_0_3_line_57 | NAYY 4x150 SE | 50 | 64 | 0.007331 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1132-6_0_3_line_58 | NAYY 4x150 SE | 51 | 52 | 0.022075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1132-6_0_3_line_59 | NAYY 4x150 SE | 52 | 53 | 0.015388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1132-6_0_3_line_60 | NAYY 4x150 SE | 54 | 55 | 0.011478 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1132-6_0_3_line_61 | NAYY 4x150 SE | 55 | 61 | 0.014497 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1132-6_0_3_line_62 | NAYY 4x150 SE | 56 | 57 | 0.025235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
63 | LV_1132-6_0_3_line_63 | NAYY 4x150 SE | 56 | 58 | 0.024622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
64 | LV_1132-6_0_3_line_64 | NAYY 4x150 SE | 57 | 67 | 0.024857 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1132-6_0_3_line_65 | NAYY 4x150 SE | 58 | 70 | 0.033401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
66 | LV_1132-6_0_3_line_66 | NAYY 4x150 SE | 58 | 71 | 0.063315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1132-6_0_3_line_67 | NAYY 4x150 SE | 60 | 70 | 0.02232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
68 | LV_1132-6_0_3_line_68 | NAYY 4x150 SE | 61 | 62 | 0.02045 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1132-6_0_3_line_69 | NAYY 4x150 SE | 63 | 64 | 0.016891 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1132-6_0_3_line_70 | NAYY 4x150 SE | 65 | 66 | 0.016015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1132-6_0_3_line_71 | NAYY 4x150 SE | 65 | 67 | 0.010609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1132-6_0_3_line_72 | NAYY 4x150 SE | 66 | 74 | 0.030597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1132-6_0_3_line_73 | NAYY 4x150 SE | 67 | 77 | 0.017416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1132-6_0_3_line_74 | NAYY 4x150 SE | 68 | 69 | 0.015023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1132-6_0_3_line_75 | NAYY 4x150 SE | 69 | 73 | 0.004026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1132-6_0_3_line_76 | NAYY 4x150 SE | 71 | 102 | 0.0023623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1132-6_0_3_line_77 | NAYY 4x150 SE | 73 | 74 | 0.015856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1132-6_0_3_line_78 | NAYY 4x150 SE | 73 | 75 | 0.10936 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1132-6_0_3_line_79 | NAYY 4x150 SE | 75 | 76 | 0.081348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1132-6_0_3_line_80 | NAYY 4x150 SE | 76 | 82 | 0.019338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1132-6_0_3_line_81 | NAYY 4x150 SE | 77 | 79 | 0.004712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1132-6_0_3_line_82 | NAYY 4x150 SE | 78 | 79 | 0.013676 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1132-6_0_3_line_83 | NAYY 4x150 SE | 78 | 80 | 0.034572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1132-6_0_3_line_84 | NAYY 4x150 SE | 78 | 81 | 0.025843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1132-6_0_3_line_85 | NAYY 4x150 SE | 80 | 83 | 0.018843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1132-6_0_3_line_86 | NAYY 4x150 SE | 81 | 84 | 0.018301 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1132-6_0_3_line_87 | NAYY 4x150 SE | 81 | 85 | 0.028946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1132-6_0_3_line_88 | NAYY 4x150 SE | 85 | 103 | 0.061211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1132-6_0_3_line_89 | NAYY 4x150 SE | 86 | 88 | 0.0053222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1132-6_0_3_line_90 | NAYY 4x150 SE | 87 | 89 | 0.00053809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1132-6_0_3_line_91 | NAYY 4x150 SE | 88 | 90 | 0.023615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1132-6_0_3_line_92 | NAYY 4x150 SE | 90 | 91 | 0.0038522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1132-6_0_3_line_93 | NAYY 4x150 SE | 92 | 93 | 0.029028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1132-6_0_3_line_94 | NAYY 4x150 SE | 92 | 94 | 0.0075177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1132-6_0_3_line_95 | NAYY 4x150 SE | 93 | 95 | 0.008296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1132-6_0_3_line_96 | NAYY 4x150 SE | 94 | 96 | 0.018644 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1132-6_0_3_line_97 | NAYY 4x150 SE | 95 | 97 | 0.033562 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1132-6_0_3_line_98 | NAYY 4x150 SE | 96 | 98 | 0.0063719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1132-6_0_3_line_99 | NAYY 4x150 SE | 97 | 99 | 0.040964 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1132-6_0_3_line_100 | NAYY 4x150 SE | 98 | 100 | 0.01726 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1132-6_0_3_line_101 | NAYY 4x150 SE | 99 | 101 | 0.0056954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1132-6_0_3_line_102 | NAYY 4x150 SE | 100 | 102 | 0.020565 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1132-6_0_3_line_103 | NAYY 4x150 SE | 101 | 106 | 0.0043992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1132-6_0_3_line_104 | NAYY 4x150 SE | 101 | 105 | 0.031718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1132-6_0_3_line_105 | NAYY 4x150 SE | 103 | 104 | 0.025126 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1132-6_0_3_line_106 | NAYY 4x150 SE | 106 | 107 | 0.030063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1132-6_0_3_line_107 | NAYY 4x150 SE | 107 | 108 | 0.015821 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1132-6_0_3_line_108 | NAYY 4x150 SE | 108 | 109 | 0.010052 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1132-6_0_3_line_109 | NAYY 4x150 SE | 109 | 110 | 0.019967 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1132-6_0_3_trafo_104 | 0.25 MVA 20/0.4 kV | 111 | 60 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17
0 | 2639653.0105 | 1215353.9981 | 2639662.6351 | 1215346.0149 | 2639664.4731 | 1215343.6702 | 2639665.3902 | 1215341.6529 | 2639665.7626 | 1215339.3206 | 2639665.6924 | 1215337.3079 | 2639665.6924 | 1215337.3079
1 | 2639632.5973 | 1215370.9299 | 2639653.0105 | 1215353.9981
2 | 2639661.1781 | 1215329.7174 | 2639663.6361 | 1215332.5136 | 2639665.0553 | 1215334.9134 | 2639665.6924 | 1215337.3079
3 | 2639632.5973 | 1215370.9299 | 2639623.4554 | 1215367.4227
4 | 2639632.5973 | 1215370.9299 | 2639637.1233 | 1215373.1613 | 2639655.943 | 1215385.2045 | 2639664.3583 | 1215389.4851 | 2639672.6988 | 1215392.4534 | 2639683.093 | 1215394.8795 | 2639685.1385 | 1215395.1499
5 | 2639654.7587 | 1215322.4149 | 2639661.1781 | 1215329.7174
6 | 2639623.4554 | 1215367.4227 | 2639621.0767 | 1215365.7581
7 | 2639623.4554 | 1215367.4227 | 2639621.1974 | 1215368.9864 | 2639616.0911 | 1215374.0999 | 2639608.7289 | 1215380.2261
8 | 2639654.7587 | 1215322.4149 | 2639640.0585 | 1215305.6922
9 | 2639601.6663 | 1215352.3178 | 2639608.0896 | 1215356.6699 | 2639621.0767 | 1215365.7581
10 | 2639594.3528 | 1215392.1885 | 2639608.7289 | 1215380.2261
11 | 2639639.934 | 1215305.5506 | 2639640.0585 | 1215305.6922
12 | 2639601.6663 | 1215352.3178 | 2639591.7587 | 1215345.605
13 | 2639594.3528 | 1215392.1885 | 2639602.4477 | 1215405.0832
14 | 2639591.7587 | 1215345.605 | 2639587.4753 | 1215342.7028 | 2639579.8299 | 1215336.8042 | 2639574.932 | 1215332.2579 | 2639573.7863 | 1215330.9675
15 | 2639631.6106 | 1215451.5379 | 2639602.4477 | 1215405.0832
16 | 2639656.1682 | 1215490.6566 | 2639631.6106 | 1215451.5379
17 | 2639547.8741 | 1215277.691 | 2639558.8119 | 1215307.0126
18 | 2639547.8741 | 1215277.691 | 2639538.3413 | 1215281.5857 | 2639534.1392 | 1215283.181 | 2639526.3987 | 1215264.1186 | 2639522.8734 | 1215265.5628
19 | 2639547.8741 | 1215277.691 | 2639543.7416 | 1215264.2113
20 | 2639558.8119 | 1215307.0126 | 2639559.0952 | 1215307.7719 | 2639563.1891 | 1215316.771 | 2639566.3963 | 1215322.062 | 2639569.9575 | 1215326.655 | 2639573.7863 | 1215330.9675
21 | 2639522.8734 | 1215265.5628 | 2639529.2774 | 1215281.4011
22 | 2639522.8734 | 1215265.5628 | 2639514.6042 | 1215246.0633 | 2639501.4388 | 1215219.4383 | 2639500.9153 | 1215218.5081
23 | 2639522.8734 | 1215265.5628 | 2639500.7774 | 1215274.5887
24 | 2639543.7416 | 1215264.2113 | 2639539.7511 | 1215255.6354 | 2639537.721 | 1215251.4116
25 | 2639543.7416 | 1215264.2113 | 2639568.073 | 1215249.9876
26 | 2639536.5643 | 1215299.4233 | 2639529.2774 | 1215281.4011
27 | 2639489.276 | 1215197.8243 | 2639500.9153 | 1215218.5081
28 | 2639481.1234 | 1215280.6508 | 2639483.9173 | 1215280.7138 | 2639489.1812 | 1215279.3255 | 2639500.7774 | 1215274.5887
29 | 2639656.1682 | 1215490.6566 | 2639652.925 | 1215493.0809
30 | 2639656.1682 | 1215490.6566 | 2639661.9949 | 1215500.2267
31 | 2639475.7232 | 1215131.6946 | 2639473.1481 | 1215132.9672 | 2639466.6863 | 1215136.3487 | 2639459.9483 | 1215140.173 | 2639461.833 | 1215143.3874 | 2639458.5608 | 1215145.5781
32 | 2639428.4703 | 1215165.8133 | 2639430.9797 | 1215164.1289 | 2639455.2352 | 1215147.813 | 2639458.5608 | 1215145.5781
33 | 2639475.7232 | 1215131.6946 | 2639500.8459 | 1215179.7275
34 | 2639431.8403 | 1215171.7835 | 2639428.4703 | 1215165.8133
35 | 2639428.4703 | 1215165.8133 | 2639426.9963 | 1215163.1939
36 | 2639526.3901 | 1215227.8365 | 2639537.721 | 1215251.4116
37 | 2639593.6115 | 1215235.0583 | 2639568.073 | 1215249.9876
38 | 2639536.5643 | 1215299.4233 | 2639541.6554 | 1215312.0144 | 2639543.618 | 1215316.0095
39 | 2639508.7323 | 1215194.8055 | 2639500.8459 | 1215179.7275
40 | 2639481.1234 | 1215280.6508 | 2639482.2765 | 1215291.1312 | 2639483.4931 | 1215295.7849
41 | 2639481.1234 | 1215280.6508 | 2639479.1358 | 1215280.3597 | 2639477.2725 | 1215279.6581 | 2639474.4979 | 1215277.8164 | 2639451.8628 | 1215253.5525 | 2639450.4597 | 1215251.939
42 | 2639652.925 | 1215493.0809 | 2639638.9805 | 1215470.2573
43 | 2639652.925 | 1215493.0809 | 2639648.0639 | 1215496.7285 | 2639645.1269 | 1215499.922 | 2639644.137 | 1215506.0412 | 2639645.1208 | 1215511.1174 | 2639659.0714 | 1215540.0156
44 | 2639616.7046 | 1215274.657 | 2639615.7074 | 1215272.9604 | 2639604.1491 | 1215253.1339
45 | 2639593.6115 | 1215235.0583 | 2639604.1491 | 1215253.1339
46 | 2639593.6115 | 1215235.0583 | 2639587.2703 | 1215224.3903
47 | 2639593.6115 | 1215235.0583 | 2639621.751 | 1215218.4041
48 | 2639586.409 | 1215222.9415 | 2639587.2703 | 1215224.3903
49 | 2639621.751 | 1215218.4041 | 2639623.0172 | 1215217.6547
50 | 2639599.6811 | 1215408.1074 | 2639630.8412 | 1215456.9353 | 2639638.9805 | 1215470.2573
51 | 2639659.0714 | 1215540.0156 | 2639542.9092 | 1215621.4405
52 | 2639542.9092 | 1215621.4405 | 2639499.5372 | 1215603.5305
53 | 2639578.8625 | 1215210.2459 | 2639586.409 | 1215222.9415
54 | 2639578.8625 | 1215210.2459 | 2639572.1702 | 1215198.9971
55 | 2639578.8625 | 1215210.2459 | 2639589.902 | 1215203.5143
56 | 2639564.4062 | 1215185.9469 | 2639572.1702 | 1215198.9971
57 | 2639596.1612 | 1215199.6976 | 2639589.902 | 1215203.5143
58 | 2639516.1268 | 1215208.3001 | 2639523.2352 | 1215221.2726 | 2639526.3901 | 1215227.8365
59 | 2639508.7323 | 1215194.8055 | 2639516.1268 | 1215208.3001
60 | 2639564.4062 | 1215185.9469 | 2639558.5357 | 1215176.0838
61 | 2639564.4062 | 1215185.9469 | 2639576.788 | 1215178.4061
62 | 2639433.489 | 1215103.888 | 2639420.635 | 1215082.1723
63 | 2639410.9744 | 1215112.9891 | 2639415.3656 | 1215112.6734 | 2639419.3511 | 1215111.6992 | 2639423.2504 | 1215109.9795 | 2639433.489 | 1215103.888
64 | 2639407.4596 | 1215061.1022 | 2639414.4291 | 1215071.6877 | 2639420.635 | 1215082.1723
65 | 2639410.9744 | 1215112.9891 | 2639407.63 | 1215124.9629 | 2639407.4626 | 1215127.3076 | 2639407.9053 | 1215129.2672 | 2639416.0507 | 1215143.7425
66 | 2639410.9744 | 1215112.9891 | 2639407.839 | 1215112.8683 | 2639403.8064 | 1215111.7744 | 2639399.9066 | 1215110.1254 | 2639396.1786 | 1215107.7439 | 2639391.9597 | 1215103.8248 | 2639388.7256 | 1215101.3909 | 2639386.3558 | 1215100.3302 | 2639383.4501 | 1215099.9331 | 2639380.2893 | 1215100.2012 | 2639377.771 | 1215100.9295 | 2639375.75 | 1215102.2503 | 2639373.192 | 1215104.3902 | 2639371.2461 | 1215106.9789 | 2639370.2098 | 1215109.8181 | 2639369.6323 | 1215113.3275 | 2639369.8726 | 1215117.1869 | 2639371.1862 | 1215123.8375
67 | 2639416.0507 | 1215143.7425 | 2639426.9963 | 1215163.1939
68 | 2639576.788 | 1215178.4061 | 2639594.2536 | 1215167.7691
69 | 2639610.5829 | 1215190.9035 | 2639596.1612 | 1215199.6976
70 | 2639401.6179 | 1215052.2362 | 2639392.9737 | 1215038.755
71 | 2639401.6179 | 1215052.2362 | 2639407.4596 | 1215061.1022
72 | 2639376.4583 | 1215012.9978 | 2639392.9737 | 1215038.755
73 | 2639392.6141 | 1215070.2762 | 2639407.4596 | 1215061.1022
74 | 2639371.4283 | 1214997.694 | 2639379.0963 | 1215010.6125
75 | 2639371.4283 | 1214997.694 | 2639367.8995 | 1214999.6496
76 | 2639371.1862 | 1215123.8375 | 2639371.644 | 1215126.155
77 | 2639367.8995 | 1214999.6496 | 2639376.4583 | 1215012.9978
78 | 2639295.9351 | 1214975.1388 | 2639301.3048 | 1214966.9472 | 2639306.0437 | 1214959.9743 | 2639308.9068 | 1214959.9376 | 2639312.7844 | 1214959.2182 | 2639319.4012 | 1214956.5269 | 2639321.4297 | 1214959.8422 | 2639347.4393 | 1215002.3385 | 2639349.6479 | 1215004.8212 | 2639351.7892 | 1215005.9915 | 2639354.4301 | 1215006.2535 | 2639357.0699 | 1215005.5261 | 2639361.543 | 1215003.1764 | 2639367.8995 | 1214999.6496
79 | 2639295.9351 | 1214975.1388 | 2639295.3078 | 1214979.2927 | 2639295.7229 | 1214984.2983 | 2639296.7984 | 1214990.4868 | 2639298.1841 | 1214996.8441 | 2639300.4063 | 1215004.1852 | 2639303.1617 | 1215010.1291 | 2639306.4985 | 1215015.4097 | 2639322.0564 | 1215037.5584 | 2639324.4684 | 1215041.4433 | 2639326.3014 | 1215045.6022 | 2639327.1017 | 1215048.1644
80 | 2639330.556 | 1215067.1651 | 2639329.4205 | 1215058.5748 | 2639327.6549 | 1215049.9359 | 2639327.1017 | 1215048.1644
81 | 2639392.6141 | 1215070.2762 | 2639388.3932 | 1215072.394
82 | 2639381.1648 | 1215060.7729 | 2639388.3932 | 1215072.394
83 | 2639360.77 | 1215035.1567 | 2639369.762 | 1215048.8129 | 2639378.0246 | 1215061.3636 | 2639381.1648 | 1215060.7729
84 | 2639358.9747 | 1215073.6118 | 2639378.0246 | 1215061.3636 | 2639381.1648 | 1215060.7729
85 | 2639360.77 | 1215035.1567 | 2639350.4108 | 1215019.4172
86 | 2639358.9747 | 1215073.6118 | 2639358.355 | 1215076.6205 | 2639358.1992 | 1215078.365 | 2639358.5306 | 1215079.9236 | 2639359.2923 | 1215081.8742 | 2639364.4848 | 1215090.1735
87 | 2639358.9747 | 1215073.6118 | 2639353.2562 | 1215074.8303 | 2639334.6087 | 1215087.1034 | 2639333.9517 | 1215087.515
88 | 2639282.1293 | 1215077.7704 | 2639284.9042 | 1215079.605 | 2639290.9912 | 1215084.6925 | 2639296.864 | 1215090.0232 | 2639301.7335 | 1215095.4918 | 2639303.5335 | 1215096.5931 | 2639306.2324 | 1215097.278 | 2639309.4461 | 1215097.0323 | 2639321.2641 | 1215094.3864 | 2639326.8462 | 1215091.9662 | 2639333.9517 | 1215087.515
89 | 2639484.8393 | 1215300.9341 | 2639483.4931 | 1215295.7849
90 | 2639450.1066 | 1215251.533 | 2639450.4597 | 1215251.939
91 | 2639484.8393 | 1215300.9341 | 2639484.9056 | 1215301.1878 | 2639487.2948 | 1215308.4857 | 2639494.2031 | 1215322.555
92 | 2639494.2031 | 1215322.555 | 2639495.901 | 1215326.0129
93 | 2639387.7887 | 1215194.5738 | 2639394.5965 | 1215222.7925
94 | 2639387.7887 | 1215194.5738 | 2639386.0987 | 1215187.5684 | 2639386.0085 | 1215187.2704
95 | 2639394.5965 | 1215222.7925 | 2639396.5422 | 1215230.8571
96 | 2639380.6693 | 1215169.4077 | 2639381.1717 | 1215171.282 | 2639386.0085 | 1215187.2704
97 | 2639396.5422 | 1215230.8571 | 2639397.4515 | 1215234.6265 | 2639400.4086 | 1215242.1948 | 2639410.1346 | 1215261.4356
98 | 2639380.6693 | 1215169.4077 | 2639379.0196 | 1215163.2531
99 | 2639420.9649 | 1215300.1968 | 2639421.3712 | 1215297.788 | 2639421.1895 | 1215293.1174 | 2639420.6176 | 1215287.7327 | 2639419.5553 | 1215283.0118 | 2639418.0004 | 1215278.1543 | 2639415.9092 | 1215272.8596 | 2639410.1346 | 1215261.4356
100 | 2639375.6291 | 1215146.3306 | 2639378.8372 | 1215162.5726 | 2639379.0196 | 1215163.2531
101 | 2639417.9988 | 1215304.8254 | 2639419.602 | 1215303.5241 | 2639420.7943 | 1215301.2084 | 2639420.9649 | 1215300.1968
102 | 2639375.6291 | 1215146.3306 | 2639371.644 | 1215126.155
103 | 2639417.9988 | 1215304.8254 | 2639415.8148 | 1215305.5336 | 2639413.7203 | 1215305.3419 | 2639413.7203 | 1215305.3419
104 | 2639417.9988 | 1215304.8254 | 2639437.7948 | 1215329.6075
105 | 2639264.2122 | 1215062.82 | 2639265.3341 | 1215067.1022 | 2639266.7355 | 1215069.9242 | 2639268.0771 | 1215071.4562 | 2639270.0947 | 1215072.9592 | 2639278.0197 | 1215075.7019 | 2639281.2524 | 1215077.1907 | 2639282.1293 | 1215077.7704
106 | 2639413.7203 | 1215305.3419 | 2639410.7806 | 1215304.3441 | 2639407.3955 | 1215301.8092 | 2639403.8069 | 1215297.9054 | 2639399.3228 | 1215291.6055 | 2639394.793 | 1215283.0344
107 | 2639394.793 | 1215283.0344 | 2639387.4004 | 1215269.0464
108 | 2639382.7034 | 1215260.1588 | 2639387.4004 | 1215269.0464
109 | 2639373.3737 | 1215242.5055 | 2639382.7034 | 1215260.1588

## bus_geodata
| x | y | coords
0 | 2639653.0105 | 1215353.9981
1 | 2639665.6924 | 1215337.3079
2 | 2639632.5973 | 1215370.9299
3 | 2639661.1781 | 1215329.7174
4 | 2639623.4554 | 1215367.4227
5 | 2639685.1385 | 1215395.1499
6 | 2639654.7587 | 1215322.4149
7 | 2639621.0767 | 1215365.7581
8 | 2639608.7289 | 1215380.2261
9 | 2639640.0585 | 1215305.6922
10 | 2639601.6663 | 1215352.3178
11 | 2639594.3528 | 1215392.1885
12 | 2639639.934 | 1215305.5506
13 | 2639591.7587 | 1215345.605
14 | 2639602.4477 | 1215405.0831
15 | 2639631.6106 | 1215451.5379
16 | 2639547.8741 | 1215277.691
17 | 2639558.8119 | 1215307.0126
18 | 2639522.8734 | 1215265.5628
19 | 2639543.7416 | 1215264.2113
20 | 2639529.2774 | 1215281.4011
21 | 2639500.9153 | 1215218.5081
22 | 2639500.7774 | 1215274.5887
23 | 2639656.1682 | 1215490.6566
24 | 2639573.7863 | 1215330.9675
25 | 2639458.5608 | 1215145.5781
26 | 2639475.7232 | 1215131.6946
27 | 2639428.4703 | 1215165.8133
28 | 2639537.721 | 1215251.4116
29 | 2639568.073 | 1215249.9876
30 | 2639536.5643 | 1215299.4233
31 | 2639489.276 | 1215197.8243
32 | 2639500.8459 | 1215179.7275
33 | 2639481.1234 | 1215280.6508
34 | 2639652.925 | 1215493.0809
35 | 2639661.9949 | 1215500.2267
36 | 2639616.7046 | 1215274.657
37 | 2639604.1491 | 1215253.1339
38 | 2639593.6115 | 1215235.0583
39 | 2639587.2703 | 1215224.3903
40 | 2639621.751 | 1215218.4041
41 | 2639638.9805 | 1215470.2573
42 | 2639659.0714 | 1215540.0156
43 | 2639599.6811 | 1215408.1074
44 | 2639542.9092 | 1215621.4405
45 | 2639499.5372 | 1215603.5305
46 | 2639586.409 | 1215222.9415
47 | 2639623.0172 | 1215217.6547
48 | 2639578.8625 | 1215210.2459
49 | 2639572.1702 | 1215198.9971
50 | 2639589.902 | 1215203.5143
51 | 2639526.3901 | 1215227.8365
52 | 2639516.1268 | 1215208.3001
53 | 2639508.7323 | 1215194.8055
54 | 2639558.5357 | 1215176.0838
55 | 2639564.4062 | 1215185.9469
56 | 2639433.489 | 1215103.888
57 | 2639420.635 | 1215082.1723
58 | 2639410.9744 | 1215112.9891
59 | 2639431.8403 | 1215171.7835
60 | 2639426.9963 | 1215163.1939
61 | 2639576.788 | 1215178.4061
62 | 2639594.2536 | 1215167.7691
63 | 2639610.5829 | 1215190.9035
64 | 2639596.1612 | 1215199.6976
65 | 2639401.6179 | 1215052.2362
66 | 2639392.9737 | 1215038.755
67 | 2639407.4596 | 1215061.1022
68 | 2639379.0963 | 1215010.6125
69 | 2639371.4283 | 1214997.694
70 | 2639416.0507 | 1215143.7425
71 | 2639371.1862 | 1215123.8375
72 | 2639543.618 | 1215316.0095
73 | 2639367.8995 | 1214999.6496
74 | 2639376.4583 | 1215012.9978
75 | 2639295.9351 | 1214975.1388
76 | 2639327.1017 | 1215048.1644
77 | 2639392.6141 | 1215070.2762
78 | 2639381.1648 | 1215060.7729
79 | 2639388.3932 | 1215072.394
80 | 2639360.77 | 1215035.1567
81 | 2639358.9747 | 1215073.6118
82 | 2639330.556 | 1215067.1651
83 | 2639350.4108 | 1215019.4172
84 | 2639364.4848 | 1215090.1735
85 | 2639333.9517 | 1215087.515
86 | 2639483.4931 | 1215295.7849
87 | 2639450.4597 | 1215251.939
88 | 2639484.8393 | 1215300.9341
89 | 2639450.1066 | 1215251.533
90 | 2639494.2031 | 1215322.555
91 | 2639495.901 | 1215326.0129
92 | 2639387.7887 | 1215194.5738
93 | 2639394.5965 | 1215222.7925
94 | 2639386.0085 | 1215187.2704
95 | 2639396.5422 | 1215230.8571
96 | 2639380.6693 | 1215169.4077
97 | 2639410.1346 | 1215261.4356
98 | 2639379.0196 | 1215163.2531
99 | 2639420.9649 | 1215300.1968
100 | 2639375.6291 | 1215146.3306
101 | 2639417.9988 | 1215304.8254
102 | 2639371.644 | 1215126.155
103 | 2639282.1293 | 1215077.7704
104 | 2639264.2122 | 1215062.82
105 | 2639437.7948 | 1215329.6075
106 | 2639413.7203 | 1215305.3419
107 | 2639394.793 | 1215283.0344
108 | 2639387.4004 | 1215269.0464
109 | 2639382.7034 | 1215260.1588
110 | 2639373.3737 | 1215242.5055
111 | 2639428.4703 | 1215165.8133

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97704 | -0.16119 | 0.00015247 | 3.8213e-05
1 | 0.97699 | -0.16157 | 0.00031168 | 7.8113e-05
2 | 0.97711 | -0.16068 | 0 | 0
3 | 0.97697 | -0.1617 | 0.00015702 | 3.9353e-05
4 | 0.97714 | -0.16045 | 0 | 0
5 | 0.97707 | -0.16096 | 0.00044603 | 0.00011179
6 | 0.97695 | -0.16182 | 0.00088108 | 0.00022082
7 | 0.97718 | -0.16019 | 0.00017982 | 4.5067e-05
8 | 0.97696 | -0.16175 | 0.00018602 | 4.6622e-05
9 | 0.97694 | -0.16189 | 0.00014976 | 3.7534e-05
10 | 0.97748 | -0.15802 | 0.0015294 | 0.00038331
11 | 0.97679 | -0.16295 | 0 | 0
12 | 0.97694 | -0.16189 | 0.00015839 | 3.9695e-05
13 | 0.97766 | -0.15673 | 0.0005619 | 0.00014083
14 | 0.97666 | -0.16393 | 0.00027808 | 6.9695e-05
15 | 0.97619 | -0.16731 | 0.00035198 | 8.8214e-05
16 | 0.97907 | -0.14657 | 0 | 0
17 | 0.9785 | -0.15064 | 0.00090791 | 0.00022754
18 | 0.97728 | -0.15935 | 0 | 0
19 | 0.97997 | -0.14014 | 0 | 0
20 | 0.97723 | -0.15976 | 0.0011039 | 0.00027666
21 | 0.97664 | -0.16395 | 0.0042858 | 0.0010741
22 | 0.97657 | -0.16448 | 0.0070715 | 0.0017723
23 | 0.97582 | -0.16998 | 0 | 0
24 | 0.97803 | -0.15409 | 0.00069874 | 0.00017512
25 | 0.99625 | -0.025795 | 0 | 0
26 | 0.99383 | -0.042584 | 0 | 0
27 | 0.99968 | -0.0021776 | 0 | 0
28 | 0.98124 | -0.13113 | 0.00088233 | 0.00022113
29 | 0.97925 | -0.1453 | 0.00082673 | 0.0002072
30 | 0.97719 | -0.16 | 0.0005342 | 0.00013388
31 | 0.9765 | -0.16499 | 0.0041718 | 0.0010456
32 | 0.98869 | -0.078434 | 0.00060906 | 0.00015264
33 | 0.97616 | -0.16741 | 0 | 0
34 | 0.97579 | -0.1702 | 0 | 0
35 | 0.97582 | -0.17 | 0.0002252 | 5.644e-05
36 | 0.97819 | -0.15291 | 0.0020861 | 0.00052284
37 | 0.97826 | -0.15237 | 0.006669 | 0.0016714
38 | 0.97853 | -0.15046 | 0 | 0
39 | 0.97841 | -0.15129 | 0.00086403 | 0.00021655
40 | 0.97846 | -0.15099 | 0.00095653 | 0.00023973
41 | 0.97572 | -0.17073 | 0.00064268 | 0.00016107
42 | 0.97552 | -0.17213 | 0.00017118 | 4.2903e-05
43 | 0.97559 | -0.17167 | 0.0012255 | 0.00030715
44 | 0.97486 | -0.17693 | 0.00046967 | 0.00011771
45 | 0.97467 | -0.17829 | 0.002748 | 0.00068872
46 | 0.9784 | -0.15139 | 0.0011481 | 0.00028773
47 | 0.97845 | -0.151 | 0.00060631 | 0.00015196
48 | 0.97831 | -0.15207 | 0 | 0
49 | 0.97825 | -0.15248 | 0.0013071 | 0.00032759
50 | 0.97828 | -0.15225 | 0.00044511 | 0.00011155
51 | 0.98361 | -0.11429 | 0.0013176 | 0.00033023
52 | 0.98565 | -0.099839 | 0.00090975 | 0.00022801
53 | 0.9871 | -0.089658 | 0 | 0
54 | 0.9782 | -0.15281 | 0.00045593 | 0.00011427
55 | 0.97821 | -0.15275 | 0 | 0
56 | 0.99219 | -0.054362 | 0 | 0
57 | 0.99025 | -0.067955 | 0.024821 | 0.0062206
58 | 0.99408 | -0.041149 | 0 | 0
59 | 0.99961 | -0.0026874 | 0.007448 | 0.0018666
60 | 1 | 0 | -0.22546 | -0.056744
61 | 0.97818 | -0.15294 | 0.00065424 | 0.00016397
62 | 0.97817 | -0.15307 | 0.00059963 | 0.00015028
63 | 0.97826 | -0.15241 | 0.00049275 | 0.00012349
64 | 0.97827 | -0.15233 | 0.00044511 | 0.00011155
65 | 0.98665 | -0.093372 | 0 | 0
66 | 0.98562 | -0.10064 | 0.012437 | 0.003117
67 | 0.98733 | -0.088567 | 0 | 0
68 | 0.98357 | -0.1152 | 0.0046529 | 0.0011661
69 | 0.98367 | -0.11447 | 0 | 0
70 | 0.9976 | -0.016614 | 0.0028213 | 0.00070709
71 | 0.99043 | -0.066764 | 0.0019058 | 0.00047764
72 | 0.97718 | -0.16012 | 0.0006408 | 0.0001606
73 | 0.9837 | -0.11428 | 0 | 0
74 | 0.98421 | -0.11063 | 0.0094485 | 0.002368
75 | 0.98089 | -0.13425 | 0 | 0
76 | 0.9788 | -0.14916 | 0.010541 | 0.0026419
77 | 0.9864 | -0.095176 | 0 | 0
78 | 0.98564 | -0.10052 | 0 | 0
79 | 0.98614 | -0.096966 | 0.011687 | 0.0029289
80 | 0.98493 | -0.1056 | 0 | 0
81 | 0.98523 | -0.10346 | 0 | 0
82 | 0.9786 | -0.15059 | 0.0070934 | 0.0017778
83 | 0.98454 | -0.10837 | 0.014283 | 0.0035796
84 | 0.98514 | -0.10412 | 0.0035193 | 0.00088201
85 | 0.98491 | -0.1057 | 0.0014655 | 0.00036729
86 | 0.97599 | -0.16865 | 0.0021599 | 0.00054133
87 | 0.9758 | -0.16998 | 0.003803 | 0.00095313
88 | 0.97595 | -0.16896 | 0.0024995 | 0.00062642
89 | 0.9758 | -0.16999 | 0.001948 | 0.00048821
90 | 0.97584 | -0.16971 | 0.0024208 | 0.00060671
91 | 0.97584 | -0.16974 | 0.00062524 | 0.0001567
92 | 0.98728 | -0.089049 | 0.0022381 | 0.00056092
93 | 0.9863 | -0.095961 | 0.0026745 | 0.00067028
94 | 0.98755 | -0.087089 | 0.00168 | 0.00042104
95 | 0.98605 | -0.097711 | 0.0061101 | 0.0015313
96 | 0.98828 | -0.081912 | 0.001752 | 0.0004391
97 | 0.98535 | -0.10269 | 0.0020066 | 0.00050289
98 | 0.98855 | -0.080031 | 0.0022531 | 0.00056467
99 | 0.98462 | -0.10793 | 0.0026513 | 0.00066449
100 | 0.98933 | -0.074542 | 0.0016069 | 0.00040273
101 | 0.98454 | -0.1085 | 0 | 0
102 | 0.9903 | -0.067677 | 0.0052309 | 0.001311
103 | 0.98438 | -0.10952 | 0.0017362 | 0.00043514
104 | 0.98422 | -0.11064 | 0.0043164 | 0.0010818
105 | 0.98441 | -0.10942 | 0.0028055 | 0.00070313
106 | 0.98449 | -0.10882 | 0.0019537 | 0.00048965
107 | 0.98427 | -0.11037 | 0.0019411 | 0.0004865
108 | 0.9842 | -0.11087 | 0.0012432 | 0.00031157
109 | 0.98418 | -0.11106 | 0.001104 | 0.00027669
110 | 0.98416 | -0.11121 | 0.00072089 | 0.00018067
111 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0016581 | 0.00041477 | -0.001658 | -0.00041502 | 8.7823e-08 | -2.4268e-07 | 0.0025249 | 0.002525 | 0.002525 | 0.97704 | -0.16119 | 0.97699 | -0.16157 | 0.93519
1 | -0.0018105 | -0.00045299 | 0.0018107 | 0.0004527 | 1.258e-07 | -2.8379e-07 | 0.0027571 | 0.002757 | 0.0027571 | 0.97704 | -0.16119 | 0.97711 | -0.16068 | 1.0212
2 | 0.0013463 | 0.0003369 | -0.0013463 | -0.00033701 | 2.358e-08 | -1.0349e-07 | 0.0020503 | 0.0020504 | 0.0020504 | 0.97699 | -0.16157 | 0.97697 | -0.1617 | 0.75939
3 | -0.0022567 | -0.00056376 | 0.0022568 | 0.00056367 | 7.1954e-08 | -9.4667e-08 | 0.003436 | 0.003436 | 0.003436 | 0.97711 | -0.16068 | 0.97714 | -0.16045 | 1.2726
4 | 0.00044605 | 0.00011106 | -0.00044603 | -0.00011179 | 1.6814e-08 | -7.2526e-07 | 0.00067901 | 0.00067928 | 0.00067928 | 0.97711 | -0.16068 | 0.97707 | -0.16096 | 0.25158
5 | 0.0011893 | 0.00029766 | -0.0011892 | -0.00029777 | 1.9903e-08 | -1.1409e-07 | 0.0018112 | 0.0018112 | 0.0018112 | 0.97697 | -0.1617 | 0.97695 | -0.16182 | 0.67083
6 | -0.0085669 | -0.0021403 | 0.0085672 | 0.0021404 | 3.0822e-07 | 8.2178e-08 | 0.013043 | 0.013043 | 0.013043 | 0.97714 | -0.16045 | 0.97718 | -0.16019 | 4.8309
7 | 0.0063101 | 0.0015766 | -0.006309 | -0.0015764 | 1.1261e-06 | 1.8825e-07 | 0.0096075 | 0.0096075 | 0.0096075 | 0.97714 | -0.16045 | 0.97696 | -0.16175 | 3.5583
8 | 0.00030815 | 7.6949e-05 | -0.00030815 | -7.7227e-05 | 3.06e-09 | -2.7762e-07 | 0.00046925 | 0.00046935 | 0.00046935 | 0.97695 | -0.16182 | 0.97694 | -0.16189 | 0.17383
9 | -0.008747 | -0.0021854 | 0.0087496 | 0.0021862 | 2.6128e-06 | 7.0906e-07 | 0.013317 | 0.013317 | 0.013317 | 0.97718 | -0.16019 | 0.97748 | -0.15802 | 4.9323
10 | 0.006123 | 0.0015298 | -0.0061219 | -0.0015297 | 1.0146e-06 | 1.5609e-07 | 0.0093242 | 0.0093243 | 0.0093243 | 0.97696 | -0.16175 | 0.97679 | -0.16295 | 3.4534
11 | 0.00015839 | 3.9693e-05 | -0.00015839 | -3.9695e-05 | 6.8398e-12 | -2.3582e-09 | 0.00024124 | 0.00024124 | 0.00024124 | 0.97694 | -0.16189 | 0.97694 | -0.16189 | 0.089349
12 | -0.010279 | -0.0025695 | 0.010281 | 0.00257 | 1.8279e-06 | 5.5301e-07 | 0.015645 | 0.015645 | 0.015645 | 0.97748 | -0.15802 | 0.97766 | -0.15673 | 5.7946
13 | 0.0061219 | 0.0015297 | -0.0061211 | -0.0015295 | 8.2599e-07 | 1.2714e-07 | 0.0093243 | 0.0093244 | 0.0093244 | 0.97679 | -0.16295 | 0.97666 | -0.16393 | 3.4535
14 | -0.010843 | -0.0027108 | 0.010847 | 0.0027121 | 3.9481e-06 | 1.227e-06 | 0.016501 | 0.0165 | 0.016501 | 0.97766 | -0.15673 | 0.97803 | -0.15409 | 6.1113
15 | 0.005843 | 0.0014598 | -0.0058403 | -0.0014595 | 2.7116e-06 | 3.5684e-07 | 0.0089007 | 0.0089009 | 0.0089009 | 0.97666 | -0.16393 | 0.97619 | -0.16731 | 3.2966
16 | 0.0054883 | 0.0013713 | -0.0054863 | -0.0013711 | 2.0165e-06 | 1.9835e-07 | 0.0083644 | 0.0083646 | 0.0083646 | 0.97619 | -0.16731 | 0.97582 | -0.16998 | 3.098
17 | 0.012466 | 0.0031188 | -0.012459 | -0.0031165 | 7.0082e-06 | 2.3021e-06 | 0.018944 | 0.018944 | 0.018944 | 0.97907 | -0.14657 | 0.9785 | -0.15064 | 7.0163
18 | 0.03135 | 0.0078647 | -0.031295 | -0.0078439 | 5.5504e-05 | 2.0856e-05 | 0.047649 | 0.04765 | 0.04765 | 0.97907 | -0.14657 | 0.97728 | -0.15935 | 17.648
19 | -0.043816 | -0.010984 | 0.043855 | 0.010998 | 3.9013e-05 | 1.4827e-05 | 0.066593 | 0.066593 | 0.066593 | 0.97907 | -0.14657 | 0.97997 | -0.14014 | 24.6642
20 | 0.011551 | 0.0028889 | -0.011545 | -0.0028872 | 5.4788e-06 | 1.7499e-06 | 0.017563 | 0.017564 | 0.017564 | 0.9785 | -0.15064 | 0.97803 | -0.15409 | 6.505
21 | 0.0022791 | 0.00057053 | -0.0022789 | -0.0005707 | 1.2836e-07 | -1.6468e-07 | 0.0034699 | 0.00347 | 0.00347 | 0.97728 | -0.15935 | 0.97723 | -0.15976 | 1.2852
22 | 0.0084637 | 0.002121 | -0.0084583 | -0.0021196 | 5.3835e-06 | 1.4201e-06 | 0.012887 | 0.012887 | 0.012887 | 0.97728 | -0.15935 | 0.97664 | -0.16395 | 4.773
23 | 0.020552 | 0.0051523 | -0.020537 | -0.005147 | 1.4585e-05 | 5.3107e-06 | 0.031293 | 0.031293 | 0.031293 | 0.97728 | -0.15935 | 0.97657 | -0.16448 | 11.59
24 | -0.06144 | -0.015406 | 0.061517 | 0.015435 | 7.6827e-05 | 2.937e-05 | 0.093295 | 0.093295 | 0.093295 | 0.97997 | -0.14014 | 0.98124 | -0.13113 | 34.5539
25 | 0.017585 | 0.0044076 | -0.017573 | -0.0044032 | 1.2539e-05 | 4.468e-06 | 0.026702 | 0.026702 | 0.026702 | 0.97997 | -0.14014 | 0.97925 | -0.1453 | 9.8897
26 | 0.001175 | 0.00029403 | -0.001175 | -0.00029426 | 3.8828e-08 | -2.2861e-07 | 0.0017891 | 0.0017892 | 0.0017892 | 0.97723 | -0.15976 | 0.97719 | -0.16 | 0.66265
27 | 0.0041724 | 0.0010455 | -0.0041718 | -0.0010456 | 5.9851e-07 | -6.6755e-08 | 0.0063571 | 0.0063572 | 0.0063572 | 0.97664 | -0.16395 | 0.9765 | -0.16499 | 2.3545
28 | 0.013466 | 0.0033747 | -0.01346 | -0.0033729 | 5.4549e-06 | 1.8384e-06 | 0.020518 | 0.020518 | 0.020518 | 0.97657 | -0.16448 | 0.97616 | -0.16741 | 7.5993
29 | 0.0052611 | 0.0013148 | -0.005261 | -0.0013148 | 1.6228e-07 | 1.1922e-08 | 0.0080213 | 0.0080213 | 0.0080213 | 0.97582 | -0.16998 | 0.97579 | -0.1702 | 2.9708
30 | 0.0002252 | 5.63e-05 | -0.0002252 | -5.644e-05 | 8.2435e-10 | -1.3965e-07 | 0.00034335 | 0.0003434 | 0.0003434 | 0.97582 | -0.16998 | 0.97582 | -0.17 | 0.12719
31 | 0.066192 | 0.016733 | -0.066036 | -0.016673 | 0.00015616 | 5.9729e-05 | 0.098916 | 0.098916 | 0.098916 | 0.99625 | -0.025795 | 0.99383 | -0.042584 | 36.6356
32 | -0.066192 | -0.016733 | 0.066413 | 0.016818 | 0.00022096 | 8.4513e-05 | 0.098916 | 0.098916 | 0.098916 | 0.99625 | -0.025795 | 0.99968 | -0.0021776 | 36.6356
33 | 0.066036 | 0.016673 | -0.065705 | -0.016547 | 0.00033096 | 0.00012659 | 0.098916 | 0.098916 | 0.098916 | 0.99383 | -0.042584 | 0.98869 | -0.078434 | 36.6357
34 | 0.0074485 | 0.0018667 | -0.007448 | -0.0018666 | 5.2557e-07 | 1.1231e-07 | 0.011087 | 0.011087 | 0.011087 | 0.99968 | -0.0021776 | 0.99961 | -0.0026874 | 4.1063
35 | -0.073861 | -0.018684 | 0.073884 | 0.018693 | 2.2695e-05 | 8.6894e-06 | 0.11 | 0.11 | 0.11 | 0.99968 | -0.0021776 | 1 | 0 | 40.7418
36 | -0.0624 | -0.015656 | 0.062546 | 0.015712 | 0.00014617 | 5.5888e-05 | 0.094633 | 0.094633 | 0.094633 | 0.98124 | -0.13113 | 0.98361 | -0.11429 | 35.0494
37 | 0.016746 | 0.004196 | -0.016734 | -0.0041917 | 1.1952e-05 | 4.2252e-06 | 0.025446 | 0.025446 | 0.025446 | 0.97925 | -0.1453 | 0.97853 | -0.15046 | 9.4245
38 | 0.00064081 | 0.00016038 | -0.0006408 | -0.0001606 | 1.0713e-08 | -2.2178e-07 | 0.00097571 | 0.00097579 | 0.00097579 | 0.97719 | -0.16 | 0.97718 | -0.16012 | 0.3614
39 | 0.065096 | 0.016394 | -0.064994 | -0.016355 | 0.00010197 | 3.9003e-05 | 0.098 | 0.098 | 0.098 | 0.98869 | -0.078434 | 0.9871 | -0.089658 | 36.2962
40 | 0.0077073 | 0.0019313 | -0.007706 | -0.001931 | 1.3224e-06 | 3.1671e-07 | 0.011749 | 0.011749 | 0.011749 | 0.97616 | -0.16741 | 0.97599 | -0.16865 | 4.3513
41 | 0.0057531 | 0.0014416 | -0.005751 | -0.0014413 | 2.0468e-06 | 2.5426e-07 | 0.0087696 | 0.0087698 | 0.0087698 | 0.97616 | -0.16741 | 0.9758 | -0.16998 | 3.2481
42 | 0.0018685 | 0.00046708 | -0.0018684 | -0.00046736 | 1.3547e-07 | -2.8198e-07 | 0.0028489 | 0.0028491 | 0.0028491 | 0.97579 | -0.1702 | 0.97572 | -0.17073 | 1.0552
43 | 0.0033924 | 0.00084767 | -0.0033915 | -0.000848 | 8.9943e-07 | -3.2688e-07 | 0.0051723 | 0.0051726 | 0.0051726 | 0.97579 | -0.1702 | 0.97552 | -0.17213 | 1.9158
44 | -0.0020861 | -0.00052284 | 0.0020863 | 0.00052258 | 1.5658e-07 | -2.526e-07 | 0.0031734 | 0.0031733 | 0.0031734 | 0.97819 | -0.15291 | 0.97826 | -0.15237 | 1.1753
45 | -0.0087553 | -0.002194 | 0.0087576 | 0.0021946 | 2.3155e-06 | 6.2781e-07 | 0.013317 | 0.013317 | 0.013317 | 0.97826 | -0.15237 | 0.97853 | -0.15046 | 4.9324
46 | 0.0064135 | 0.0016058 | -0.0064128 | -0.0016057 | 7.3651e-07 | 1.2739e-07 | 0.0097522 | 0.0097523 | 0.0097523 | 0.97853 | -0.15046 | 0.97841 | -0.15129 | 3.612
47 | 0.001563 | 0.0003913 | -0.0015628 | -0.00039167 | 1.1525e-07 | -3.664e-07 | 0.0023766 | 0.0023767 | 0.0023767 | 0.97853 | -0.15046 | 0.97846 | -0.15099 | 0.88027
48 | 0.0055487 | 0.0013891 | -0.0055487 | -0.0013891 | 7.4887e-08 | 7.6353e-09 | 0.0084382 | 0.0084382 | 0.0084382 | 0.97841 | -0.15129 | 0.9784 | -0.15139 | 3.1253
49 | 0.00060631 | 0.00015194 | -0.00060631 | -0.00015196 | 7.8056e-10 | -1.8179e-08 | 0.00092206 | 0.00092206 | 0.00092206 | 0.97846 | -0.15099 | 0.97845 | -0.151 | 0.3415
50 | 0.0012257 | 0.00030629 | -0.0012255 | -0.00030715 | 1.603e-07 | -8.5667e-07 | 0.0018689 | 0.0018693 | 0.0018693 | 0.97572 | -0.17073 | 0.97559 | -0.17167 | 0.69232
51 | 0.0032204 | 0.0008051 | -0.0032182 | -0.00080605 | 2.1356e-06 | -9.485e-07 | 0.0049115 | 0.0049121 | 0.0049121 | 0.97552 | -0.17213 | 0.97486 | -0.17693 | 1.8193
52 | 0.0027486 | 0.00068834 | -0.002748 | -0.00068872 | 5.1536e-07 | -3.8672e-07 | 0.0041952 | 0.0041954 | 0.0041954 | 0.97486 | -0.17693 | 0.97467 | -0.17829 | 1.5539
53 | 0.0044006 | 0.0011014 | -0.0044002 | -0.0011014 | 4.1274e-07 | -2.6716e-08 | 0.0066922 | 0.0066922 | 0.0066922 | 0.9784 | -0.15139 | 0.97831 | -0.15207 | 2.4786
54 | 0.0030172 | 0.00075527 | -0.003017 | -0.00075537 | 1.7199e-07 | -9.819e-08 | 0.0045888 | 0.0045889 | 0.0045889 | 0.97831 | -0.15207 | 0.97825 | -0.15248 | 1.6996
55 | 0.001383 | 0.00034616 | -0.001383 | -0.0003463 | 3.5698e-08 | -1.4862e-07 | 0.0021034 | 0.0021035 | 0.0021035 | 0.97831 | -0.15207 | 0.97828 | -0.15225 | 0.77906
56 | 0.0017099 | 0.00042778 | -0.0017098 | -0.00042795 | 6.4089e-08 | -1.6599e-07 | 0.0026007 | 0.0026007 | 0.0026007 | 0.97825 | -0.15248 | 0.97821 | -0.15275 | 0.96324
57 | 0.00093787 | 0.00023475 | -0.00093786 | -0.00023484 | 9.3082e-09 | -8.8464e-08 | 0.0014264 | 0.0014265 | 0.0014265 | 0.97828 | -0.15225 | 0.97827 | -0.15233 | 0.52832
58 | -0.063863 | -0.016043 | 0.063992 | 0.016092 | 0.00012861 | 4.9185e-05 | 0.096627 | 0.096627 | 0.096627 | 0.98361 | -0.11429 | 0.98565 | -0.099839 | 35.7876
59 | -0.064902 | -0.01632 | 0.064994 | 0.016355 | 9.2217e-05 | 3.5272e-05 | 0.098 | 0.098 | 0.098 | 0.98565 | -0.099839 | 0.9871 | -0.089658 | 36.2963
60 | -0.00045593 | -0.00011427 | 0.00045594 | 0.00011412 | 3.4449e-09 | -1.4277e-07 | 0.00069355 | 0.0006935 | 0.00069355 | 0.9782 | -0.15281 | 0.97821 | -0.15275 | 0.25687
61 | 0.0012539 | 0.00031383 | -0.0012539 | -0.00031399 | 3.2908e-08 | -1.6933e-07 | 0.0019072 | 0.0019073 | 0.0019073 | 0.97821 | -0.15275 | 0.97818 | -0.15294 | 0.70641
62 | 0.10674 | 0.026841 | -0.10653 | -0.026764 | 0.00020183 | 7.6975e-05 | 0.16011 | 0.16011 | 0.16011 | 0.99219 | -0.054362 | 0.99025 | -0.067955 | 29.6496
63 | -0.10674 | -0.026841 | 0.10693 | 0.026916 | 0.00019693 | 7.5103e-05 | 0.16011 | 0.16011 | 0.16011 | 0.99219 | -0.054362 | 0.99408 | -0.041149 | 29.6496
64 | 0.081714 | 0.020544 | -0.08148 | -0.020454 | 0.00023395 | 8.966e-05 | 0.12281 | 0.12281 | 0.12281 | 0.99025 | -0.067955 | 0.98733 | -0.088567 | 45.4856
65 | -0.1471 | -0.037016 | 0.1476 | 0.037209 | 0.00050549 | 0.00019355 | 0.22024 | 0.22024 | 0.22024 | 0.99408 | -0.041149 | 0.9976 | -0.016614 | 40.7851
66 | 0.040164 | 0.0101 | -0.040021 | -0.010045 | 0.00014286 | 5.4128e-05 | 0.060132 | 0.060132 | 0.060132 | 0.99408 | -0.041149 | 0.99043 | -0.066764 | 22.2712
67 | 0.15077 | 0.038051 | -0.15042 | -0.037916 | 0.00035081 | 0.00013434 | 0.22445 | 0.22445 | 0.22445 | 1 | 0 | 0.9976 | -0.016614 | 41.5643
68 | 0.00059964 | 0.00015003 | -0.00059963 | -0.00015028 | 1.0616e-08 | -2.5262e-07 | 0.00091208 | 0.00091217 | 0.00091217 | 0.97818 | -0.15294 | 0.97817 | -0.15307 | 0.33784
69 | -0.00049275 | -0.00012349 | 0.00049275 | 0.00012328 | 5.9205e-09 | -2.098e-07 | 0.00074951 | 0.00074943 | 0.00074951 | 0.97826 | -0.15241 | 0.97827 | -0.15233 | 0.2776
70 | 0.044361 | 0.011139 | -0.044316 | -0.011122 | 4.474e-05 | 1.7003e-05 | 0.066911 | 0.066911 | 0.066911 | 0.98665 | -0.093372 | 0.98562 | -0.10064 | 24.7819
71 | -0.044361 | -0.011139 | 0.044391 | 0.011151 | 2.9638e-05 | 1.1264e-05 | 0.066911 | 0.066911 | 0.066911 | 0.98665 | -0.093372 | 0.98733 | -0.088567 | 24.7819
72 | 0.031879 | 0.0080054 | -0.031835 | -0.0079888 | 4.4237e-05 | 1.6625e-05 | 0.048135 | 0.048135 | 0.048135 | 0.98562 | -0.10064 | 0.98421 | -0.11063 | 17.8277
73 | 0.037089 | 0.0093032 | -0.037055 | -0.0092904 | 3.3959e-05 | 1.2839e-05 | 0.0559 | 0.0559 | 0.0559 | 0.98733 | -0.088567 | 0.9864 | -0.095176 | 20.7037
74 | -0.0046529 | -0.0011661 | 0.0046533 | 0.0011661 | 4.645e-07 | -1.2033e-08 | 0.0070392 | 0.0070392 | 0.0070392 | 0.98357 | -0.1152 | 0.98367 | -0.11447 | 2.6071
75 | -0.0046533 | -0.0011661 | 0.0046535 | 0.0011661 | 1.2448e-07 | -3.2319e-09 | 0.0070392 | 0.0070391 | 0.0070392 | 0.98367 | -0.11447 | 0.9837 | -0.11428 | 2.6071
76 | 0.038115 | 0.0095678 | -0.03811 | -0.009566 | 4.8347e-06 | 1.8291e-06 | 0.057269 | 0.057269 | 0.057269 | 0.99043 | -0.066764 | 0.9903 | -0.067677 | 21.2107
77 | -0.022375 | -0.0056166 | 0.022387 | 0.0056208 | 1.1337e-05 | 4.159e-06 | 0.03385 | 0.03385 | 0.03385 | 0.9837 | -0.11428 | 0.98421 | -0.11063 | 12.537
78 | 0.017722 | 0.0044505 | -0.017673 | -0.004433 | 4.9055e-05 | 1.7483e-05 | 0.026811 | 0.026811 | 0.026811 | 0.9837 | -0.11428 | 0.98089 | -0.13425 | 9.9301
79 | 0.017673 | 0.004433 | -0.017636 | -0.00442 | 3.649e-05 | 1.301e-05 | 0.026811 | 0.026812 | 0.026812 | 0.98089 | -0.13425 | 0.9788 | -0.14916 | 9.9302
80 | 0.0070948 | 0.0017781 | -0.0070934 | -0.0017778 | 1.4038e-06 | 2.9693e-07 | 0.010786 | 0.010786 | 0.010786 | 0.9788 | -0.14916 | 0.9786 | -0.15059 | 3.9948
81 | 0.037055 | 0.0092904 | -0.037046 | -0.0092869 | 9.1879e-06 | 3.4737e-06 | 0.0559 | 0.0559 | 0.0559 | 0.9864 | -0.095176 | 0.98614 | -0.096966 | 20.7037
82 | -0.025347 | -0.0063533 | 0.025359 | 0.006358 | 1.2496e-05 | 4.6317e-06 | 0.038266 | 0.038266 | 0.038266 | 0.98564 | -0.10052 | 0.98614 | -0.096966 | 14.1726
83 | 0.014298 | 0.0035849 | -0.014288 | -0.0035815 | 1.0053e-05 | 3.4261e-06 | 0.021587 | 0.021587 | 0.021587 | 0.98564 | -0.10052 | 0.98493 | -0.1056 | 7.9951
84 | 0.011048 | 0.0027684 | -0.011044 | -0.002767 | 4.4863e-06 | 1.3963e-06 | 0.016679 | 0.01668 | 0.01668 | 0.98564 | -0.10052 | 0.98523 | -0.10346 | 6.1776
85 | 0.014288 | 0.0035815 | -0.014283 | -0.0035796 | 5.479e-06 | 1.8676e-06 | 0.021587 | 0.021587 | 0.021587 | 0.98493 | -0.1056 | 0.98454 | -0.10837 | 7.9951
86 | 0.0035196 | 0.0008819 | -0.0035193 | -0.00088201 | 3.2268e-07 | -1.0892e-07 | 0.0053156 | 0.0053157 | 0.0053157 | 0.98523 | -0.10346 | 0.98514 | -0.10412 | 1.9688
87 | 0.0075243 | 0.0018851 | -0.007522 | -0.0018846 | 2.3326e-06 | 5.2865e-07 | 0.011364 | 0.011364 | 0.011364 | 0.98523 | -0.10346 | 0.98491 | -0.1057 | 4.2089
88 | 0.0060565 | 0.0015173 | -0.0060533 | -0.0015169 | 3.1979e-06 | 4.5139e-07 | 0.00915 | 0.0091503 | 0.0091503 | 0.98491 | -0.1057 | 0.98438 | -0.10952 | 3.389
89 | 0.005546 | 0.0013896 | -0.0055458 | -0.0013896 | 2.3744e-07 | 2.4816e-08 | 0.0084555 | 0.0084555 | 0.0084555 | 0.97599 | -0.16865 | 0.97595 | -0.16896 | 3.1317
90 | 0.001948 | 0.00048821 | -0.001948 | -0.00048821 | 2.9629e-09 | -5.5823e-09 | 0.0029705 | 0.0029705 | 0.0029705 | 0.9758 | -0.16998 | 0.9758 | -0.16999 | 1.1002
91 | 0.0030463 | 0.00076319 | -0.003046 | -0.00076336 | 3.179e-07 | -1.7279e-07 | 0.0046446 | 0.0046447 | 0.0046447 | 0.97595 | -0.16896 | 0.97584 | -0.16971 | 1.7203
92 | 0.00062524 | 0.00015665 | -0.00062524 | -0.0001567 | 2.1849e-09 | -4.7285e-08 | 0.00095338 | 0.0009534 | 0.0009534 | 0.97584 | -0.16971 | 0.97584 | -0.16974 | 0.35311
93 | 0.02326 | 0.0058331 | -0.023238 | -0.0058249 | 2.2264e-05 | 8.1921e-06 | 0.035059 | 0.035059 | 0.035059 | 0.98728 | -0.089049 | 0.9863 | -0.095961 | 12.9847
94 | -0.025498 | -0.0063941 | 0.025505 | 0.0063966 | 6.9287e-06 | 2.5687e-06 | 0.038432 | 0.038432 | 0.038432 | 0.98728 | -0.089049 | 0.98755 | -0.087089 | 14.234
95 | 0.020563 | 0.0051547 | -0.020558 | -0.0051528 | 4.9825e-06 | 1.8105e-06 | 0.031024 | 0.031024 | 0.031024 | 0.9863 | -0.095961 | 0.98605 | -0.097711 | 11.4903
96 | -0.027185 | -0.0068177 | 0.027204 | 0.0068249 | 1.9522e-05 | 7.2696e-06 | 0.040963 | 0.040963 | 0.040963 | 0.98755 | -0.087089 | 0.98828 | -0.081912 | 15.1715
97 | 0.014448 | 0.0036215 | -0.014438 | -0.0036181 | 9.9559e-06 | 3.4014e-06 | 0.021803 | 0.021803 | 0.021803 | 0.98605 | -0.097711 | 0.98535 | -0.10269 | 8.0753
98 | -0.028956 | -0.007264 | 0.028964 | 0.0072669 | 7.5586e-06 | 2.8255e-06 | 0.043601 | 0.043601 | 0.043601 | 0.98828 | -0.081912 | 0.98855 | -0.080031 | 16.1485
99 | 0.012432 | 0.0031152 | -0.012423 | -0.0031123 | 9.0089e-06 | 2.9436e-06 | 0.018773 | 0.018773 | 0.018773 | 0.98535 | -0.10269 | 0.98462 | -0.10793 | 6.9531
100 | -0.031217 | -0.0078315 | 0.031241 | 0.0078404 | 2.3784e-05 | 8.9263e-06 | 0.046992 | 0.046992 | 0.046992 | 0.98855 | -0.080031 | 0.98933 | -0.074542 | 17.4046
101 | 0.0097712 | 0.0024478 | -0.0097705 | -0.0024476 | 7.7493e-07 | 2.2562e-07 | 0.014767 | 0.014767 | 0.014767 | 0.98462 | -0.10793 | 0.98454 | -0.1085 | 5.4691
102 | -0.032848 | -0.0082432 | 0.032879 | 0.008255 | 3.1328e-05 | 1.1785e-05 | 0.049409 | 0.049409 | 0.049409 | 0.98933 | -0.074542 | 0.9903 | -0.067677 | 18.2997
103 | 0.0069646 | 0.0017447 | -0.0069643 | -0.0017446 | 3.0414e-07 | 6.1038e-08 | 0.010526 | 0.010526 | 0.010526 | 0.98454 | -0.1085 | 0.98449 | -0.10882 | 3.8985
104 | 0.0028059 | 0.00070287 | -0.0028055 | -0.00070313 | 3.5594e-07 | -2.664e-07 | 0.0042407 | 0.0042408 | 0.0042408 | 0.98454 | -0.1085 | 0.98441 | -0.10942 | 1.5707
105 | 0.0043171 | 0.0010817 | -0.0043164 | -0.0010818 | 6.6769e-07 | -6.2564e-08 | 0.0065257 | 0.0065258 | 0.0065258 | 0.98438 | -0.10952 | 0.98422 | -0.11064 | 2.417
106 | 0.0050105 | 0.001255 | -0.0050095 | -0.0012549 | 1.0759e-06 | 3.1609e-08 | 0.0075729 | 0.0075731 | 0.0075731 | 0.98449 | -0.10882 | 0.98427 | -0.11037 | 2.8048
107 | 0.0030683 | 0.00076845 | -0.0030681 | -0.00076857 | 2.1242e-07 | -1.1937e-07 | 0.0046385 | 0.0046386 | 0.0046386 | 0.98427 | -0.11037 | 0.9842 | -0.11087 | 1.718
108 | 0.001825 | 0.000457 | -0.0018249 | -0.00045711 | 4.775e-08 | -1.0938e-07 | 0.002759 | 0.0027591 | 0.0027591 | 0.9842 | -0.11087 | 0.98418 | -0.11106 | 1.0219
109 | 0.00072091 | 0.00018042 | -0.00072089 | -0.00018067 | 1.4801e-08 | -2.4803e-07 | 0.0010899 | 0.00109 | 0.00109 | 0.98418 | -0.11106 | 0.98416 | -0.11121 | 0.40369

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2279 | 0.057356

## res_load
| p_mw | q_mvar
0 | 0.00015247 | 3.8213e-05
1 | 0.00031168 | 7.8113e-05
2 | 0.00015702 | 3.9353e-05
3 | 0.00044603 | 0.00011179
4 | 0.00088108 | 0.00022082
5 | 0.00017982 | 4.5067e-05
6 | 0.00018602 | 4.6622e-05
7 | 0.00014976 | 3.7534e-05
8 | 0.0015294 | 0.00038331
9 | 0.00015839 | 3.9695e-05
10 | 0.0005619 | 0.00014083
11 | 0.00027808 | 6.9695e-05
12 | 0.00035198 | 8.8214e-05
13 | 0.00090791 | 0.00022754
14 | 0.0011039 | 0.00027666
15 | 0.0042858 | 0.0010741
16 | 0.0070715 | 0.0017723
17 | 0.00069874 | 0.00017512
18 | 0.00088233 | 0.00022113
19 | 0.00082673 | 0.0002072
20 | 0.0005342 | 0.00013388
21 | 0.0041718 | 0.0010456
22 | 0.00060906 | 0.00015264
23 | 0.0002252 | 5.644e-05
24 | 0.0020861 | 0.00052284
25 | 0.006669 | 0.0016714
26 | 0.00086403 | 0.00021655
27 | 0.00095653 | 0.00023973
28 | 0.00064268 | 0.00016107
29 | 0.00017118 | 4.2903e-05
30 | 0.0012255 | 0.00030715
31 | 0.00046967 | 0.00011771
32 | 0.002748 | 0.00068872
33 | 0.0011481 | 0.00028773
34 | 0.00060631 | 0.00015196
35 | 0.0013071 | 0.00032759
36 | 0.00044511 | 0.00011155
37 | 0.0013176 | 0.00033023
38 | 0.00090975 | 0.00022801
39 | 0.00045593 | 0.00011427
40 | 0.024821 | 0.0062206
41 | 0.007448 | 0.0018666
42 | 0.0024424 | 0.00061212
43 | 0.00065424 | 0.00016397
44 | 0.00059963 | 0.00015028
45 | 0.00049275 | 0.00012349
46 | 0.00044511 | 0.00011155
47 | 0.012437 | 0.003117
48 | 0.0046529 | 0.0011661
49 | 0.0028213 | 0.00070709
50 | 0.0019058 | 0.00047764
51 | 0.0006408 | 0.0001606
52 | 0.0094485 | 0.002368
53 | 0.010541 | 0.0026419
54 | 0.011687 | 0.0029289
55 | 0.0070934 | 0.0017778
56 | 0.014283 | 0.0035796
57 | 0.0035193 | 0.00088201
58 | 0.0014655 | 0.00036729
59 | 0.0021599 | 0.00054133
60 | 0.003803 | 0.00095313
61 | 0.0024995 | 0.00062642
62 | 0.001948 | 0.00048821
63 | 0.0024208 | 0.00060671
64 | 0.00062524 | 0.0001567
65 | 0.0022381 | 0.00056092
66 | 0.0026745 | 0.00067028
67 | 0.00168 | 0.00042104
68 | 0.0061101 | 0.0015313
69 | 0.001752 | 0.0004391
70 | 0.0020066 | 0.00050289
71 | 0.0022531 | 0.00056467
72 | 0.0026513 | 0.00066449
73 | 0.0016069 | 0.00040273
74 | 0.0052309 | 0.001311
75 | 0.0017362 | 0.00043514
76 | 0.0043164 | 0.0010818
77 | 0.0028055 | 0.00070313
78 | 0.0019537 | 0.00048965
79 | 0.0019411 | 0.0004865
80 | 0.0012432 | 0.00031157
81 | 0.001104 | 0.00027669
82 | 0.00072089 | 0.00018067

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1