## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1136-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1136-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1136-6_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1136-6_0_4_node_21 | 0.4 | n |  | TRUE
4 | bus_LV_1136-6_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1136-6_0_4_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1136-6_0_4_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1136-6_0_4_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_1136-6_0_4_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_1136-6_0_4_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1136-6_0_4_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1136-6_0_4_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_1136-6_0_4_node_20 | 0.4 | n |  | TRUE
13 | bus_LV_1136-6_0_4_node_3 | 0.4 | n |  | TRUE
14 | bus_LV_1136-6_0_4_node_4 | 0.4 | n |  | TRUE
15 | bus_LV_1136-6_0_4_node_5 | 0.4 | n |  | TRUE
16 | bus_LV_1136-6_0_4_node_110 | 0.4 | n |  | TRUE
17 | bus_LV_1136-6_0_4_node_99 | 0.4 | n |  | TRUE
18 | bus_LV_1136-6_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1136-6_0_4_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1136-6_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_1136-6_0_4_node_12 | 0.4 | n |  | TRUE
22 | bus_LV_1136-6_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_1136-6_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_1136-6_0_4_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_1136-6_0_4_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_1136-6_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1136-6_0_4_node_44 | 0.4 | n |  | TRUE
28 | bus_LV_1136-6_0_4_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_1136-6_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1136-6_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_1136-6_0_4_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1136-6_0_4_node_47 | 0.4 | n |  | TRUE
33 | bus_LV_1136-6_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1136-6_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_1136-6_0_4_node_32 | 0.4 | n |  | TRUE
36 | bus_LV_1136-6_0_4_node_115 | 0.4 | n |  | TRUE
37 | bus_LV_1136-6_0_4_node_67 | 0.4 | n |  | TRUE
38 | bus_LV_1136-6_0_4_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1136-6_0_4_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1136-6_0_4_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_1136-6_0_4_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_1136-6_0_4_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_1136-6_0_4_node_98 | 0.4 | n |  | TRUE
44 | bus_LV_1136-6_0_4_node_107 | 0.4 | n |  | TRUE
45 | bus_LV_1136-6_0_4_node_96 | 0.4 | n |  | TRUE
46 | bus_LV_1136-6_0_4_node_108 | 0.4 | n |  | TRUE
47 | bus_LV_1136-6_0_4_node_76 | 0.4 | n |  | TRUE
48 | bus_LV_1136-6_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_1136-6_0_4_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_1136-6_0_4_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_1136-6_0_4_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_1136-6_0_4_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_1136-6_0_4_node_43 | 0.4 | n |  | TRUE
54 | bus_LV_1136-6_0_4_node_101 | 0.4 | n |  | TRUE
55 | bus_LV_1136-6_0_4_node_88 | 0.4 | n |  | TRUE
56 | bus_LV_1136-6_0_4_node_113 | 0.4 | n |  | TRUE
57 | bus_LV_1136-6_0_4_node_100 | 0.4 | n |  | TRUE
58 | bus_LV_1136-6_0_4_node_89 | 0.4 | n |  | TRUE
59 | bus_LV_1136-6_0_4_node_95 | 0.4 | n |  | TRUE
60 | bus_LV_1136-6_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_1136-6_0_4_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_1136-6_0_4_node_48 | 0.4 | n |  | TRUE
63 | bus_LV_1136-6_0_4_node_60 | 0.4 | n |  | TRUE
64 | bus_LV_1136-6_0_4_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_1136-6_0_4_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_1136-6_0_4_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_1136-6_0_4_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_1136-6_0_4_node_52 | 0.4 | n |  | TRUE
69 | bus_LV_1136-6_0_4_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_1136-6_0_4_node_105 | 0.4 | n |  | TRUE
71 | bus_LV_1136-6_0_4_node_106 | 0.4 | n |  | TRUE
72 | bus_LV_1136-6_0_4_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_1136-6_0_4_node_69 | 0.4 | n |  | TRUE
74 | bus_LV_1136-6_0_4_node_55 | 0.4 | n |  | TRUE
75 | bus_LV_1136-6_0_4_node_56 | 0.4 | n |  | TRUE
76 | bus_LV_1136-6_0_4_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_1136-6_0_4_node_58 | 0.4 | n |  | TRUE
78 | bus_LV_1136-6_0_4_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_1136-6_0_4_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_1136-6_0_4_node_65 | 0.4 | n |  | TRUE
81 | bus_LV_1136-6_0_4_node_62 | 0.4 | n |  | TRUE
82 | bus_LV_1136-6_0_4_node_102 | 0.4 | n |  | TRUE
83 | bus_LV_1136-6_0_4_node_103 | 0.4 | n |  | TRUE
84 | bus_LV_1136-6_0_4_node_64 | 0.4 | n |  | TRUE
85 | bus_LV_1136-6_0_4_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_1136-6_0_4_node_71 | 0.4 | n |  | TRUE
87 | bus_LV_1136-6_0_4_node_114 | 0.4 | n |  | TRUE
88 | bus_LV_1136-6_0_4_node_70 | 0.4 | n |  | TRUE
89 | bus_LV_1136-6_0_4_node_83 | 0.4 | n |  | TRUE
90 | bus_LV_1136-6_0_4_node_84 | 0.4 | n |  | TRUE
91 | bus_LV_1136-6_0_4_node_72 | 0.4 | n |  | TRUE
92 | bus_LV_1136-6_0_4_node_73 | 0.4 | n |  | TRUE
93 | bus_LV_1136-6_0_4_node_74 | 0.4 | n |  | TRUE
94 | bus_LV_1136-6_0_4_node_75 | 0.4 | n |  | TRUE
95 | bus_LV_1136-6_0_4_node_77 | 0.4 | n |  | TRUE
96 | bus_LV_1136-6_0_4_node_109 | 0.4 | n |  | TRUE
97 | bus_LV_1136-6_0_4_node_111 | 0.4 | n |  | TRUE
98 | bus_LV_1136-6_0_4_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_1136-6_0_4_node_112 | 0.4 | n |  | TRUE
100 | bus_LV_1136-6_0_4_node_78 | 0.4 | n |  | TRUE
101 | bus_LV_1136-6_0_4_node_79 | 0.4 | n |  | TRUE
102 | bus_LV_1136-6_0_4_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_1136-6_0_4_node_81 | 0.4 | n |  | TRUE
104 | bus_LV_1136-6_0_4_node_82 | 0.4 | n |  | TRUE
105 | bus_LV_1136-6_0_4_node_85 | 0.4 | n |  | TRUE
106 | bus_LV_1136-6_0_4_node_86 | 0.4 | n |  | TRUE
107 | bus_LV_1136-6_0_4_node_87 | 0.4 | n |  | TRUE
108 | bus_LV_1136-6_0_4_node_90 | 0.4 | n |  | TRUE
109 | bus_LV_1136-6_0_4_node_91 | 0.4 | n |  | TRUE
110 | bus_LV_1136-6_0_4_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_1136-6_0_4_node_93 | 0.4 | n |  | TRUE
112 | bus_LV_1136-6_0_4_node_104 | 0.4 | n |  | TRUE
113 | bus_LV_1136-6_0_4_node_97 | 0.4 | n |  | TRUE
114 | bus_MV_124_0_node_104 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1136-6_0_4_load_0 | 0 | 0.00056793 | 0.00014234 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1136-6_0_4_load_1 | 1 | 0.00042678 | 0.00010696 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1136-6_0_4_load_2 | 2 | 0.00040357 | 0.00010114 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1136-6_0_4_load_21 | 3 | 0.0019516 | 0.00048912 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1136-6_0_4_load_7 | 4 | 0.0006981 | 0.00017496 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1136-6_0_4_load_8 | 5 | 0.001532 | 0.00038395 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1136-6_0_4_load_6 | 6 | 0.00029783 | 7.4643e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1136-6_0_4_load_22 | 7 | 0.00023435 | 5.8734e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1136-6_0_4_load_16 | 8 | 0.00031011 | 7.7722e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1136-6_0_4_load_23 | 9 | 0.0018406 | 0.00046129 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1136-6_0_4_load_14 | 10 | 0.0022874 | 0.00057327 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1136-6_0_4_load_15 | 11 | 0.00017204 | 4.3118e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1136-6_0_4_load_20 | 12 | 0.0018144 | 0.00045473 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1136-6_0_4_load_3 | 13 | 0.00042498 | 0.00010651 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1136-6_0_4_load_4 | 14 | 0.00019387 | 4.8588e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1136-6_0_4_load_110 | 16 | 0.00048555 | 0.00012169 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1136-6_0_4_load_99 | 17 | 0.0014902 | 0.00037347 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1136-6_0_4_load_10 | 18 | 0.00022644 | 5.6752e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1136-6_0_4_load_9 | 19 | 0.00042688 | 0.00010699 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1136-6_0_4_load_11 | 20 | 0.00026117 | 6.5454e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1136-6_0_4_load_12 | 21 | 0.00049129 | 0.00012313 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1136-6_0_4_load_24 | 22 | 0.00052568 | 0.00013175 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1136-6_0_4_load_13 | 23 | 0.0010203 | 0.00025572 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1136-6_0_4_load_17 | 25 | 0.0012041 | 0.00030178 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1136-6_0_4_load_44 | 27 | 0.00037006 | 9.2746e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1136-6_0_4_load_25 | 29 | 0.00086151 | 0.00021591 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1136-6_0_4_load_27 | 30 | 0.00025133 | 6.299e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1136-6_0_4_load_28 | 31 | 0.0016797 | 0.00042098 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1136-6_0_4_load_47 | 32 | 0.002689 | 0.00067393 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1136-6_0_4_load_30 | 34 | 0.0010771 | 0.00026995 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1136-6_0_4_load_32 | 35 | 0.001463 | 0.00036666 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1136-6_0_4_load_115 | 36 | 0.0050416 | 0.0012635 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1136-6_0_4_load_33 | 38 | 0.00079154 | 0.00019838 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1136-6_0_4_load_36 | 41 | 0.0037246 | 0.00093348 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1136-6_0_4_load_37 | 42 | 0.0064886 | 0.0016262 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1136-6_0_4_load_96 | 45 | 0.0014155 | 0.00035475 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1136-6_0_4_load_108 | 46 | 0.0018502 | 0.00046372 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1136-6_0_4_load_76 | 47 | 0.028141 | 0.0070529 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1136-6_0_4_load_38 | 48 | 0.0027016 | 0.00067709 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1136-6_0_4_load_39 | 49 | 0.0023319 | 0.00058443 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1136-6_0_4_load_42 | 52 | 0.0018061 | 0.00045265 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1136-6_0_4_load_101 | 54 | 0.0049927 | 0.0012513 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1136-6_0_4_load_88 | 55 | 0.0021346 | 0.00053498 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1136-6_0_4_load_113 | 56 | 0.0011258 | 0.00028214 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1136-6_0_4_load_100 | 57 | 0.0011951 | 0.00029953 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1136-6_0_4_load_89 | 58 | 0.0027668 | 0.00069343 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1136-6_0_4_load_95 | 59 | 0.00064494 | 0.00016164 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1136-6_0_4_load_45 | 60 | 0.00028508 | 7.1449e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1136-6_0_4_load_46 | 61 | 0.00030223 | 7.5747e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1136-6_0_4_load_48 | 62 | 0.00028668 | 7.1848e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1136-6_0_4_load_60 | 63 | 0.00022244 | 5.5749e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1136-6_0_4_load_61 | 64 | 0.00059866 | 0.00015004 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1136-6_0_4_load_49 | 65 | 0.0030132 | 0.00075517 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1136-6_0_4_load_50 | 66 | 0.0013676 | 0.00034276 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1136-6_0_4_load_52 | 68 | 0.0028561 | 0.00071581 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1136-6_0_4_load_54 | 69 | 0.0025357 | 0.0006355 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1136-6_0_4_load_105 | 70 | 0.0018082 | 0.00045318 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1136-6_0_4_load_106 | 71 | 0.0027782 | 0.00069627 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1136-6_0_4_load_68 | 72 | 0.001732 | 0.00043409 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1136-6_0_4_load_69 | 73 | 0.0015962 | 0.00040004 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1136-6_0_4_load_55 | 74 | 0.0029531 | 0.0007401 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1136-6_0_4_load_56 | 75 | 0.0016816 | 0.00042145 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1136-6_0_4_load_57 | 76 | 0.00243 | 0.00060902 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1136-6_0_4_load_58 | 77 | 0.0025683 | 0.00064368 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1136-6_0_4_load_59 | 78 | 0.0019706 | 0.00049387 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1136-6_0_4_load_65 | 80 | 0.0022843 | 0.0005725 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1136-6_0_4_load_62 | 81 | 0.0014667 | 0.00036759 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1136-6_0_4_load_102 | 82 | 0.0014126 | 0.00035402 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1136-6_0_4_load_103 | 83 | 0.00037715 | 9.4522e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1136-6_0_4_load_66 | 85 | 0.0020327 | 0.00050944 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1136-6_0_4_load_71 | 86 | 0.005441 | 0.0013637 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1136-6_0_4_load_114 | 87 | 0.0052122 | 0.0013063 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1136-6_0_4_load_70 | 88 | 0.0011372 | 0.00028501 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1136-6_0_4_load_83 | 89 | 0.0011348 | 0.0002844 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1136-6_0_4_load_84 | 90 | 0.0015475 | 0.00038783 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1136-6_0_4_load_72 | 91 | 0.013644 | 0.0034196 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1136-6_0_4_load_73 | 92 | 0.00061951 | 0.00015526 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1136-6_0_4_load_75 | 94 | 0.0063095 | 0.0015813 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1136-6_0_4_load_77 | 95 | 0.0018981 | 0.0004757 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1136-6_0_4_load_109 | 96 | 0.013425 | 0.0033646 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1136-6_0_4_load_111 | 97 | 0.0031774 | 0.00079634 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1136-6_0_4_load_112 | 99 | 0.0028034 | 0.00070261 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1136-6_0_4_load_78 | 100 | 0.0017614 | 0.00044146 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1136-6_0_4_load_79 | 101 | 0.003546 | 0.00088872 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1136-6_0_4_load_80 | 102 | 0.0038297 | 0.00095981 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1136-6_0_4_load_81 | 103 | 0.0027609 | 0.00069196 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1136-6_0_4_load_82 | 104 | 0.0027812 | 0.00069704 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1136-6_0_4_load_85 | 105 | 0.0028136 | 0.00070516 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1136-6_0_4_load_86 | 106 | 0.0014447 | 0.00036207 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1136-6_0_4_load_87 | 107 | 0.0030454 | 0.00076324 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1136-6_0_4_load_90 | 108 | 0.0024422 | 0.00061208 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1136-6_0_4_load_91 | 109 | 0.00022926 | 5.7458e-05 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1136-6_0_4_load_92 | 110 | 0.0033689 | 0.00084432 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1136-6_0_4_load_93 | 111 | 0.0035483 | 0.00088929 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1136-6_0_4_load_104 | 112 | 0.001265 | 0.00031704 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 42 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1136-6_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.0017211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1136-6_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.01392 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1136-6_0_4_line_2 | NAYY 4x150 SE | 0 | 3 | 0.23632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1136-6_0_4_line_3 | NAYY 4x150 SE | 1 | 4 | 0.14707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1136-6_0_4_line_4 | NAYY 4x150 SE | 3 | 7 | 0.27053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1136-6_0_4_line_5 | NAYY 4x150 SE | 3 | 8 | 0.11222 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1136-6_0_4_line_6 | NAYY 4x150 SE | 4 | 5 | 0.045255 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1136-6_0_4_line_7 | NAYY 4x150 SE | 4 | 6 | 0.13276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1136-6_0_4_line_8 | NAYY 4x150 SE | 5 | 19 | 0.013831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1136-6_0_4_line_9 | NAYY 4x150 SE | 7 | 9 | 0.038041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1136-6_0_4_line_10 | NAYY 4x150 SE | 8 | 11 | 0.010853 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1136-6_0_4_line_11 | NAYY 4x150 SE | 9 | 26 | 0.05862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1136-6_0_4_line_12 | NAYY 4x150 SE | 10 | 11 | 0.026261 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1136-6_0_4_line_13 | NAYY 4x150 SE | 10 | 12 | 0.35211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1136-6_0_4_line_14 | NAYY 4x150 SE | 12 | 24 | 0.015728 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1136-6_0_4_line_15 | NAYY 4x150 SE | 13 | 14 | 0.028796 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1136-6_0_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.011822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1136-6_0_4_line_17 | NAYY 4x150 SE | 15 | 18 | 0.061249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1136-6_0_4_line_18 | NAYY 4x150 SE | 15 | 19 | 0.018092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1136-6_0_4_line_19 | NAYY 4x150 SE | 16 | 17 | 0.084561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1136-6_0_4_line_20 | NAYY 4x150 SE | 17 | 113 | 0.048587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1136-6_0_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.10908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1136-6_0_4_line_22 | NAYY 4x150 SE | 20 | 21 | 0.0395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1136-6_0_4_line_23 | NAYY 4x150 SE | 21 | 22 | 0.09691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1136-6_0_4_line_24 | NAYY 4x150 SE | 23 | 24 | 0.18424 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1136-6_0_4_line_25 | NAYY 4x150 SE | 24 | 25 | 0.057603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1136-6_0_4_line_26 | NAYY 4x150 SE | 26 | 27 | 0.10219 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1136-6_0_4_line_27 | NAYY 4x150 SE | 26 | 28 | 0.19129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1136-6_0_4_line_28 | NAYY 4x150 SE | 27 | 32 | 0.01181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1136-6_0_4_line_29 | NAYY 4x150 SE | 28 | 31 | 0.033576 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1136-6_0_4_line_30 | NAYY 4x150 SE | 29 | 30 | 0.35337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1136-6_0_4_line_31 | NAYY 4x150 SE | 30 | 31 | 0.034319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1136-6_0_4_line_32 | NAYY 4x150 SE | 31 | 33 | 0.15511 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1136-6_0_4_line_33 | NAYY 4x150 SE | 32 | 60 | 0.075926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1136-6_0_4_line_34 | NAYY 4x150 SE | 33 | 34 | 0.05735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1136-6_0_4_line_35 | NAYY 4x150 SE | 35 | 36 | 0.14602 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1136-6_0_4_line_36 | NAYY 4x150 SE | 36 | 37 | 0.030539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1136-6_0_4_line_37 | NAYY 4x150 SE | 37 | 87 | 0.035864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1136-6_0_4_line_38 | NAYY 4x150 SE | 37 | 84 | 0.008712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1136-6_0_4_line_39 | NAYY 4x150 SE | 38 | 39 | 0.015785 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1136-6_0_4_line_40 | NAYY 4x150 SE | 38 | 40 | 0.0013671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1136-6_0_4_line_41 | NAYY 4x150 SE | 39 | 41 | 0.022801 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1136-6_0_4_line_42 | NAYY 4x150 SE | 40 | 42 | 0.030068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1136-6_0_4_line_43 | NAYY 4x150 SE | 41 | 43 | 0.040771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1136-6_0_4_line_44 | NAYY 4x150 SE | 42 | 44 | 0.030138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1136-6_0_4_line_45 | NAYY 4x150 SE | 43 | 45 | 0.044021 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1136-6_0_4_line_46 | NAYY 4x150 SE | 44 | 46 | 0.030022 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1136-6_0_4_line_47 | NAYY 4x150 SE | 44 | 47 | 0.0085593 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
48 | LV_1136-6_0_4_line_48 | NAYY 4x150 SE | 45 | 113 | 0.01516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1136-6_0_4_line_49 | NAYY 4x150 SE | 46 | 80 | 0.012842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1136-6_0_4_line_50 | NAYY 4x150 SE | 47 | 93 | 0.016679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1136-6_0_4_line_51 | NAYY 4x150 SE | 48 | 49 | 0.042807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1136-6_0_4_line_52 | NAYY 4x150 SE | 48 | 50 | 0.076852 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
53 | LV_1136-6_0_4_line_53 | NAYY 4x150 SE | 49 | 51 | 0.016594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_1136-6_0_4_line_54 | NAYY 4x150 SE | 50 | 52 | 0.042446 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1136-6_0_4_line_55 | NAYY 4x150 SE | 50 | 53 | 0.031709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1136-6_0_4_line_56 | NAYY 4x150 SE | 51 | 54 | 0.034311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_1136-6_0_4_line_57 | NAYY 4x150 SE | 52 | 55 | 0.043603 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1136-6_0_4_line_58 | NAYY 4x150 SE | 53 | 56 | 0.04367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1136-6_0_4_line_59 | NAYY 4x150 SE | 54 | 57 | 0.037083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1136-6_0_4_line_60 | NAYY 4x150 SE | 55 | 58 | 0.022547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1136-6_0_4_line_61 | NAYY 4x150 SE | 56 | 59 | 0.063624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1136-6_0_4_line_62 | NAYY 4x150 SE | 57 | 78 | 0.00015947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_1136-6_0_4_line_63 | NAYY 4x150 SE | 58 | 108 | 0.019786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1136-6_0_4_line_64 | NAYY 4x150 SE | 59 | 107 | 0.013109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1136-6_0_4_line_65 | NAYY 4x150 SE | 60 | 61 | 0.010948 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1136-6_0_4_line_66 | NAYY 4x150 SE | 61 | 62 | 0.027158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1136-6_0_4_line_67 | NAYY 4x150 SE | 62 | 63 | 0.0038764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1136-6_0_4_line_68 | NAYY 4x150 SE | 63 | 64 | 0.028633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1136-6_0_4_line_69 | NAYY 4x150 SE | 64 | 82 | 0.0025397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1136-6_0_4_line_70 | NAYY 4x150 SE | 65 | 66 | 0.011141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1136-6_0_4_line_71 | NAYY 4x150 SE | 65 | 67 | 0.023518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1136-6_0_4_line_72 | NAYY 4x150 SE | 66 | 68 | 0.028069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1136-6_0_4_line_73 | NAYY 4x150 SE | 67 | 69 | 0.016171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1136-6_0_4_line_74 | NAYY 4x150 SE | 68 | 70 | 0.021405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1136-6_0_4_line_75 | NAYY 4x150 SE | 70 | 71 | 0.030954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1136-6_0_4_line_76 | NAYY 4x150 SE | 71 | 108 | 0.0006633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1136-6_0_4_line_77 | NAYY 4x150 SE | 72 | 73 | 0.0048003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1136-6_0_4_line_78 | NAYY 4x150 SE | 73 | 88 | 0.012112 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1136-6_0_4_line_79 | NAYY 4x150 SE | 74 | 75 | 0.016417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_1136-6_0_4_line_80 | NAYY 4x150 SE | 74 | 76 | 0.0071161 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
81 | LV_1136-6_0_4_line_81 | NAYY 4x150 SE | 75 | 77 | 0.036236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
82 | LV_1136-6_0_4_line_82 | NAYY 4x150 SE | 76 | 78 | 0.020989 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1136-6_0_4_line_83 | NAYY 4x150 SE | 77 | 79 | 0.0051573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_1136-6_0_4_line_84 | NAYY 4x150 SE | 79 | 80 | 0.042735 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_1136-6_0_4_line_85 | NAYY 4x150 SE | 79 | 81 | 0.012931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1136-6_0_4_line_86 | NAYY 4x150 SE | 81 | 84 | 0.016588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1136-6_0_4_line_87 | NAYY 4x150 SE | 82 | 83 | 0.02456 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1136-6_0_4_line_88 | NAYY 4x150 SE | 83 | 112 | 0.036626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
89 | LV_1136-6_0_4_line_89 | NAYY 4x150 SE | 84 | 85 | 0.014197 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1136-6_0_4_line_90 | NAYY 4x150 SE | 85 | 86 | 0.027079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1136-6_0_4_line_91 | NAYY 4x150 SE | 88 | 89 | 0.0030849 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1136-6_0_4_line_92 | NAYY 4x150 SE | 89 | 90 | 0.0051515 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1136-6_0_4_line_93 | NAYY 4x150 SE | 90 | 104 | 0.0066625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1136-6_0_4_line_94 | NAYY 4x150 SE | 91 | 92 | 0.011267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_1136-6_0_4_line_95 | NAYY 4x150 SE | 91 | 93 | 0.01617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_1136-6_0_4_line_96 | NAYY 4x150 SE | 92 | 94 | 0.0082312 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1136-6_0_4_line_97 | NAYY 4x150 SE | 93 | 95 | 0.013656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1136-6_0_4_line_98 | NAYY 4x150 SE | 94 | 96 | 0.0029124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_1136-6_0_4_line_99 | NAYY 4x150 SE | 95 | 97 | 0.035886 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1136-6_0_4_line_100 | NAYY 4x150 SE | 96 | 98 | 0.012954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
101 | LV_1136-6_0_4_line_101 | NAYY 4x150 SE | 97 | 99 | 0.0048212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1136-6_0_4_line_102 | NAYY 4x150 SE | 98 | 112 | 0.027271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
103 | LV_1136-6_0_4_line_103 | NAYY 4x150 SE | 98 | 110 | 0.043012 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1136-6_0_4_line_104 | NAYY 4x150 SE | 100 | 101 | 0.021427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1136-6_0_4_line_105 | NAYY 4x150 SE | 100 | 102 | 0.0017047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1136-6_0_4_line_106 | NAYY 4x150 SE | 101 | 103 | 0.0013287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1136-6_0_4_line_107 | NAYY 4x150 SE | 102 | 104 | 0.0079933 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1136-6_0_4_line_108 | NAYY 4x150 SE | 103 | 105 | 0.0018315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1136-6_0_4_line_109 | NAYY 4x150 SE | 105 | 106 | 0.044075 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1136-6_0_4_line_110 | NAYY 4x150 SE | 106 | 107 | 0.018627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1136-6_0_4_line_111 | NAYY 4x150 SE | 109 | 110 | 0.0010819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1136-6_0_4_line_112 | NAYY 4x150 SE | 109 | 111 | 0.051774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1136-6_0_4_trafo_37 | 0.25 MVA 20/0.4 kV | 114 | 42 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2642152.3275 | 1210630.826 | 2642151.7838 | 1210629.193
1 | 2642152.3275 | 1210630.826 | 2642152.5814 | 1210631.5883 | 2642153.2693 | 1210635.3286 | 2642153.6592 | 1210638.2219 | 2642153.7355 | 1210641.4132 | 2642153.6749 | 1210644.6146
2 | 2642152.3275 | 1210630.826 | 2642387.443 | 1210607.003
3 | 2642060.7998 | 1210513.6481 | 2642151.7838 | 1210629.193
4 | 2642584.9549 | 1210422.1372 | 2642387.443 | 1210607.003
5 | 2642439.3093 | 1210706.5228 | 2642387.443 | 1210607.003
6 | 2642060.7998 | 1210513.6481 | 2642056.1618 | 1210500.8438 | 2642046.9203 | 1210470.5867
7 | 2642060.7998 | 1210513.6481 | 2641984.5324 | 1210622.3101
8 | 2642046.9203 | 1210470.5867 | 2642042.88 | 1210457.3585 | 2642042.88 | 1210457.3585
9 | 2642584.9549 | 1210422.1372 | 2642586.886 | 1210422.1039 | 2642612.8083 | 1210416.808 | 2642622.2687 | 1210414.8925
10 | 2642443.3777 | 1210716.492 | 2642443.1479 | 1210714.55 | 2642439.3093 | 1210706.5228
11 | 2642662.2773 | 1210383.4974 | 2642662.6889 | 1210391.8274 | 2642661.8304 | 1210397.1021 | 2642659.1525 | 1210401.7524 | 2642654.0257 | 1210405.5846 | 2642634.8185 | 1210412.3514 | 2642622.2687 | 1210414.8925
12 | 2642438.0875 | 1210741.7557 | 2642442.7872 | 1210730.012 | 2642443.8719 | 1210720.6698 | 2642443.3777 | 1210716.492
13 | 2642438.0875 | 1210741.7557 | 2642384.2038 | 1211089.7199
14 | 2642378.5064 | 1211104.317 | 2642380.7095 | 1211096.9061 | 2642383.9725 | 1211090.0475 | 2642384.2038 | 1211089.7199
15 | 2642001.0528 | 1210441.5289 | 2642001.4971 | 1210441.5804 | 2642010.0286 | 1210446.3098 | 2642017.0153 | 1210452.4069 | 2642020.988 | 1210452.6906 | 2642025.0527 | 1210449.2295
16 | 2642034.0541 | 1210441.565 | 2642025.0527 | 1210449.2295
17 | 2642034.0541 | 1210441.565 | 2642021.3823 | 1210426.9007 | 2642006.9926 | 1210415.5262 | 2641986.933 | 1210403.2343
18 | 2642034.0541 | 1210441.565 | 2642042.88 | 1210457.3585
19 | 2642309.531 | 1210068.2385 | 2642275.6118 | 1210145.6989
20 | 2642303.1712 | 1210020.4549 | 2642304.8556 | 1210049.795 | 2642306.1285 | 1210060.0099 | 2642309.531 | 1210068.2385
21 | 2641986.933 | 1210403.2343 | 2641894.6506 | 1210345.0685
22 | 2641886.8938 | 1210308.8907 | 2641884.5699 | 1210314.7191 | 2641884.9547 | 1210327.0289 | 2641887.1718 | 1210334.8934 | 2641892.2522 | 1210343.0227 | 2641894.6506 | 1210345.0685
23 | 2641886.8938 | 1210308.8907 | 2641889.0567 | 1210303.4663 | 2641898.2623 | 1210291.246 | 2641914.3844 | 1210270.2915 | 2641923.6623 | 1210257.5159 | 2641940.3615 | 1210230.1617 | 2641941.2879 | 1210228.9894
24 | 2642378.5064 | 1211104.317 | 2642549.5281 | 1211172.8355
25 | 2642378.5064 | 1211104.317 | 2642354.9113 | 1211096.9342 | 2642333.6095 | 1211091.9024 | 2642323.3604 | 1211087.9302
26 | 2642662.2773 | 1210383.4974 | 2642656.0095 | 1210385.3426 | 2642640.0611 | 1210385.9291 | 2642626.7209 | 1210382.0316 | 2642615.1362 | 1210374.967 | 2642608.1038 | 1210367.8794 | 2642605.9877 | 1210363.0282 | 2642606.4408 | 1210358.1174 | 2642618.3626 | 1210341.4039 | 2642621.2732 | 1210336.0883 | 2642621.6995 | 1210330.6771
27 | 2642662.2773 | 1210383.4974 | 2642847.3441 | 1210335.1055
28 | 2642621.6995 | 1210330.6771 | 2642619.4047 | 1210324.2348 | 2642616.1274 | 1210320.4972
29 | 2642847.3441 | 1210335.1055 | 2642863.6753 | 1210339.4363 | 2642875.9177 | 1210344.8496 | 2642878.0545 | 1210347.3577
30 | 2642893.0603 | 1210377.9555 | 2643217.6037 | 1210517.7399
31 | 2642893.0603 | 1210377.9555 | 2642882.1502 | 1210352.1652 | 2642878.0545 | 1210347.3577
32 | 2642878.0545 | 1210347.3577 | 2642968.5438 | 1210221.3771
33 | 2642549.5674 | 1210294.753 | 2642549.5674 | 1210294.753 | 2642561.7923 | 1210299.4762 | 2642573.7991 | 1210301.7409 | 2642587.5742 | 1210301.1499 | 2642594.3539 | 1210301.0648 | 2642600.5887 | 1210302.777 | 2642616.1274 | 1210320.4972
34 | 2642968.5438 | 1210221.3771 | 2642963.999 | 1210219.2654 | 2642960.8766 | 1210216.9972 | 2642958.8799 | 1210214.5925 | 2642957.3381 | 1210211.2906 | 2642957.0982 | 1210208.7096 | 2642957.8336 | 1210205.791 | 2642961.0903 | 1210201.0228 | 2642965.4549 | 1210194.3837 | 2642967.7579 | 1210190.1311 | 2642969.7541 | 1210185.2204 | 2642971.1091 | 1210178.5819 | 2642972.3948 | 1210177.3459 | 2642975.7005 | 1210175.702
35 | 2642522.1731 | 1210006.2798 | 2642667.2404 | 1209989.6653
36 | 2642522.1731 | 1210006.2798 | 2642518.7125 | 1210000.2295 | 2642511.6023 | 1209996.5211 | 2642505.0918 | 1209995.0517 | 2642496.9111 | 1209998.6511
37 | 2642496.9111 | 1209998.6511 | 2642499.3944 | 1209993.5881 | 2642498.6113 | 1209988.2906 | 2642487.7251 | 1209965.93
38 | 2642496.9111 | 1209998.6511 | 2642492.866 | 1210006.3713
39 | 2642382.7066 | 1210104.0228 | 2642395.404 | 1210102.2229 | 2642398.2437 | 1210101.3836
40 | 2642399.5548 | 1210100.9961 | 2642398.2437 | 1210101.3836
41 | 2642382.7066 | 1210104.0228 | 2642369.7294 | 1210102.4297 | 2642360.5142 | 1210099.3176
42 | 2642399.5548 | 1210100.9961 | 2642412.5477 | 1210097.1751 | 2642421.2376 | 1210094.6131 | 2642428.5518 | 1210093.1177
43 | 2642331.7146 | 1210072.2983 | 2642340.2629 | 1210085.422 | 2642347.9255 | 1210093.7479 | 2642356.2791 | 1210097.8873 | 2642360.5142 | 1210099.3176
44 | 2642458.4072 | 1210089.6299 | 2642440.9962 | 1210090.5734 | 2642428.5518 | 1210093.1177
45 | 2642331.7146 | 1210072.2983 | 2642310.4829 | 1210033.7353
46 | 2642458.4072 | 1210089.6299 | 2642466.6107 | 1210084.93 | 2642472.7397 | 1210079.1257 | 2642480.068 | 1210069.4646
47 | 2642458.4072 | 1210089.6299 | 2642466.4447 | 1210092.5727
48 | 2642303.1712 | 1210020.4549 | 2642310.4829 | 1210033.7353
49 | 2642484.6696 | 1210057.731 | 2642484.8069 | 1210059.1 | 2642481.4629 | 1210067.6256 | 2642480.068 | 1210069.4646
50 | 2642479.5736 | 1210102.4323 | 2642474.6474 | 1210097.272 | 2642470.0506 | 1210093.8929 | 2642466.4447 | 1210092.5727
51 | 2642407.4861 | 1209820.334 | 2642403.1149 | 1209845.9072 | 2642401.1427 | 1209861.4133 | 2642401.1854 | 1209862.6442
52 | 2642419.2422 | 1209744.4187 | 2642417.4447 | 1209762.0716 | 2642407.4861 | 1209820.334
53 | 2642401.761 | 1209879.228 | 2642401.1854 | 1209862.6442
54 | 2642419.2422 | 1209744.4187 | 2642413.0909 | 1209745.8425 | 2642408.5736 | 1209750.4797 | 2642404.8728 | 1209755.7343 | 2642396.7804 | 1209777.5106
55 | 2642419.2422 | 1209744.4187 | 2642419.0901 | 1209719.8367 | 2642420.5458 | 1209712.8652
56 | 2642401.761 | 1209879.228 | 2642401.9884 | 1209885.7334 | 2642404.635 | 1209902.6064 | 2642407.6502 | 1209912.896
57 | 2642381.8412 | 1209818.4732 | 2642386.8495 | 1209804.2344 | 2642396.7804 | 1209777.5106
58 | 2642420.5458 | 1209712.8652 | 2642379.8067 | 1209728.593
59 | 2642407.6502 | 1209912.896 | 2642410.9943 | 1209924.3085 | 2642414.1174 | 1209932.9579 | 2642420.3828 | 1209947.6748
60 | 2642381.8412 | 1209818.4732 | 2642374.3598 | 1209839.7431
61 | 2642331.2567 | 1209766.6155 | 2642333.0611 | 1209762.4176 | 2642342.2248 | 1209749.9198 | 2642355.2803 | 1209739.5285 | 2642371.372 | 1209731.8494 | 2642379.8067 | 1209728.593
62 | 2642420.3828 | 1209947.6748 | 2642420.4453 | 1209947.8215
63 | 2642368.5533 | 1209858.6428 | 2642371.1804 | 1209848.7822 | 2642374.3598 | 1209839.7431
64 | 2642331.2567 | 1209766.6155 | 2642327.1724 | 1209776.1171 | 2642326.6052 | 1209778.8255
65 | 2642549.5674 | 1210294.753 | 2642540.6294 | 1210288.4301
66 | 2642532.1158 | 1210262.804 | 2642536.4997 | 1210280.3293 | 2642540.6294 | 1210288.4301
67 | 2642532.1158 | 1210262.804 | 2642531.1751 | 1210259.0435
68 | 2642531.1751 | 1210259.0435 | 2642529.4428 | 1210252.1183 | 2642528.4048 | 1210238.8699 | 2642528.1438 | 1210230.6687
69 | 2642528.0631 | 1210228.1303 | 2642528.1438 | 1210230.6687
70 | 2642353.2513 | 1209949.1087 | 2642355.8212 | 1209944.9956 | 2642357.1262 | 1209938.841
71 | 2642332.7018 | 1209959.8958 | 2642346.6437 | 1209954.1247 | 2642352.3772 | 1209950.5077 | 2642353.2513 | 1209949.1087
72 | 2642360.4562 | 1209910.9821 | 2642358.8287 | 1209923.8825 | 2642357.5747 | 1209936.7255 | 2642357.1262 | 1209938.841
73 | 2642332.7018 | 1209959.8958 | 2642335.5216 | 1209975.8195
74 | 2642363.1353 | 1209889.7458 | 2642360.4562 | 1209910.9821
75 | 2642363.1353 | 1209889.7458 | 2642363.7977 | 1209884.495 | 2642366.3703 | 1209866.8363 | 2642368.3825 | 1209859.2837
76 | 2642368.3825 | 1209859.2837 | 2642368.5533 | 1209858.6428
77 | 2642300.0158 | 1209904.8468 | 2642301.1243 | 1209900.1762
78 | 2642303.6724 | 1209888.3363 | 2642301.7077 | 1209897.7181 | 2642301.1243 | 1209900.1762
79 | 2642433.9118 | 1209972.4324 | 2642435.2086 | 1209974.6096 | 2642443.1734 | 1209985.9803
80 | 2642433.9118 | 1209972.4324 | 2642430.2705 | 1209966.3186
81 | 2642443.1734 | 1209985.9803 | 2642463.9627 | 1210015.6593
82 | 2642420.4453 | 1209947.8215 | 2642423.4319 | 1209954.8367 | 2642430.2705 | 1209966.3186
83 | 2642466.9215 | 1210019.8834 | 2642463.9627 | 1210015.6593
84 | 2642466.9215 | 1210019.8834 | 2642479.5048 | 1210037.3386 | 2642483.7424 | 1210048.4863 | 2642484.6696 | 1210057.731
85 | 2642466.9215 | 1210019.8834 | 2642478.1073 | 1210013.395
86 | 2642492.866 | 1210006.3713 | 2642489.7556 | 1210006.6382 | 2642478.1073 | 1210013.395
87 | 2642528.0631 | 1210228.1303 | 2642527.8149 | 1210220.3328 | 2642525.9324 | 1210213.6155 | 2642522.1057 | 1210204.6126
88 | 2642522.1057 | 1210204.6126 | 2642509.6226 | 1210175.2438 | 2642509.3023 | 1210170.54
89 | 2642492.866 | 1210006.3713 | 2642495.1479 | 1210007.188 | 2642497.4915 | 1210010.0063 | 2642501.3893 | 1210017.1154
90 | 2642514.408 | 1210040.8595 | 2642501.3893 | 1210017.1154
91 | 2642303.6724 | 1209888.3363 | 2642304.3047 | 1209885.3169
92 | 2642305.3606 | 1209880.2748 | 2642304.3047 | 1209885.3169
93 | 2642306.7261 | 1209873.7538 | 2642305.3606 | 1209880.2748
94 | 2642490.4575 | 1210114.3902 | 2642498.0418 | 1210122.723
95 | 2642479.5736 | 1210102.4323 | 2642490.4575 | 1210114.3902
96 | 2642503.2011 | 1210129.1042 | 2642501.5936 | 1210126.6252 | 2642498.0418 | 1210122.723
97 | 2642479.5736 | 1210102.4323 | 2642490.6664 | 1210094.4683
98 | 2642504.7856 | 1210131.5479 | 2642503.2011 | 1210129.1042
99 | 2642490.6664 | 1210094.4683 | 2642509.3663 | 1210081.043 | 2642520.2401 | 1210074.1655
100 | 2642509.7588 | 1210143.3152 | 2642508.1263 | 1210136.6997 | 2642504.7856 | 1210131.5479
101 | 2642524.3147 | 1210071.5884 | 2642520.2401 | 1210074.1655
102 | 2642509.7588 | 1210143.3152 | 2642509.6796 | 1210150.163 | 2642508.8107 | 1210163.32 | 2642509.3023 | 1210170.54
103 | 2642509.7588 | 1210143.3152 | 2642537.6813 | 1210141.1905 | 2642543.9941 | 1210142.6586 | 2642550.8567 | 1210147.7201
104 | 2642308.7139 | 1209864.2616 | 2642313.1057 | 1209843.2895
105 | 2642308.7139 | 1209864.2616 | 2642308.3645 | 1209865.9302
106 | 2642313.1057 | 1209843.2895 | 2642313.378 | 1209841.989
107 | 2642306.7261 | 1209873.7538 | 2642308.3645 | 1209865.9302
108 | 2642313.7534 | 1209840.1964 | 2642313.378 | 1209841.989
109 | 2642313.7534 | 1209840.1964 | 2642322.7872 | 1209797.0575
110 | 2642322.7872 | 1209797.0575 | 2642326.6052 | 1209778.8255
111 | 2642551.7274 | 1210148.3624 | 2642550.8567 | 1210147.7201
112 | 2642588.3445 | 1210183.6095 | 2642583.0683 | 1210173.2214 | 2642578.4991 | 1210168.1081 | 2642551.7274 | 1210148.3624

## bus_geodata
| x | y | coords
0 | 2642152.3275 | 1210630.826
1 | 2642151.7838 | 1210629.193
2 | 2642153.6749 | 1210644.6146
3 | 2642387.443 | 1210607.003
4 | 2642060.7998 | 1210513.6481
5 | 2642046.9203 | 1210470.5867
6 | 2641984.5324 | 1210622.3101
7 | 2642584.9549 | 1210422.1372
8 | 2642439.3093 | 1210706.5228
9 | 2642622.2687 | 1210414.8925
10 | 2642438.0875 | 1210741.7557
11 | 2642443.3777 | 1210716.492
12 | 2642384.2038 | 1211089.7199
13 | 2642001.0528 | 1210441.5289
14 | 2642025.0527 | 1210449.2295
15 | 2642034.0541 | 1210441.565
16 | 2642275.6118 | 1210145.6989
17 | 2642309.531 | 1210068.2385
18 | 2641986.933 | 1210403.2343
19 | 2642042.88 | 1210457.3585
20 | 2641894.6506 | 1210345.0685
21 | 2641886.8938 | 1210308.8907
22 | 2641941.2879 | 1210228.9894
23 | 2642549.5281 | 1211172.8355
24 | 2642378.5064 | 1211104.317
25 | 2642323.3604 | 1211087.9302
26 | 2642662.2773 | 1210383.4974
27 | 2642621.6995 | 1210330.6771
28 | 2642847.3441 | 1210335.1055
29 | 2643217.6037 | 1210517.7399
30 | 2642893.0603 | 1210377.9555
31 | 2642878.0545 | 1210347.3577
32 | 2642616.1274 | 1210320.4972
33 | 2642968.5438 | 1210221.3771
34 | 2642975.7005 | 1210175.702
35 | 2642667.2404 | 1209989.6653
36 | 2642522.1731 | 1210006.2798
37 | 2642496.9111 | 1209998.6511
38 | 2642398.2437 | 1210101.3836
39 | 2642382.7066 | 1210104.0228
40 | 2642399.5548 | 1210100.9961
41 | 2642360.5142 | 1210099.3176
42 | 2642428.5518 | 1210093.1177
43 | 2642331.7146 | 1210072.2983
44 | 2642458.4072 | 1210089.6299
45 | 2642310.4829 | 1210033.7353
46 | 2642480.068 | 1210069.4646
47 | 2642466.4447 | 1210092.5727
48 | 2642407.4861 | 1209820.334
49 | 2642401.1854 | 1209862.6442
50 | 2642419.2422 | 1209744.4187
51 | 2642401.761 | 1209879.228
52 | 2642396.7804 | 1209777.5106
53 | 2642420.5458 | 1209712.8652
54 | 2642407.6502 | 1209912.896
55 | 2642381.8412 | 1209818.4732
56 | 2642379.8067 | 1209728.593
57 | 2642420.3828 | 1209947.6748
58 | 2642374.3598 | 1209839.7431
59 | 2642331.2567 | 1209766.6155
60 | 2642549.5674 | 1210294.753
61 | 2642540.6294 | 1210288.4301
62 | 2642532.1158 | 1210262.804
63 | 2642531.1751 | 1210259.0435
64 | 2642528.1438 | 1210230.6687
65 | 2642353.2513 | 1209949.1087
66 | 2642357.1262 | 1209938.8411
67 | 2642332.7018 | 1209959.8958
68 | 2642360.4562 | 1209910.9821
69 | 2642335.5216 | 1209975.8195
70 | 2642363.1353 | 1209889.7458
71 | 2642368.3825 | 1209859.2837
72 | 2642300.0158 | 1209904.8468
73 | 2642301.1243 | 1209900.1762
74 | 2642433.9118 | 1209972.4324
75 | 2642443.1734 | 1209985.9803
76 | 2642430.2705 | 1209966.3186
77 | 2642463.9627 | 1210015.6593
78 | 2642420.4453 | 1209947.8215
79 | 2642466.9215 | 1210019.8834
80 | 2642484.6696 | 1210057.731
81 | 2642478.1073 | 1210013.395
82 | 2642528.0631 | 1210228.1303
83 | 2642522.1057 | 1210204.6126
84 | 2642492.866 | 1210006.3713
85 | 2642501.3893 | 1210017.1154
86 | 2642514.408 | 1210040.8595
87 | 2642487.7251 | 1209965.93
88 | 2642303.6724 | 1209888.3363
89 | 2642304.3047 | 1209885.3169
90 | 2642305.3606 | 1209880.2748
91 | 2642490.4575 | 1210114.3902
92 | 2642498.0418 | 1210122.7229
93 | 2642479.5736 | 1210102.4323
94 | 2642503.2011 | 1210129.1042
95 | 2642490.6664 | 1210094.4683
96 | 2642504.7856 | 1210131.5479
97 | 2642520.2401 | 1210074.1655
98 | 2642509.7588 | 1210143.3152
99 | 2642524.3147 | 1210071.5884
100 | 2642308.7139 | 1209864.2616
101 | 2642313.1057 | 1209843.2895
102 | 2642308.3645 | 1209865.9302
103 | 2642313.378 | 1209841.989
104 | 2642306.7261 | 1209873.7538
105 | 2642313.7534 | 1209840.1964
106 | 2642322.7872 | 1209797.0575
107 | 2642326.6052 | 1209778.8255
108 | 2642368.5533 | 1209858.6428
109 | 2642551.7274 | 1210148.3624
110 | 2642550.8567 | 1210147.7201
111 | 2642588.3445 | 1210183.6095
112 | 2642509.3023 | 1210170.54
113 | 2642303.1712 | 1210020.4549
114 | 2642399.5548 | 1210100.9961

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97273 | -0.19376 | 0.00056793 | 0.00014234
1 | 0.97272 | -0.19386 | 0.00042678 | 0.00010696
2 | 0.97273 | -0.19382 | 0.00040357 | 0.00010114
3 | 0.97498 | -0.17746 | 0.0019516 | 0.00048912
4 | 0.97162 | -0.20183 | 0.0006981 | 0.00017496
5 | 0.97135 | -0.20381 | 0.001532 | 0.00038395
6 | 0.97157 | -0.20226 | 0.00029783 | 7.4643e-05
7 | 0.98102 | -0.13396 | 0.00023435 | 5.8734e-05
8 | 0.97386 | -0.18557 | 0.00031011 | 7.7722e-05
9 | 0.98188 | -0.12779 | 0.0018406 | 0.00046129
10 | 0.97351 | -0.18808 | 0.0022874 | 0.00057327
11 | 0.97375 | -0.18631 | 0.00017204 | 4.3118e-05
12 | 0.97143 | -0.20324 | 0.0018144 | 0.00045473
13 | 0.97122 | -0.2048 | 0.00042498 | 0.00010651
14 | 0.97123 | -0.20467 | 0.00019387 | 4.8588e-05
15 | 0.97125 | -0.2046 | 0 | 0
16 | 0.99861 | -0.0098162 | 0.00048555 | 0.00012169
17 | 0.99866 | -0.0094018 | 0.0014902 | 0.00037347
18 | 0.97111 | -0.20559 | 0.00022644 | 5.6752e-05
19 | 0.9713 | -0.20418 | 0.00042688 | 0.00010699
20 | 0.97091 | -0.20708 | 0.00026117 | 6.5454e-05
21 | 0.97085 | -0.20751 | 0.00049129 | 0.00012313
22 | 0.97077 | -0.20806 | 0.00052568 | 0.00013175
23 | 0.9711 | -0.20562 | 0.0010203 | 0.00025572
24 | 0.97137 | -0.20361 | 0 | 0
25 | 0.97127 | -0.20435 | 0.0012041 | 0.00030178
26 | 0.98337 | -0.11719 | 0 | 0
27 | 0.98653 | -0.094631 | 0.00037006 | 9.2746e-05
28 | 0.98229 | -0.12497 | 0 | 0
29 | 0.98161 | -0.12996 | 0.00086151 | 0.00021591
30 | 0.98205 | -0.12674 | 0.00025133 | 6.299e-05
31 | 0.9821 | -0.12634 | 0.0016797 | 0.00042098
32 | 0.9869 | -0.091988 | 0.002689 | 0.00067393
33 | 0.98186 | -0.12809 | 0 | 0
34 | 0.98177 | -0.12873 | 0.0010771 | 0.00026995
35 | 0.99127 | -0.060894 | 0.001463 | 0.00036666
36 | 0.99158 | -0.058714 | 0.0050416 | 0.0012635
37 | 0.99187 | -0.056694 | 0 | 0
38 | 0.99965 | -0.0024905 | 0.00079154 | 0.00019838
39 | 0.99949 | -0.0036166 | 0 | 0
40 | 0.99966 | -0.0023822 | 0 | 0
41 | 0.99925 | -0.0052434 | 0.0037246 | 0.00093348
42 | 1 | 0 | -0.21955 | -0.055103
43 | 0.99906 | -0.0066341 | 0 | 0
44 | 0.99698 | -0.02099 | 0 | 0
45 | 0.99884 | -0.0081344 | 0.0014155 | 0.00035475
46 | 0.9955 | -0.031275 | 0.0018502 | 0.00046372
47 | 0.99654 | -0.024042 | 0.028141 | 0.0070529
48 | 0.98601 | -0.097669 | 0.0027016 | 0.00067709
49 | 0.9872 | -0.089303 | 0.0023319 | 0.00058443
50 | 0.98296 | -0.11922 | 0 | 0
51 | 0.98768 | -0.085933 | 0 | 0
52 | 0.9815 | -0.12955 | 0.0018061 | 0.00045265
53 | 0.98152 | -0.12937 | 0 | 0
54 | 0.98867 | -0.078974 | 0.0049927 | 0.0012513
55 | 0.98012 | -0.13938 | 0.0021346 | 0.00053498
56 | 0.97955 | -0.14338 | 0.0011258 | 0.00028214
57 | 0.98983 | -0.070838 | 0.0011951 | 0.00029953
58 | 0.97948 | -0.14397 | 0.0027668 | 0.00069343
59 | 0.97677 | -0.16315 | 0.00064494 | 0.00016164
60 | 0.98959 | -0.072958 | 0.00028508 | 7.1449e-05
61 | 0.98998 | -0.070191 | 0.00030223 | 7.5747e-05
62 | 0.99096 | -0.06325 | 0.00028668 | 7.1848e-05
63 | 0.9911 | -0.06225 | 0.00022244 | 5.5749e-05
64 | 0.99216 | -0.054801 | 0.00059866 | 0.00015004
65 | 0.97778 | -0.15613 | 0.0030132 | 0.00075517
66 | 0.97787 | -0.15548 | 0.0013676 | 0.00034276
67 | 0.9777 | -0.15675 | 0 | 0
68 | 0.97816 | -0.15345 | 0.0028561 | 0.00071581
69 | 0.97764 | -0.15718 | 0.0025357 | 0.0006355
70 | 0.97846 | -0.15127 | 0.0018082 | 0.00045318
71 | 0.97898 | -0.14753 | 0.0027782 | 0.00069627
72 | 0.97298 | -0.1904 | 0.001732 | 0.00043409
73 | 0.97299 | -0.19031 | 0.0015962 | 0.00040004
74 | 0.99077 | -0.064289 | 0.0029531 | 0.0007401
75 | 0.99135 | -0.060224 | 0.0016816 | 0.00042145
76 | 0.99053 | -0.065981 | 0.00243 | 0.00060902
77 | 0.99266 | -0.051063 | 0.0025683 | 0.00064368
78 | 0.98984 | -0.070803 | 0.0019706 | 0.00049387
79 | 0.99285 | -0.049716 | 0 | 0
80 | 0.99488 | -0.035603 | 0.0022843 | 0.0005725
81 | 0.99247 | -0.052425 | 0.0014667 | 0.00036759
82 | 0.99226 | -0.054126 | 0.0014126 | 0.00035402
83 | 0.99324 | -0.04725 | 0.00037715 | 9.4522e-05
84 | 0.99201 | -0.055657 | 0 | 0
85 | 0.99186 | -0.056733 | 0.0020327 | 0.00050944
86 | 0.99165 | -0.058229 | 0.005441 | 0.0013637
87 | 0.9916 | -0.058591 | 0.0052122 | 0.0013063
88 | 0.97305 | -0.18989 | 0.0011372 | 0.00028501
89 | 0.97307 | -0.18974 | 0.0011348 | 0.0002844
90 | 0.97311 | -0.18944 | 0.0015475 | 0.00038783
91 | 0.99537 | -0.032247 | 0.013644 | 0.0034196
92 | 0.99507 | -0.034397 | 0.00061951 | 0.00015526
93 | 0.99592 | -0.028423 | 0 | 0
94 | 0.99485 | -0.035952 | 0.0063095 | 0.0015813
95 | 0.99577 | -0.029506 | 0.0018981 | 0.0004757
96 | 0.99478 | -0.03644 | 0.013425 | 0.0033646
97 | 0.99546 | -0.031668 | 0.0031774 | 0.00079634
98 | 0.99455 | -0.038028 | 0 | 0
99 | 0.99544 | -0.031804 | 0.0028034 | 0.00070261
100 | 0.97333 | -0.18785 | 0.0017614 | 0.00044146
101 | 0.97382 | -0.18435 | 0.003546 | 0.00088872
102 | 0.9733 | -0.1881 | 0.0038297 | 0.00095981
103 | 0.97386 | -0.18408 | 0.0027609 | 0.00069196
104 | 0.97318 | -0.18893 | 0.0027812 | 0.00069704
105 | 0.97391 | -0.18366 | 0.0028136 | 0.00070516
106 | 0.9755 | -0.17225 | 0.0014447 | 0.00036207
107 | 0.97622 | -0.16715 | 0.0030454 | 0.00076324
108 | 0.979 | -0.14743 | 0.0024422 | 0.00061208
109 | 0.9941 | -0.041175 | 0.00022926 | 5.7458e-05
110 | 0.99411 | -0.041134 | 0.0033689 | 0.00084432
111 | 0.99384 | -0.043032 | 0.0035483 | 0.00088929
112 | 0.99397 | -0.042061 | 0.001265 | 0.00031704
113 | 0.9988 | -0.0084362 | 0 | 0
114 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0055126 | 0.0013739 | -0.0055125 | -0.0013739 | 7.6321e-08 | 7.9894e-09 | 0.00843 | 0.00843 | 0.00843 | 0.97273 | -0.19376 | 0.97272 | -0.19386 | 3.1222
1 | 0.00040357 | 0.00010097 | -0.00040357 | -0.00010114 | 3.3102e-09 | -1.7153e-07 | 0.00061729 | 0.00061735 | 0.00061735 | 0.97273 | -0.19376 | 0.97273 | -0.19382 | 0.22865
2 | -0.0064841 | -0.0016172 | 0.0064986 | 0.0016198 | 1.4498e-05 | 2.6359e-06 | 0.009916 | 0.009915 | 0.009916 | 0.97273 | -0.19376 | 0.97498 | -0.17746 | 3.6726
3 | 0.0050857 | 0.0012669 | -0.0050802 | -0.0012666 | 5.551e-06 | 3.1148e-07 | 0.0077771 | 0.0077778 | 0.0077778 | 0.97272 | -0.19386 | 0.97162 | -0.20183 | 2.8807
4 | -0.015277 | -0.003813 | 0.015369 | 0.0038449 | 9.1724e-05 | 3.1884e-05 | 0.023311 | 0.023309 | 0.023311 | 0.97498 | -0.17746 | 0.98102 | -0.13396 | 8.6335
5 | 0.0068271 | 0.0017041 | -0.0068195 | -0.0017026 | 7.5995e-06 | 1.5249e-06 | 0.010417 | 0.010418 | 0.010418 | 0.97498 | -0.17746 | 0.97386 | -0.18557 | 3.8584
6 | 0.0040842 | 0.0010186 | -0.0040831 | -0.0010187 | 1.1042e-06 | -1.3564e-07 | 0.0062531 | 0.0062533 | 0.0062533 | 0.97162 | -0.20183 | 0.97135 | -0.20381 | 2.316
7 | 0.00029785 | 7.3005e-05 | -0.00029783 | -7.4643e-05 | 1.7214e-08 | -1.6375e-06 | 0.00045555 | 0.00045614 | 0.00045614 | 0.97162 | -0.20183 | 0.97157 | -0.20226 | 0.16894
8 | 0.0025511 | 0.00063479 | -0.002551 | -0.00063491 | 1.3171e-07 | -1.2054e-07 | 0.0039064 | 0.0039065 | 0.0039065 | 0.97135 | -0.20381 | 0.9713 | -0.20418 | 1.4469
9 | -0.015603 | -0.0039037 | 0.015617 | 0.0039083 | 1.3294e-05 | 4.6322e-06 | 0.023665 | 0.023665 | 0.023665 | 0.98102 | -0.13396 | 0.98188 | -0.12779 | 8.7647
10 | 0.0065094 | 0.0016249 | -0.0065087 | -0.0016248 | 6.6965e-07 | 1.2253e-07 | 0.0099437 | 0.0099438 | 0.0099438 | 0.97386 | -0.18557 | 0.97375 | -0.18631 | 3.6829
11 | -0.017457 | -0.0043696 | 0.017483 | 0.0043787 | 2.5598e-05 | 9.1029e-06 | 0.026454 | 0.026454 | 0.026454 | 0.98188 | -0.12779 | 0.98337 | -0.11719 | 9.7978
12 | -0.0063351 | -0.0015814 | 0.0063367 | 0.0015816 | 1.5358e-06 | 2.6409e-07 | 0.009681 | 0.0096809 | 0.009681 | 0.97351 | -0.18808 | 0.97375 | -0.18631 | 3.5855
13 | 0.0040477 | 0.0010081 | -0.0040393 | -0.0010092 | 8.4065e-06 | -1.1353e-06 | 0.0061847 | 0.0061863 | 0.0061863 | 0.97351 | -0.18808 | 0.97143 | -0.20324 | 2.2912
14 | 0.002225 | 0.00055451 | -0.0022248 | -0.00055466 | 1.1392e-07 | -1.5089e-07 | 0.003407 | 0.0034071 | 0.0034071 | 0.97143 | -0.20324 | 0.97137 | -0.20361 | 1.2619
15 | -0.00042498 | -0.00010651 | 0.00042498 | 0.00010616 | 7.6164e-09 | -3.5343e-07 | 0.00065111 | 0.00065099 | 0.00065111 | 0.97122 | -0.2048 | 0.97123 | -0.20467 | 0.24115
16 | -0.00061885 | -0.00015474 | 0.00061886 | 0.0001546 | 6.6296e-09 | -1.4376e-07 | 0.00094801 | 0.00094795 | 0.00094801 | 0.97123 | -0.20467 | 0.97125 | -0.2046 | 0.35111
17 | 0.0015051 | 0.00037351 | -0.0015049 | -0.00037419 | 2.0302e-07 | -6.7981e-07 | 0.0023047 | 0.0023049 | 0.0023049 | 0.97125 | -0.2046 | 0.97111 | -0.20559 | 0.85368
18 | -0.002124 | -0.00052811 | 0.0021241 | 0.00052793 | 1.1943e-07 | -1.7798e-07 | 0.0032526 | 0.0032525 | 0.0032526 | 0.97125 | -0.2046 | 0.9713 | -0.20418 | 1.2047
19 | -0.00048555 | -0.00012169 | 0.00048557 | 0.00012059 | 2.7607e-08 | -1.0957e-06 | 0.00072351 | 0.00072312 | 0.00072351 | 0.99861 | -0.0098162 | 0.99866 | -0.0094018 | 0.26797
20 | -0.0019757 | -0.00049406 | 0.001976 | 0.00049353 | 2.6266e-07 | -5.3478e-07 | 0.0029435 | 0.0029433 | 0.0029435 | 0.99866 | -0.0094018 | 0.9988 | -0.0084362 | 1.0902
21 | 0.0012785 | 0.00031743 | -0.0012782 | -0.00031868 | 2.6101e-07 | -1.2489e-06 | 0.001958 | 0.0019584 | 0.0019584 | 0.97111 | -0.20559 | 0.97091 | -0.20708 | 0.72535
22 | 0.0010171 | 0.00025323 | -0.001017 | -0.00025369 | 5.985e-08 | -4.6545e-07 | 0.0015582 | 0.0015583 | 0.0015583 | 0.97091 | -0.20708 | 0.97085 | -0.20751 | 0.57717
23 | 0.00052572 | 0.00013057 | -0.00052568 | -0.00013175 | 3.9242e-08 | -1.1832e-06 | 0.00080534 | 0.00080578 | 0.00080578 | 0.97085 | -0.20751 | 0.97077 | -0.20806 | 0.29844
24 | -0.0010203 | -0.00025572 | 0.0010206 | 0.00025354 | 2.8086e-07 | -2.172e-06 | 0.0015634 | 0.0015626 | 0.0015634 | 0.9711 | -0.20562 | 0.97137 | -0.20361 | 0.57905
25 | 0.0012042 | 0.00030112 | -0.0012041 | -0.00030178 | 1.2231e-07 | -6.6595e-07 | 0.0018445 | 0.0018448 | 0.0018448 | 0.97137 | -0.20361 | 0.97127 | -0.20435 | 0.68324
26 | -0.021358 | -0.0053402 | 0.021425 | 0.0053645 | 6.6583e-05 | 2.4308e-05 | 0.032314 | 0.032314 | 0.032314 | 0.98337 | -0.11719 | 0.98653 | -0.094631 | 11.9683
27 | 0.0038753 | 0.00096155 | -0.0038712 | -0.00096239 | 4.1003e-06 | -8.4708e-07 | 0.0058606 | 0.0058614 | 0.0058614 | 0.98337 | -0.11719 | 0.98229 | -0.12497 | 2.1709
28 | -0.021795 | -0.0054573 | 0.021803 | 0.0054602 | 7.963e-06 | 2.9119e-06 | 0.032872 | 0.032872 | 0.032872 | 0.98653 | -0.094631 | 0.9869 | -0.091988 | 12.1748
29 | 0.0038712 | 0.00096239 | -0.0038705 | -0.00096254 | 7.1985e-07 | -1.4809e-07 | 0.0058614 | 0.0058616 | 0.0058616 | 0.98229 | -0.12497 | 0.9821 | -0.12634 | 2.171
30 | -0.00086151 | -0.00021591 | 0.00086188 | 0.00021159 | 3.7561e-07 | -4.3245e-06 | 0.001306 | 0.0013044 | 0.001306 | 0.98161 | -0.12996 | 0.98205 | -0.12674 | 0.48369
31 | -0.0011132 | -0.00027458 | 0.0011133 | 0.00027417 | 6.081e-08 | -4.1085e-07 | 0.0016852 | 0.001685 | 0.0016852 | 0.98205 | -0.12674 | 0.9821 | -0.12634 | 0.62415
32 | 0.0010775 | 0.0002674 | -0.0010772 | -0.00026926 | 2.5776e-07 | -1.8631e-06 | 0.0016315 | 0.0016322 | 0.0016322 | 0.9821 | -0.12634 | 0.98186 | -0.12809 | 0.60454
33 | -0.024492 | -0.0061341 | 0.024556 | 0.006158 | 6.4602e-05 | 2.3874e-05 | 0.036926 | 0.036926 | 0.036926 | 0.9869 | -0.091988 | 0.98959 | -0.072958 | 13.6764
34 | 0.0010772 | 0.00026926 | -0.0010771 | -0.00026995 | 9.5358e-08 | -6.886e-07 | 0.0016322 | 0.0016325 | 0.0016325 | 0.98186 | -0.12809 | 0.98177 | -0.12873 | 0.60463
35 | -0.001463 | -0.00036666 | 0.0014634 | 0.00036494 | 4.3929e-07 | -1.714e-06 | 0.0021961 | 0.0021954 | 0.0021961 | 0.99127 | -0.060894 | 0.99158 | -0.058714 | 0.81337
36 | -0.006505 | -0.0016285 | 0.0065068 | 0.0016288 | 1.8156e-06 | 3.0428e-07 | 0.0097611 | 0.009761 | 0.0097611 | 0.99158 | -0.058714 | 0.99187 | -0.056694 | 3.6152
37 | 0.0052136 | 0.0013064 | -0.0052122 | -0.0013063 | 1.3691e-06 | 6.3804e-08 | 0.0078214 | 0.0078216 | 0.0078216 | 0.99187 | -0.056694 | 0.9916 | -0.058591 | 2.8969
38 | -0.01172 | -0.0029352 | 0.011722 | 0.0029357 | 1.6806e-06 | 5.3391e-07 | 0.017582 | 0.017582 | 0.017582 | 0.99187 | -0.056694 | 0.99201 | -0.055657 | 6.512
39 | 0.0071202 | 0.0017815 | -0.0071191 | -0.0017813 | 1.1063e-06 | 2.1858e-07 | 0.010598 | 0.010598 | 0.010598 | 0.99965 | -0.0024905 | 0.99949 | -0.0036166 | 3.9251
40 | -0.0079118 | -0.0019799 | 0.0079119 | 0.0019799 | 1.183e-07 | 2.7577e-08 | 0.011776 | 0.011776 | 0.011776 | 0.99965 | -0.0024905 | 0.99966 | -0.0023822 | 4.3615
41 | 0.0071191 | 0.0017813 | -0.0071175 | -0.001781 | 1.598e-06 | 3.1586e-07 | 0.010598 | 0.010598 | 0.010598 | 0.99949 | -0.0036166 | 0.99925 | -0.0052434 | 3.9252
42 | -0.0079119 | -0.0019799 | 0.0079145 | 0.0019805 | 2.6019e-06 | 6.0637e-07 | 0.011776 | 0.011776 | 0.011776 | 0.99966 | -0.0023822 | 1 | 0 | 4.3615
43 | 0.0033929 | 0.00084752 | -0.0033923 | -0.00084781 | 6.4921e-07 | -2.8428e-07 | 0.0050515 | 0.0050517 | 0.0050517 | 0.99925 | -0.0052434 | 0.99906 | -0.0066341 | 1.871
44 | 0.21083 | 0.053122 | -0.21021 | -0.052886 | 0.00061737 | 0.00023627 | 0.31382 | 0.31382 | 0.31382 | 1 | 0 | 0.99698 | -0.02099 | 38.7433
45 | 0.0033923 | 0.00084781 | -0.0033916 | -0.00084811 | 7.0103e-07 | -3.0669e-07 | 0.0050517 | 0.0050519 | 0.0050519 | 0.99906 | -0.0066341 | 0.99884 | -0.0081344 | 1.8711
46 | 0.10344 | 0.026088 | -0.10329 | -0.026032 | 0.00014894 | 5.6111e-05 | 0.15444 | 0.15444 | 0.15444 | 0.99698 | -0.02099 | 0.9955 | -0.031275 | 19.0664
47 | 0.10678 | 0.026798 | -0.10673 | -0.026781 | 4.5226e-05 | 1.706e-05 | 0.15938 | 0.15938 | 0.15938 | 0.99698 | -0.02099 | 0.99654 | -0.024042 | 19.6769
48 | 0.0019761 | 0.00049336 | -0.001976 | -0.00049353 | 8.1947e-08 | -1.669e-07 | 0.0029432 | 0.0029433 | 0.0029433 | 0.99884 | -0.0081344 | 0.9988 | -0.0084362 | 1.0901
49 | 0.10144 | 0.025568 | -0.10137 | -0.025545 | 6.1448e-05 | 2.3133e-05 | 0.15167 | 0.15167 | 0.15167 | 0.9955 | -0.031275 | 0.99488 | -0.035603 | 18.725
50 | 0.078592 | 0.019728 | -0.078544 | -0.019711 | 4.7786e-05 | 1.7728e-05 | 0.11736 | 0.11736 | 0.11736 | 0.99654 | -0.024042 | 0.99592 | -0.028423 | 14.4893
51 | -0.057645 | -0.01451 | 0.057713 | 0.014534 | 6.7418e-05 | 2.429e-05 | 0.087017 | 0.087016 | 0.087017 | 0.98601 | -0.097669 | 0.9872 | -0.089303 | 10.7428
52 | 0.054944 | 0.013833 | -0.054779 | -0.013771 | 0.00016494 | 6.1486e-05 | 0.08294 | 0.08294 | 0.08294 | 0.98601 | -0.097669 | 0.98296 | -0.11922 | 15.3593
53 | -0.060045 | -0.015119 | 0.060073 | 0.015129 | 2.8288e-05 | 1.0243e-05 | 0.090531 | 0.090531 | 0.090531 | 0.9872 | -0.089303 | 0.98768 | -0.085933 | 11.1767
54 | 0.023605 | 0.0059255 | -0.023571 | -0.005913 | 3.3826e-05 | 1.2473e-05 | 0.035737 | 0.035737 | 0.035737 | 0.98296 | -0.11922 | 0.9815 | -0.12955 | 13.2358
55 | 0.031174 | 0.007846 | -0.03113 | -0.0078295 | 4.4088e-05 | 1.6556e-05 | 0.047204 | 0.047204 | 0.047204 | 0.98296 | -0.11922 | 0.98152 | -0.12937 | 17.483
56 | -0.060073 | -0.015129 | 0.060132 | 0.01515 | 5.8491e-05 | 2.1178e-05 | 0.090531 | 0.09053 | 0.090531 | 0.98768 | -0.085933 | 0.98867 | -0.078974 | 11.1767
57 | 0.021765 | 0.0054603 | -0.021735 | -0.0054495 | 2.9628e-05 | 1.0845e-05 | 0.032999 | 0.032999 | 0.032999 | 0.9815 | -0.12955 | 0.98012 | -0.13938 | 12.2218
58 | 0.03113 | 0.0078295 | -0.031069 | -0.0078067 | 6.0719e-05 | 2.2803e-05 | 0.047204 | 0.047204 | 0.047204 | 0.98152 | -0.12937 | 0.97955 | -0.14338 | 17.4831
59 | -0.065124 | -0.016401 | 0.065198 | 0.016429 | 7.4146e-05 | 2.709e-05 | 0.098045 | 0.098044 | 0.098045 | 0.98867 | -0.078974 | 0.98983 | -0.070838 | 12.1043
60 | 0.0196 | 0.0049145 | -0.019588 | -0.00491 | 1.2459e-05 | 4.508e-06 | 0.029758 | 0.029758 | 0.029758 | 0.98012 | -0.13938 | 0.97948 | -0.14397 | 11.0215
61 | 0.029944 | 0.0075245 | -0.029861 | -0.0074937 | 8.2171e-05 | 3.0806e-05 | 0.045494 | 0.045494 | 0.045494 | 0.97955 | -0.14338 | 0.97677 | -0.16315 | 16.8498
62 | -0.066393 | -0.016728 | 0.066394 | 0.016728 | 3.3065e-07 | 1.2102e-07 | 0.099841 | 0.099841 | 0.099841 | 0.98983 | -0.070838 | 0.98984 | -0.070803 | 12.326
63 | 0.016821 | 0.0042166 | -0.016813 | -0.0042137 | 8.0631e-06 | 2.8523e-06 | 0.025555 | 0.025555 | 0.025555 | 0.97948 | -0.14397 | 0.979 | -0.14743 | 9.4648
64 | 0.029217 | 0.0073321 | -0.0292 | -0.007326 | 1.6208e-05 | 6.0697e-06 | 0.044512 | 0.044512 | 0.044512 | 0.97677 | -0.16315 | 0.97622 | -0.16715 | 16.4859
65 | -0.024841 | -0.0062295 | 0.024851 | 0.006233 | 9.5328e-06 | 3.5258e-06 | 0.037355 | 0.037355 | 0.037355 | 0.98959 | -0.072958 | 0.98998 | -0.070191 | 13.8351
66 | -0.025153 | -0.0063087 | 0.025177 | 0.0063177 | 2.4225e-05 | 8.9679e-06 | 0.037809 | 0.037809 | 0.037809 | 0.98998 | -0.070191 | 0.99096 | -0.06325 | 14.0033
67 | -0.025464 | -0.0063895 | 0.025468 | 0.0063909 | 3.5369e-06 | 1.3104e-06 | 0.038239 | 0.038239 | 0.038239 | 0.99096 | -0.06325 | 0.9911 | -0.06225 | 14.1627
68 | -0.02569 | -0.0064466 | 0.025717 | 0.0064565 | 2.6584e-05 | 9.8552e-06 | 0.038573 | 0.038573 | 0.038573 | 0.9911 | -0.06225 | 0.99216 | -0.054801 | 14.2864
69 | -0.026315 | -0.0066065 | 0.026318 | 0.0066074 | 2.469e-06 | 9.168e-07 | 0.039471 | 0.039471 | 0.039471 | 0.99216 | -0.054801 | 0.99226 | -0.054126 | 14.6189
70 | -0.0055492 | -0.0013903 | 0.0055497 | 0.0013904 | 4.9579e-07 | 5.0932e-08 | 0.0084448 | 0.0084447 | 0.0084448 | 0.97778 | -0.15613 | 0.97787 | -0.15548 | 3.1277
71 | 0.002536 | 0.00063514 | -0.0025358 | -0.00063536 | 2.1858e-07 | -2.1089e-07 | 0.0038593 | 0.0038594 | 0.0038594 | 0.97778 | -0.15613 | 0.9777 | -0.15675 | 1.4294
72 | -0.0069174 | -0.0017331 | 0.0069193 | 0.0017335 | 1.9406e-06 | 3.9413e-07 | 0.010526 | 0.010526 | 0.010526 | 0.97787 | -0.15548 | 0.97816 | -0.15345 | 3.8985
73 | 0.0025358 | 0.00063536 | -0.0025357 | -0.0006355 | 1.503e-07 | -1.4498e-07 | 0.0038594 | 0.0038594 | 0.0038594 | 0.9777 | -0.15675 | 0.97764 | -0.15718 | 1.4294
74 | -0.0097754 | -0.0024493 | 0.0097784 | 0.0024502 | 2.9536e-06 | 8.6722e-07 | 0.014871 | 0.01487 | 0.014871 | 0.97816 | -0.15345 | 0.97846 | -0.15127 | 5.5076
75 | -0.011587 | -0.0029034 | 0.011593 | 0.0029053 | 5.9968e-06 | 1.9175e-06 | 0.01762 | 0.01762 | 0.01762 | 0.97846 | -0.15127 | 0.97898 | -0.14753 | 6.5261
76 | -0.014371 | -0.0036016 | 0.014371 | 0.0036016 | 1.9748e-07 | 6.7612e-08 | 0.021843 | 0.021843 | 0.021843 | 0.97898 | -0.14753 | 0.979 | -0.14743 | 8.09
77 | -0.001732 | -0.00043409 | 0.0017321 | 0.00043404 | 2.1017e-08 | -5.1536e-08 | 0.0026489 | 0.0026488 | 0.0026489 | 0.97298 | -0.1904 | 0.97299 | -0.19031 | 0.98106
78 | -0.0033282 | -0.00083407 | 0.0033284 | 0.000834 | 1.9579e-07 | -7.5132e-08 | 0.0050899 | 0.0050898 | 0.0050899 | 0.97299 | -0.19031 | 0.97305 | -0.18989 | 1.8851
79 | -0.07381 | -0.018594 | 0.073852 | 0.01861 | 4.1988e-05 | 1.5515e-05 | 0.11089 | 0.11089 | 0.11089 | 0.99077 | -0.064289 | 0.99135 | -0.060224 | 13.6899
80 | 0.070857 | 0.017854 | -0.070841 | -0.017848 | 1.6773e-05 | 6.1765e-06 | 0.10645 | 0.10645 | 0.10645 | 0.99077 | -0.064289 | 0.99053 | -0.065981 | 13.1424
81 | -0.075534 | -0.019031 | 0.075631 | 0.019067 | 9.6944e-05 | 3.5883e-05 | 0.11341 | 0.11341 | 0.11341 | 0.99135 | -0.060224 | 0.99266 | -0.051063 | 14.0015
82 | 0.06841 | 0.017239 | -0.068364 | -0.017222 | 4.6138e-05 | 1.6935e-05 | 0.1028 | 0.1028 | 0.1028 | 0.99053 | -0.065981 | 0.98984 | -0.070803 | 12.6918
83 | -0.078199 | -0.019711 | 0.078214 | 0.019716 | 1.475e-05 | 5.4731e-06 | 0.11726 | 0.11726 | 0.11726 | 0.99266 | -0.051063 | 0.99285 | -0.049716 | 14.4768
84 | -0.098895 | -0.024899 | 0.09909 | 0.024972 | 0.00019538 | 7.3484e-05 | 0.14826 | 0.14826 | 0.14826 | 0.99285 | -0.049716 | 0.99488 | -0.035603 | 18.3033
85 | 0.020681 | 0.0051826 | -0.020673 | -0.0051798 | 7.7521e-06 | 2.8144e-06 | 0.030995 | 0.030995 | 0.030995 | 0.99285 | -0.049716 | 0.99247 | -0.052425 | 11.4797
86 | 0.019207 | 0.0048122 | -0.019198 | -0.0048091 | 8.5832e-06 | 3.087e-06 | 0.028796 | 0.028796 | 0.028796 | 0.99247 | -0.052425 | 0.99201 | -0.055657 | 10.6653
87 | -0.02773 | -0.0069614 | 0.027757 | 0.0069713 | 2.6508e-05 | 9.8777e-06 | 0.041589 | 0.041589 | 0.041589 | 0.99226 | -0.054126 | 0.99324 | -0.04725 | 15.4034
88 | -0.028134 | -0.0070658 | 0.028154 | 0.0070727 | 2.0306e-05 | 6.8613e-06 | 0.042154 | 0.042154 | 0.042154 | 0.99324 | -0.04725 | 0.99397 | -0.042061 | 7.8063
89 | 0.007476 | 0.0018734 | -0.0074749 | -0.0018732 | 1.114e-06 | 2.452e-07 | 0.011214 | 0.011214 | 0.011214 | 0.99201 | -0.055657 | 0.99186 | -0.056733 | 4.1533
90 | 0.0054422 | 0.0013637 | -0.005441 | -0.0013637 | 1.1264e-06 | 8.3789e-08 | 0.0081644 | 0.0081645 | 0.0081645 | 0.99186 | -0.056733 | 0.99165 | -0.058229 | 3.0239
91 | -0.0044656 | -0.001119 | 0.0044657 | 0.001119 | 8.9769e-08 | -3.7936e-09 | 0.0068289 | 0.0068289 | 0.0068289 | 0.97305 | -0.18989 | 0.97307 | -0.18974 | 2.5292
92 | -0.0056005 | -0.0014034 | 0.0056007 | 0.0014034 | 2.3577e-07 | 2.6686e-08 | 0.0085642 | 0.0085642 | 0.0085642 | 0.97307 | -0.18974 | 0.97311 | -0.18944 | 3.1719
93 | -0.0071482 | -0.0017913 | 0.0071487 | 0.0017914 | 4.967e-07 | 1.0826e-07 | 0.01093 | 0.01093 | 0.01093 | 0.97311 | -0.18944 | 0.97318 | -0.18893 | 4.0483
94 | 0.056981 | 0.014302 | -0.056964 | -0.014296 | 1.7009e-05 | 6.1025e-06 | 0.08519 | 0.08519 | 0.08519 | 0.99537 | -0.032247 | 0.99507 | -0.034397 | 10.5173
95 | -0.070625 | -0.017722 | 0.070662 | 0.017735 | 3.7496e-05 | 1.379e-05 | 0.10559 | 0.10559 | 0.10559 | 0.99537 | -0.032247 | 0.99592 | -0.028423 | 13.0354
96 | 0.056344 | 0.014141 | -0.056332 | -0.014136 | 1.2156e-05 | 4.3548e-06 | 0.084264 | 0.084264 | 0.084264 | 0.99507 | -0.034397 | 0.99485 | -0.035952 | 10.4029
97 | 0.007882 | 0.0019751 | -0.0078808 | -0.0019748 | 1.1818e-06 | 2.7685e-07 | 0.011776 | 0.011776 | 0.011776 | 0.99592 | -0.028423 | 0.99577 | -0.029506 | 4.3617
98 | 0.050023 | 0.012555 | -0.050019 | -0.012554 | 3.3918e-06 | 1.1911e-06 | 0.074826 | 0.074826 | 0.074826 | 0.99485 | -0.035952 | 0.99478 | -0.03644 | 9.2378
99 | 0.0059827 | 0.0014991 | -0.0059809 | -0.0014989 | 1.7898e-06 | 2.2171e-07 | 0.0089401 | 0.0089403 | 0.0089403 | 0.99577 | -0.029506 | 0.99546 | -0.031668 | 3.3112
100 | 0.036594 | 0.0091893 | -0.036586 | -0.0091867 | 8.0754e-06 | 2.6015e-06 | 0.054745 | 0.054745 | 0.054745 | 0.99478 | -0.03644 | 0.99455 | -0.038028 | 6.7587
101 | 0.0028035 | 0.00070256 | -0.0028034 | -0.00070261 | 5.2833e-08 | -4.2356e-08 | 0.0041906 | 0.0041907 | 0.0041907 | 0.99546 | -0.031668 | 0.99544 | -0.031804 | 1.5521
102 | 0.029436 | 0.0073954 | -0.029419 | -0.0073897 | 1.6508e-05 | 5.6418e-06 | 0.044047 | 0.044048 | 0.044048 | 0.99455 | -0.038028 | 0.99397 | -0.042061 | 8.157
103 | 0.0071505 | 0.0017914 | -0.0071474 | -0.0017907 | 3.0718e-06 | 6.2355e-07 | 0.010698 | 0.010698 | 0.010698 | 0.99455 | -0.038028 | 0.99411 | -0.041134 | 3.9623
104 | -0.015523 | -0.0038902 | 0.01553 | 0.0038928 | 7.5296e-06 | 2.6295e-06 | 0.023731 | 0.023731 | 0.023731 | 0.97333 | -0.18785 | 0.97382 | -0.18435 | 8.7892
105 | 0.013761 | 0.0034487 | -0.013761 | -0.0034486 | 4.7081e-07 | 1.5989e-07 | 0.021038 | 0.021038 | 0.021038 | 0.97333 | -0.18785 | 0.9733 | -0.1881 | 7.7918
106 | -0.019076 | -0.0047815 | 0.019077 | 0.0047818 | 7.0446e-07 | 2.5442e-07 | 0.029149 | 0.029149 | 0.029149 | 0.97382 | -0.18435 | 0.97386 | -0.18408 | 10.796
107 | 0.0099311 | 0.0024888 | -0.0099299 | -0.0024884 | 1.1498e-06 | 3.429e-07 | 0.015183 | 0.015183 | 0.015183 | 0.9733 | -0.1881 | 0.97318 | -0.18893 | 5.6233
108 | -0.021838 | -0.0054737 | 0.021839 | 0.0054742 | 1.2725e-06 | 4.6662e-07 | 0.033368 | 0.033368 | 0.033368 | 0.97386 | -0.18408 | 0.97391 | -0.18366 | 12.3584
109 | -0.024653 | -0.0061794 | 0.024692 | 0.0061938 | 3.902e-05 | 1.4458e-05 | 0.037667 | 0.037666 | 0.037667 | 0.97391 | -0.18366 | 0.9755 | -0.17225 | 13.9506
110 | -0.026136 | -0.0065559 | 0.026155 | 0.0065628 | 1.8477e-05 | 6.8738e-06 | 0.03987 | 0.03987 | 0.03987 | 0.9755 | -0.17225 | 0.97622 | -0.16715 | 14.7667
111 | -0.0037785 | -0.00094643 | 0.0037785 | 0.00094642 | 2.1595e-08 | -5.7219e-09 | 0.0056556 | 0.0056556 | 0.0056556 | 0.9941 | -0.041175 | 0.99411 | -0.041134 | 2.0947
112 | 0.0035492 | 0.00088897 | -0.0035483 | -0.00088929 | 9.1182e-07 | -3.2038e-07 | 0.0053124 | 0.0053127 | 0.0053127 | 0.9941 | -0.041175 | 0.99384 | -0.043032 | 1.9677

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22603 | 0.056729

## res_load
| p_mw | q_mvar
0 | 0.00056793 | 0.00014234
1 | 0.00042678 | 0.00010696
2 | 0.00040357 | 0.00010114
3 | 0.0019516 | 0.00048912
4 | 0.0006981 | 0.00017496
5 | 0.001532 | 0.00038395
6 | 0.00029783 | 7.4643e-05
7 | 0.00023435 | 5.8734e-05
8 | 0.00031011 | 7.7722e-05
9 | 0.0018406 | 0.00046129
10 | 0.0022874 | 0.00057327
11 | 0.00017204 | 4.3118e-05
12 | 0.0018144 | 0.00045473
13 | 0.00042498 | 0.00010651
14 | 0.00019387 | 4.8588e-05
15 | 0.00048555 | 0.00012169
16 | 0.0014902 | 0.00037347
17 | 0.00022644 | 5.6752e-05
18 | 0.00042688 | 0.00010699
19 | 0.00026117 | 6.5454e-05
20 | 0.00049129 | 0.00012313
21 | 0.00052568 | 0.00013175
22 | 0.0010203 | 0.00025572
23 | 0.0012041 | 0.00030178
24 | 0.00037006 | 9.2746e-05
25 | 0.00086151 | 0.00021591
26 | 0.00025133 | 6.299e-05
27 | 0.0016797 | 0.00042098
28 | 0.002689 | 0.00067393
29 | 0.0010771 | 0.00026995
30 | 0.001463 | 0.00036666
31 | 0.0050416 | 0.0012635
32 | 0.00079154 | 0.00019838
33 | 0.0037246 | 0.00093348
34 | 0.0064886 | 0.0016262
35 | 0.0014155 | 0.00035475
36 | 0.0018502 | 0.00046372
37 | 0.028141 | 0.0070529
38 | 0.0027016 | 0.00067709
39 | 0.0023319 | 0.00058443
40 | 0.0018061 | 0.00045265
41 | 0.0049927 | 0.0012513
42 | 0.0021346 | 0.00053498
43 | 0.0011258 | 0.00028214
44 | 0.0011951 | 0.00029953
45 | 0.0027668 | 0.00069343
46 | 0.00064494 | 0.00016164
47 | 0.00028508 | 7.1449e-05
48 | 0.00030223 | 7.5747e-05
49 | 0.00028668 | 7.1848e-05
50 | 0.00022244 | 5.5749e-05
51 | 0.00059866 | 0.00015004
52 | 0.0030132 | 0.00075517
53 | 0.0013676 | 0.00034276
54 | 0.0028561 | 0.00071581
55 | 0.0025357 | 0.0006355
56 | 0.0018082 | 0.00045318
57 | 0.0027782 | 0.00069627
58 | 0.001732 | 0.00043409
59 | 0.0015962 | 0.00040004
60 | 0.0029531 | 0.0007401
61 | 0.0016816 | 0.00042145
62 | 0.00243 | 0.00060902
63 | 0.0025683 | 0.00064368
64 | 0.0019706 | 0.00049387
65 | 0.0022843 | 0.0005725
66 | 0.0014667 | 0.00036759
67 | 0.0014126 | 0.00035402
68 | 0.00037715 | 9.4522e-05
69 | 0.0020327 | 0.00050944
70 | 0.005441 | 0.0013637
71 | 0.0052122 | 0.0013063
72 | 0.0011372 | 0.00028501
73 | 0.0011348 | 0.0002844
74 | 0.0015475 | 0.00038783
75 | 0.013644 | 0.0034196
76 | 0.00061951 | 0.00015526
77 | 0.0063095 | 0.0015813
78 | 0.0018981 | 0.0004757
79 | 0.013425 | 0.0033646
80 | 0.0031774 | 0.00079634
81 | 0.0028034 | 0.00070261
82 | 0.0017614 | 0.00044146
83 | 0.003546 | 0.00088872
84 | 0.0038297 | 0.00095981
85 | 0.0027609 | 0.00069196
86 | 0.0027812 | 0.00069704
87 | 0.0028136 | 0.00070516
88 | 0.0014447 | 0.00036207
89 | 0.0030454 | 0.00076324
90 | 0.0024422 | 0.00061208
91 | 0.00022926 | 5.7458e-05
92 | 0.0033689 | 0.00084432
93 | 0.0035483 | 0.00088929
94 | 0.001265 | 0.00031704

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1