## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1136-7_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1136-7_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1136-7_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1136-7_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1136-7_0_2_node_6 | 0.4 | n |  | TRUE
5 | bus_LV_1136-7_0_2_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1136-7_0_2_node_8 | 0.4 | n |  | TRUE
7 | bus_LV_1136-7_0_2_node_66 | 0.4 | n |  | TRUE
8 | bus_LV_1136-7_0_2_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1136-7_0_2_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1136-7_0_2_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1136-7_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_1136-7_0_2_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1136-7_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1136-7_0_2_node_13 | 0.4 | n |  | TRUE
15 | bus_LV_1136-7_0_2_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_1136-7_0_2_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1136-7_0_2_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1136-7_0_2_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1136-7_0_2_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1136-7_0_2_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1136-7_0_2_node_19 | 0.4 | n |  | TRUE
22 | bus_LV_1136-7_0_2_node_20 | 0.4 | n |  | TRUE
23 | bus_LV_1136-7_0_2_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1136-7_0_2_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1136-7_0_2_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_1136-7_0_2_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1136-7_0_2_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_1136-7_0_2_node_65 | 0.4 | n |  | TRUE
29 | bus_LV_1136-7_0_2_node_78 | 0.4 | n |  | TRUE
30 | bus_LV_1136-7_0_2_node_201 | 0.4 | n |  | TRUE
31 | bus_LV_1136-7_0_2_node_202 | 0.4 | n |  | TRUE
32 | bus_LV_1136-7_0_2_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1136-7_0_2_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1136-7_0_2_node_81 | 0.4 | n |  | TRUE
35 | bus_LV_1136-7_0_2_node_44 | 0.4 | n |  | TRUE
36 | bus_LV_1136-7_0_2_node_45 | 0.4 | n |  | TRUE
37 | bus_LV_1136-7_0_2_node_46 | 0.4 | n |  | TRUE
38 | bus_LV_1136-7_0_2_node_79 | 0.4 | n |  | TRUE
39 | bus_LV_1136-7_0_2_node_85 | 0.4 | n |  | TRUE
40 | bus_LV_1136-7_0_2_node_47 | 0.4 | n |  | TRUE
41 | bus_LV_1136-7_0_2_node_48 | 0.4 | n |  | TRUE
42 | bus_LV_1136-7_0_2_node_49 | 0.4 | n |  | TRUE
43 | bus_LV_1136-7_0_2_node_50 | 0.4 | n |  | TRUE
44 | bus_LV_1136-7_0_2_node_74 | 0.4 | n |  | TRUE
45 | bus_LV_1136-7_0_2_node_52 | 0.4 | n |  | TRUE
46 | bus_LV_1136-7_0_2_node_88 | 0.4 | n |  | TRUE
47 | bus_LV_1136-7_0_2_node_89 | 0.4 | n |  | TRUE
48 | bus_LV_1136-7_0_2_node_61 | 0.4 | n |  | TRUE
49 | bus_LV_1136-7_0_2_node_62 | 0.4 | n |  | TRUE
50 | bus_LV_1136-7_0_2_node_63 | 0.4 | n |  | TRUE
51 | bus_LV_1136-7_0_2_node_64 | 0.4 | n |  | TRUE
52 | bus_LV_1136-7_0_2_node_83 | 0.4 | n |  | TRUE
53 | bus_LV_1136-7_0_2_node_67 | 0.4 | n |  | TRUE
54 | bus_LV_1136-7_0_2_node_68 | 0.4 | n |  | TRUE
55 | bus_LV_1136-7_0_2_node_70 | 0.4 | n |  | TRUE
56 | bus_LV_1136-7_0_2_node_84 | 0.4 | n |  | TRUE
57 | bus_LV_1136-7_0_2_node_71 | 0.4 | n |  | TRUE
58 | bus_LV_1136-7_0_2_node_82 | 0.4 | n |  | TRUE
59 | bus_LV_1136-7_0_2_node_72 | 0.4 | n |  | TRUE
60 | bus_LV_1136-7_0_2_node_73 | 0.4 | n |  | TRUE
61 | bus_LV_1136-7_0_2_node_75 | 0.4 | n |  | TRUE
62 | bus_LV_1136-7_0_2_node_76 | 0.4 | n |  | TRUE
63 | bus_LV_1136-7_0_2_node_206 | 0.4 | n |  | TRUE
64 | bus_LV_1136-7_0_2_node_116 | 0.4 | n |  | TRUE
65 | bus_LV_1136-7_0_2_node_77 | 0.4 | n |  | TRUE
66 | bus_LV_1136-7_0_2_node_80 | 0.4 | n |  | TRUE
67 | bus_LV_1136-7_0_2_node_86 | 0.4 | n |  | TRUE
68 | bus_LV_1136-7_0_2_node_87 | 0.4 | n |  | TRUE
69 | bus_LV_1136-7_0_2_node_92 | 0.4 | n |  | TRUE
70 | bus_LV_1136-7_0_2_node_90 | 0.4 | n |  | TRUE
71 | bus_LV_1136-7_0_2_node_91 | 0.4 | n |  | TRUE
72 | bus_LV_1136-7_0_2_node_94 | 0.4 | n |  | TRUE
73 | bus_LV_1136-7_0_2_node_93 | 0.4 | n |  | TRUE
74 | bus_LV_1136-7_0_2_node_97 | 0.4 | n |  | TRUE
75 | bus_LV_1136-7_0_2_node_98 | 0.4 | n |  | TRUE
76 | bus_LV_1136-7_0_2_node_99 | 0.4 | n |  | TRUE
77 | bus_LV_1136-7_0_2_node_100 | 0.4 | n |  | TRUE
78 | bus_LV_1136-7_0_2_node_106 | 0.4 | n |  | TRUE
79 | bus_LV_1136-7_0_2_node_110 | 0.4 | n |  | TRUE
80 | bus_LV_1136-7_0_2_node_101 | 0.4 | n |  | TRUE
81 | bus_LV_1136-7_0_2_node_107 | 0.4 | n |  | TRUE
82 | bus_LV_1136-7_0_2_node_104 | 0.4 | n |  | TRUE
83 | bus_LV_1136-7_0_2_node_105 | 0.4 | n |  | TRUE
84 | bus_LV_1136-7_0_2_node_108 | 0.4 | n |  | TRUE
85 | bus_LV_1136-7_0_2_node_114 | 0.4 | n |  | TRUE
86 | bus_LV_1136-7_0_2_node_115 | 0.4 | n |  | TRUE
87 | bus_MV_0_node_30 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1136-7_0_2_load_0 | 0 | 0.00051493 | 0.00012905 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1136-7_0_2_load_2 | 2 | 0.00029906 | 7.4952e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1136-7_0_2_load_3 | 3 | 0.0011849 | 0.00029696 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1136-7_0_2_load_66 | 7 | 0.00085272 | 0.00021371 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1136-7_0_2_load_7 | 8 | 0.0003628 | 9.0927e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1136-7_0_2_load_17 | 9 | 0.00046547 | 0.00011666 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1136-7_0_2_load_14 | 10 | 0.001071 | 0.00026841 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1136-7_0_2_load_9 | 11 | 0.0013441 | 0.00033687 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1136-7_0_2_load_10 | 12 | 0.00037674 | 9.442e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1136-7_0_2_load_21 | 15 | 0.0013214 | 0.00033117 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1136-7_0_2_load_18 | 16 | 0.0003108 | 7.7893e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1136-7_0_2_load_15 | 17 | 0.0017141 | 0.00042959 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1136-7_0_2_load_22 | 20 | 0.00039427 | 9.8813e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1136-7_0_2_load_23 | 23 | 0.0017135 | 0.00042944 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1136-7_0_2_load_29 | 27 | 0.00070741 | 0.00017729 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1136-7_0_2_load_78 | 29 | 0.0001163 | 2.9147e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1136-7_0_2_load_201 | 30 | 0.00036821 | 9.2282e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1136-7_0_2_load_202 | 31 | 0.00058072 | 0.00014554 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1136-7_0_2_load_30 | 32 | 0.0004252 | 0.00010657 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1136-7_0_2_load_31 | 33 | 0.00057248 | 0.00014348 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1136-7_0_2_load_81 | 34 | 0.00014491 | 3.6318e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1136-7_0_2_load_44 | 35 | 0.00021897 | 5.4879e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1136-7_0_2_load_45 | 36 | 9.5207e-05 | 2.3861e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1136-7_0_2_load_85 | 39 | 0.001207 | 0.0003025 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1136-7_0_2_load_47 | 40 | 0.00025606 | 6.4174e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1136-7_0_2_load_52 | 45 | 0.00065201 | 0.00016341 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1136-7_0_2_load_88 | 46 | 0.00036134 | 9.0561e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1136-7_0_2_load_89 | 47 | 8.438e-05 | 2.1148e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1136-7_0_2_load_61 | 48 | 0.00096095 | 0.00024084 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1136-7_0_2_load_62 | 49 | 0.00013664 | 3.4246e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1136-7_0_2_load_63 | 50 | 0.00020401 | 5.113e-05 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1136-7_0_2_load_64 | 51 | 9.1364e-05 | 2.2898e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1136-7_0_2_load_67 | 53 | 0.00047141 | 0.00011815 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1136-7_0_2_load_68 | 54 | 9.9019e-05 | 2.4816e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1136-7_0_2_load_84 | 56 | 5.9915e-05 | 1.5016e-05 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1136-7_0_2_load_71 | 57 | 0.00019585 | 4.9084e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1136-7_0_2_load_82 | 58 | 0.00050071 | 0.00012549 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1136-7_0_2_load_72 | 59 | 0.00014879 | 3.7291e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1136-7_0_2_load_73 | 60 | 0.00042686 | 0.00010698 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1136-7_0_2_load_75 | 61 | 0.00010688 | 2.6787e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1136-7_0_2_load_206 | 63 | 0.00067153 | 0.0001683 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1136-7_0_2_load_77 | 65 | 0.00023234 | 5.823e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1136-7_0_2_load_80 | 66 | 4.7274e-05 | 1.1848e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1136-7_0_2_load_87 | 68 | 0.00015882 | 3.9805e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1136-7_0_2_load_92 | 69 | 0.00039454 | 9.888e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1136-7_0_2_load_91 | 71 | 0.00011152 | 2.795e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1136-7_0_2_load_94 | 72 | 5.1889e-05 | 1.3005e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1136-7_0_2_load_93 | 73 | 0.00024865 | 6.2317e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1136-7_0_2_load_97 | 74 | 0.00068187 | 0.00017089 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1136-7_0_2_load_98 | 75 | 0.00013941 | 3.4938e-05 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1136-7_0_2_load_99 | 76 | 0.00013179 | 3.3029e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1136-7_0_2_load_101 | 80 | 0.00037099 | 9.298e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1136-7_0_2_load_107 | 81 | 0.00017893 | 4.4844e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1136-7_0_2_load_104 | 82 | 0.00023169 | 5.8067e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1136-7_0_2_load_105 | 83 | 0.00020876 | 5.2321e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1136-7_0_2_load_108 | 84 | 0.00016757 | 4.1997e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1136-7_0_2_load_114 | 85 | 0.00027634 | 6.9258e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1136-7_0_2_load_115 | 86 | 0.00021981 | 5.509e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 32 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1136-7_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.095299 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1136-7_0_2_line_1 | NAYY 4x150 SE | 1 | 2 | 0.21254 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1136-7_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.015146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1136-7_0_2_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0051281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1136-7_0_2_line_4 | NAYY 4x150 SE | 4 | 8 | 0.016573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1136-7_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.64947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1136-7_0_2_line_6 | NAYY 4x150 SE | 5 | 6 | 0.90459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1136-7_0_2_line_7 | NAYY 4x150 SE | 5 | 7 | 0.026633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1136-7_0_2_line_8 | NAYY 4x150 SE | 6 | 9 | 0.020229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1136-7_0_2_line_9 | NAYY 4x150 SE | 6 | 10 | 0.0012533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1136-7_0_2_line_10 | NAYY 4x150 SE | 9 | 20 | 0.0021999 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1136-7_0_2_line_11 | NAYY 4x150 SE | 10 | 17 | 0.039327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1136-7_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.03918 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1136-7_0_2_line_13 | NAYY 4x150 SE | 11 | 13 | 0.22595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1136-7_0_2_line_14 | NAYY 4x150 SE | 13 | 14 | 0.29267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1136-7_0_2_line_15 | NAYY 4x150 SE | 14 | 15 | 0.085361 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1136-7_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.26357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1136-7_0_2_line_17 | NAYY 4x150 SE | 15 | 19 | 0.29123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1136-7_0_2_line_18 | NAYY 4x150 SE | 16 | 21 | 0.019324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1136-7_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.050145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1136-7_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.1127 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1136-7_0_2_line_21 | NAYY 4x150 SE | 19 | 24 | 0.29978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1136-7_0_2_line_22 | NAYY 4x150 SE | 19 | 25 | 0.48638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1136-7_0_2_line_23 | NAYY 4x150 SE | 21 | 22 | 0.008741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1136-7_0_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.019439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1136-7_0_2_line_25 | NAYY 4x150 SE | 24 | 26 | 0.31881 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1136-7_0_2_line_26 | NAYY 4x150 SE | 24 | 27 | 0.010606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1136-7_0_2_line_27 | NAYY 4x150 SE | 25 | 30 | 0.017711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1136-7_0_2_line_28 | NAYY 4x150 SE | 25 | 31 | 0.019047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1136-7_0_2_line_29 | NAYY 4x150 SE | 26 | 28 | 0.41657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1136-7_0_2_line_30 | NAYY 4x150 SE | 26 | 29 | 0.51765 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1136-7_0_2_line_31 | NAYY 4x150 SE | 27 | 32 | 0.19512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1136-7_0_2_line_32 | NAYY 4x150 SE | 28 | 52 | 0.49 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1136-7_0_2_line_33 | NAYY 4x150 SE | 28 | 51 | 0.035169 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1136-7_0_2_line_34 | NAYY 4x150 SE | 29 | 65 | 0.03804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1136-7_0_2_line_35 | NAYY 4x150 SE | 32 | 33 | 0.035061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1136-7_0_2_line_36 | NAYY 4x150 SE | 33 | 34 | 0.02453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1136-7_0_2_line_37 | NAYY 4x150 SE | 34 | 43 | 0.03142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1136-7_0_2_line_38 | NAYY 4x150 SE | 35 | 36 | 0.0047047 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1136-7_0_2_line_39 | NAYY 4x150 SE | 36 | 37 | 0.013401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1136-7_0_2_line_40 | NAYY 4x150 SE | 37 | 38 | 0.061675 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1136-7_0_2_line_41 | NAYY 4x150 SE | 37 | 39 | 0.027105 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1136-7_0_2_line_42 | NAYY 4x150 SE | 38 | 66 | 0.24669 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1136-7_0_2_line_43 | NAYY 4x150 SE | 38 | 65 | 0.40628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1136-7_0_2_line_44 | NAYY 4x150 SE | 39 | 67 | 0.40346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1136-7_0_2_line_45 | NAYY 4x150 SE | 40 | 41 | 0.08956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1136-7_0_2_line_46 | NAYY 4x150 SE | 40 | 42 | 0.012503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1136-7_0_2_line_47 | NAYY 4x150 SE | 41 | 43 | 0.35939 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1136-7_0_2_line_48 | NAYY 4x150 SE | 41 | 44 | 0.46889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1136-7_0_2_line_49 | NAYY 4x150 SE | 42 | 45 | 0.026082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1136-7_0_2_line_50 | NAYY 4x150 SE | 43 | 46 | 0.019397 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1136-7_0_2_line_51 | NAYY 4x150 SE | 44 | 62 | 0.24567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1136-7_0_2_line_52 | NAYY 4x150 SE | 44 | 59 | 0.48639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1136-7_0_2_line_53 | NAYY 4x150 SE | 45 | 47 | 0.0035997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1136-7_0_2_line_54 | NAYY 4x150 SE | 47 | 70 | 0.043966 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1136-7_0_2_line_55 | NAYY 4x150 SE | 48 | 49 | 0.029403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1136-7_0_2_line_56 | NAYY 4x150 SE | 48 | 50 | 0.022846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1136-7_0_2_line_57 | NAYY 4x150 SE | 49 | 51 | 0.013374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1136-7_0_2_line_58 | NAYY 4x150 SE | 52 | 56 | 0.045876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1136-7_0_2_line_59 | NAYY 4x150 SE | 52 | 58 | 0.018096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1136-7_0_2_line_60 | NAYY 4x150 SE | 53 | 54 | 0.052067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1136-7_0_2_line_61 | NAYY 4x150 SE | 54 | 55 | 0.023136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1136-7_0_2_line_62 | NAYY 4x150 SE | 55 | 56 | 0.025014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1136-7_0_2_line_63 | NAYY 4x150 SE | 57 | 58 | 0.014176 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1136-7_0_2_line_64 | NAYY 4x150 SE | 59 | 60 | 0.024582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1136-7_0_2_line_65 | NAYY 4x150 SE | 60 | 61 | 0.020624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1136-7_0_2_line_66 | NAYY 4x150 SE | 62 | 63 | 0.16556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1136-7_0_2_line_67 | NAYY 4x150 SE | 62 | 64 | 0.10032 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1136-7_0_2_line_68 | NAYY 4x150 SE | 64 | 86 | 0.10706 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1136-7_0_2_line_69 | NAYY 4x150 SE | 67 | 68 | 0.041791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1136-7_0_2_line_70 | NAYY 4x150 SE | 68 | 69 | 0.00069516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1136-7_0_2_line_71 | NAYY 4x150 SE | 69 | 73 | 0.02305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1136-7_0_2_line_72 | NAYY 4x150 SE | 70 | 71 | 0.39454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1136-7_0_2_line_73 | NAYY 4x150 SE | 71 | 72 | 0.64396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1136-7_0_2_line_74 | NAYY 4x150 SE | 74 | 75 | 0.032578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1136-7_0_2_line_75 | NAYY 4x150 SE | 74 | 76 | 0.016227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1136-7_0_2_line_76 | NAYY 4x150 SE | 76 | 77 | 0.031082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1136-7_0_2_line_77 | NAYY 4x150 SE | 77 | 78 | 0.19854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1136-7_0_2_line_78 | NAYY 4x150 SE | 77 | 79 | 0.026702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1136-7_0_2_line_79 | NAYY 4x150 SE | 78 | 83 | 0.015781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1136-7_0_2_line_80 | NAYY 4x150 SE | 79 | 85 | 0.093096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1136-7_0_2_line_81 | NAYY 4x150 SE | 79 | 84 | 0.039404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1136-7_0_2_line_82 | NAYY 4x150 SE | 80 | 81 | 0.074473 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1136-7_0_2_line_83 | NAYY 4x150 SE | 81 | 84 | 0.022512 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1136-7_0_2_line_84 | NAYY 4x150 SE | 82 | 83 | 0.055477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1136-7_0_2_line_85 | NAYY 4x150 SE | 85 | 86 | 0.05303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1136-7_0_2_trafo_30 | 0.25 MVA 20/0.4 kV | 87 | 32 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53
0 | 2642766.597 | 1211252.2589 | 2642769.7607 | 1211237.0393 | 2642772.8903 | 1211234.0044 | 2642778.3618 | 1211231.8201 | 2642792.056 | 1211233.7416 | 2642798.1476 | 1211236.22 | 2642802.9613 | 1211239.9234 | 2642807.8357 | 1211242.5932 | 2642822.2911 | 1211244.3312 | 2642831.7133 | 1211245.3994 | 2642836.7808 | 1211248.6932 | 2642840.0203 | 1211252.5743 | 2642840.6317 | 1211254.8189
1 | 2642766.597 | 1211252.2589 | 2642760.7359 | 1211252.6171 | 2642736.0545 | 1211254.875 | 2642726.8908 | 1211253.7866 | 2642715.4587 | 1211250.0582 | 2642701.8435 | 1211243.4681 | 2642693.5809 | 1211237.5055 | 2642680.3667 | 1211225.8376 | 2642674.5288 | 1211222.9386 | 2642665.7205 | 1211222.0752 | 2642625.7865 | 1211220.3668 | 2642602.2171 | 1211216.941 | 2642589.0052 | 1211212.3774 | 2642576.0111 | 1211204.9694 | 2642568.8608 | 1211198.5722
2 | 2642766.597 | 1211252.2589 | 2642771.0697 | 1211253.714 | 2642774.3594 | 1211256.9728 | 2642776.4601 | 1211262.3922
3 | 2642778.3135 | 1211267.1737 | 2642776.4601 | 1211262.3922
4 | 2642787.3855 | 1211281.0579 | 2642778.3135 | 1211267.1737
5 | 2642778.3135 | 1211267.1737 | 2642775.9317 | 1211275.0834 | 2642774.381 | 1211283.6328 | 2642774.6699 | 1211293.1627 | 2642778.6482 | 1211307.4106 | 2642788.8793 | 1211330.2416 | 2642793.6658 | 1211344.0951 | 2642798.1039 | 1211351.4311 | 2642809.0746 | 1211363.3056 | 2642835.6427 | 1211380.7729 | 2642864.083 | 1211393.5734 | 2642886.1649 | 1211405.0942 | 2642914.9174 | 1211431.5162 | 2642927.7632 | 1211444.6161 | 2642936.7827 | 1211451.9853 | 2642940.0056 | 1211457.0892 | 2642940.2215 | 1211462.9942 | 2642936.043 | 1211469.2456 | 2642933.2708 | 1211476.4743 | 2642933.3859 | 1211488.9824 | 2642992.4631 | 1211503.7272 | 2642999.4156 | 1211505.834 | 2643007.9946 | 1211508.9309 | 2643014.479 | 1211511.6681 | 2643055.5502 | 1211533.4657 | 2643075.1571 | 1211540.3667 | 2643171.2708 | 1211546.2421 | 2643228.579 | 1211549.1029 | 2643235.814 | 1211546.7984 | 2643242.9014 | 1211543.9036 | 2643249.6361 | 1211540.3948 | 2643261.2844 | 1211533.0416 | 2643265.599 | 1211530.06
6 | 2642532.6501 | 1211783.152 | 2642529.841 | 1211759.407 | 2642536.6754 | 1211753.5301 | 2642543.2545 | 1211741.9258 | 2642550.3235 | 1211720.2079 | 2642557.8743 | 1211675.7025 | 2642559.5666 | 1211668.5327 | 2642562.6192 | 1211661.328 | 2642566.7927 | 1211653.5755 | 2642597.2966 | 1211610.3012 | 2642615.2054 | 1211589.0277 | 2642626.1584 | 1211576.7766 | 2642632.8034 | 1211570.8761 | 2642642.7004 | 1211564.9878 | 2642685.6521 | 1211543.9047 | 2642692.9903 | 1211540.9555 | 2642704.1148 | 1211538.7337 | 2642716.4393 | 1211538.7219 | 2642740.6639 | 1211542.7865 | 2642773.4461 | 1211547.6241 | 2642804.0536 | 1211547.3877 | 2642816.3326 | 1211546.2974 | 2642828.6206 | 1211543.9619 | 2642846.6931 | 1211541.3123 | 2642856.0379 | 1211540.401 | 2642872.7313 | 1211543.5672 | 2642887.151 | 1211550.1635 | 2642912.7192 | 1211566.0008 | 2642927.7335 | 1211574.4359 | 2642943.7894 | 1211580.6439 | 2642968.4271 | 1211584.2788 | 2643028.9265 | 1211588.1612 | 2643054.4122 | 1211586.922 | 2643160.9479 | 1211565.7566 | 2643228.579 | 1211549.1029 | 2643235.814 | 1211546.7984 | 2643242.9014 | 1211543.9036 | 2643249.6361 | 1211540.3948 | 2643261.2844 | 1211533.0416 | 2643265.599 | 1211530.06
7 | 2642532.6501 | 1211783.152 | 2642535.7735 | 1211809.6011
8 | 2643265.599 | 1211530.06 | 2643271.629 | 1211534.673 | 2643275.5112 | 1211536.8469 | 2643278.7325 | 1211537.9375 | 2643282.7546 | 1211538.6338 | 2643283.4584 | 1211538.6544
9 | 2643265.599 | 1211530.06 | 2643266.6297 | 1211529.3468
10 | 2643283.4584 | 1211538.6544 | 2643285.6574 | 1211538.7188
11 | 2643298.4119 | 1211506.3605 | 2643297.8158 | 1211507.0246 | 2643292.737 | 1211511.646 | 2643285.9747 | 1211516.8555 | 2643271.4181 | 1211526.0331 | 2643266.6297 | 1211529.3468
12 | 2643206.5718 | 1211070.5977 | 2643209.255 | 1211078.1557 | 2643210.1028 | 1211082.809 | 2643210.7478 | 1211088.1724 | 2643210.9565 | 1211090.8421 | 2643211.946 | 1211094.8071 | 2643218.944 | 1211107.2357
13 | 2643366.0063 | 1211253.5608 | 2643361.8059 | 1211257.5215 | 2643356.4577 | 1211260.4844 | 2643352.2762 | 1211261.8437 | 2643348.8027 | 1211261.9741 | 2643345.4147 | 1211260.7933 | 2643327.5691 | 1211250.8802 | 2643323.2691 | 1211247.6138 | 2643317.6821 | 1211240.5691 | 2643311.9383 | 1211233.1343 | 2643289.7142 | 1211209.804 | 2643277.239 | 1211196.9727 | 2643269.5435 | 1211190.4131 | 2643261.4421 | 1211183.2392 | 2643254.4806 | 1211173.95 | 2643246.9162 | 1211162.9221 | 2643238.6713 | 1211147.2199 | 2643228.1435 | 1211123.5744 | 2643218.944 | 1211107.2357
14 | 2643534.863 | 1211093.2297 | 2643493.827 | 1211083.1025 | 2643481.0984 | 1211081.0864 | 2643466.6608 | 1211081.0479 | 2643440.2339 | 1211082.8678 | 2643426.2326 | 1211085.5341 | 2643420.4978 | 1211088.3385 | 2643416.7668 | 1211091.4688 | 2643413.9517 | 1211096.1399 | 2643405.1349 | 1211119.4116 | 2643395.6297 | 1211151.6723 | 2643390.8567 | 1211171.6604 | 2643386.1743 | 1211209.5039 | 2643383.8699 | 1211219.1928 | 2643378.143 | 1211231.3916 | 2643370.2215 | 1211247.5768 | 2643366.0063 | 1211253.5608
15 | 2643534.863 | 1211093.2297 | 2643531.5029 | 1211095.4954 | 2643526.9271 | 1211097.7633 | 2643521.2005 | 1211099.4448 | 2643513.5012 | 1211100.7116 | 2643498.2582 | 1211101.7234 | 2643490.9642 | 1211102.6375 | 2643486.0077 | 1211103.9688 | 2643481.7211 | 1211106.1722 | 2643478.9987 | 1211108.5315 | 2643474.9282 | 1211114.4498 | 2643468.936 | 1211125.4792 | 2643466.0176 | 1211131.302
16 | 2643534.863 | 1211093.2297 | 2643539.5017 | 1211088.5941 | 2643543.018 | 1211083.6502 | 2643545.6164 | 1211078.4995 | 2643546.972 | 1211073.929 | 2643547.5085 | 1211070.1752 | 2643547.8719 | 1211062.0286 | 2643548.0161 | 1211028.7325 | 2643548.6685 | 1211022.6449 | 2643550.021 | 1211018.4856 | 2643551.9609 | 1211015.0645 | 2643554.128 | 1211012.7901 | 2643557.1129 | 1211010.9219 | 2643560.6855 | 1211009.725 | 2643567.1585 | 1211008.8606 | 2643577.9193 | 1211007.7274 | 2643588.4358 | 1211005.7141 | 2643596.9581 | 1211003.1081 | 2643604.0701 | 1211000.0805 | 2643608.6734 | 1210997.1791 | 2643612.4691 | 1210993.5492 | 2643615.2476 | 1210989.7561 | 2643617.618 | 1210985.66 | 2643619.4885 | 1210981.3489 | 2643620.7481 | 1210977.4447 | 2643620.9791 | 1210972.8771 | 2643620.9061 | 1210968.3072 | 2643618.6429 | 1210957.729 | 2643613.8712 | 1210941.0288 | 2643611.359 | 1210922.9333 | 2643610.4996 | 1210901.1811 | 2643610.5307 | 1210889.6524 | 2643611.3334 | 1210881.9177
17 | 2643413.6028 | 1211393.7105 | 2643405.0916 | 1211370.8575 | 2643404.4183 | 1211367.3173 | 2643404.6315 | 1211364.1169 | 2643405.334 | 1211361.5539 | 2643407.0998 | 1211359.0653 | 2643409.1355 | 1211357.0678 | 2643412.1599 | 1211354.9552 | 2643419.3005 | 1211351.0493 | 2643428.9185 | 1211345.0269 | 2643437.3342 | 1211337.1613 | 2643444.1221 | 1211328.4723 | 2643455.8847 | 1211308.6464 | 2643467.6903 | 1211282.9284 | 2643469.1735 | 1211275.4238 | 2643468.8342 | 1211265.6712 | 2643461.9317 | 1211233.7245 | 2643456.7354 | 1211191.829 | 2643456.5426 | 1211161.9658 | 2643460.545 | 1211144.5181 | 2643463.6617 | 1211136.0025 | 2643466.0176 | 1211131.302
18 | 2643615.353 | 1210863.0499 | 2643611.7896 | 1210877.5212 | 2643611.3334 | 1210881.9177
19 | 2643326.1368 | 1211464.8833 | 2643320.7282 | 1211475.15 | 2643317.2272 | 1211482.2176 | 2643312.0495 | 1211489.9957 | 2643303.1397 | 1211501.0931 | 2643298.4119 | 1211506.3605
20 | 2643326.1368 | 1211464.8833 | 2643344.4543 | 1211447.3949 | 2643370.4182 | 1211427.5052 | 2643397.4112 | 1211407.1895 | 2643413.6028 | 1211393.7105
21 | 2643403.9443 | 1211584.985 | 2643399.5547 | 1211572.1567 | 2643400.8102 | 1211566.6849 | 2643403.4973 | 1211561.8238 | 2643415.1972 | 1211550.5356 | 2643424.6587 | 1211538.8198 | 2643437.4301 | 1211517.089 | 2643444.4747 | 1211501.2977 | 2643449.2426 | 1211493.4834 | 2643459.2854 | 1211485.4296 | 2643467.2995 | 1211477.3832 | 2643471.5743 | 1211473.6455 | 2643476.6965 | 1211470.392 | 2643499.9624 | 1211458.966 | 2643504.5259 | 1211456.2643 | 2643506.3232 | 1211454.6654 | 2643506.9868 | 1211453.2694 | 2643507.4335 | 1211451.416 | 2643507.522 | 1211449.6934 | 2643507.0485 | 1211447.9445 | 2643506.0443 | 1211447.0589 | 2643503.0663 | 1211445.9365 | 2643495.0341 | 1211443.9546 | 2643486.7891 | 1211441.9601 | 2643481.7043 | 1211440.0775 | 2643476.4044 | 1211437.4707 | 2643471.0632 | 1211434.2855 | 2643461.9263 | 1211427.4706 | 2643435.8235 | 1211404.8119 | 2643427.7374 | 1211395.6033 | 2643424.0967 | 1211389.4732 | 2643413.6028 | 1211393.7105
22 | 2643413.6028 | 1211393.7105 | 2643424.0967 | 1211389.4732 | 2643433.206 | 1211386.5156 | 2643449.6157 | 1211380.676 | 2643458.7153 | 1211376.9623 | 2643470.2215 | 1211371.4651 | 2643479.8125 | 1211366.0206 | 2643492.3676 | 1211358.3965 | 2643508.2015 | 1211347.1275 | 2643536.6605 | 1211325.9449 | 2643562.427 | 1211299.951 | 2643577.7382 | 1211285.3765 | 2643583.5312 | 1211277.7032 | 2643594.1444 | 1211260.315 | 2643602.378 | 1211250.3693 | 2643625.0134 | 1211230.7566 | 2643640.2149 | 1211215.6367 | 2643676.5206 | 1211172.1546 | 2643700.4572 | 1211142.0011 | 2643727.4346 | 1211103.3983 | 2643746.9846 | 1211077.7377 | 2643757.0439 | 1211062.4136
23 | 2643615.353 | 1210863.0499 | 2643617.9673 | 1210854.7086
24 | 2643617.9673 | 1210854.7086 | 2643613.7791 | 1210848.6078 | 2643609.7322 | 1210845.0206 | 2643603.819 | 1210842.0196
25 | 2643671.6672 | 1211605.8272 | 2643651.6821 | 1211593.6184 | 2643552.5944 | 1211545.6446 | 2643514.6274 | 1211523.5438 | 2643503.071 | 1211518.2565 | 2643492.28 | 1211516.3545 | 2643480.8502 | 1211518.706 | 2643472.4614 | 1211522.914 | 2643455.2295 | 1211538.4309 | 2643443.1356 | 1211548.5043 | 2643418.799 | 1211559.9006 | 2643411.0213 | 1211564.7246 | 2643405.8788 | 1211570.7797 | 2643404.195 | 1211577.6826 | 2643403.9443 | 1211584.985
26 | 2643403.9443 | 1211584.985 | 2643407.4802 | 1211594.9842
27 | 2643766.7727 | 1211047.5985 | 2643757.0439 | 1211062.4136
28 | 2643770.9529 | 1211075.4676 | 2643757.0439 | 1211062.4136
29 | 2643671.6672 | 1211605.8272 | 2643672.6299 | 1211630.0151 | 2643673.098 | 1211635.6106 | 2643674.5843 | 1211641.2137 | 2643676.7798 | 1211646.455 | 2643681.008 | 1211654.2571 | 2643686.2742 | 1211662.4671 | 2643695.1203 | 1211672.5822 | 2643705.847 | 1211683.2114 | 2643783.5635 | 1211756.3012 | 2643800.1569 | 1211777.0906 | 2643805.5776 | 1211783.8899 | 2643819.2714 | 1211806.3368 | 2643823.3478 | 1211816.1502 | 2643875.9595 | 1211942.7439 | 2643882.1791 | 1211953.4848
30 | 2643671.6672 | 1211605.8272 | 2643682.8112 | 1211603.0738 | 2643688.1144 | 1211601.0337 | 2643692.013 | 1211598.872 | 2643695.3991 | 1211596.1286 | 2643698.3184 | 1211592.7924 | 2643700.3894 | 1211589.0943 | 2643701.6875 | 1211586.1466 | 2643703.1899 | 1211578.1307 | 2643703.6421 | 1211569.2955 | 2643700.8809 | 1211529.2519 | 2643702.8519 | 1211510.1664 | 2643705.8396 | 1211492.3111 | 2643708.5373 | 1211485.0155 | 2643712.8671 | 1211478.9548 | 2643730.7004 | 1211464.4547 | 2643736.2505 | 1211457.7915 | 2643743.2751 | 1211444.8465 | 2643770.03 | 1211351.4994 | 2643774.391 | 1211343.2821 | 2643781.7828 | 1211335.2094 | 2643789.1465 | 1211332.0171 | 2643798.9387 | 1211330.2545 | 2643809.5381 | 1211330.3323 | 2643817.8722 | 1211333.651 | 2643831.4233 | 1211344.6346 | 2643845.4275 | 1211355.9996 | 2643856.1725 | 1211361.0704 | 2643870.8262 | 1211365.7363 | 2643885.6779 | 1211369.292 | 2643899.6896 | 1211376.5103 | 2643919.7789 | 1211389.0543 | 2643933.7875 | 1211395.6501 | 2643966.5101 | 1211410.4192
31 | 2643407.4802 | 1211594.9842 | 2643413.5261 | 1211612.0816 | 2643422.0276 | 1211647.6975 | 2643423.3436 | 1211663.1494 | 2643422.2469 | 1211702.1419 | 2643421.9234 | 1211718.3935 | 2643423.0032 | 1211734.9776 | 2643432.2402 | 1211787.1412
32 | 2644214.908 | 1212043.7036 | 2644205.4605 | 1212056.4967 | 2644199.0915 | 1212062.9533 | 2644182.2874 | 1212076.0365 | 2644171.4165 | 1212085.0947 | 2644158.8943 | 1212097.5983 | 2644152.539 | 1212103.2323 | 2644144.5593 | 1212107.6426 | 2644114.9494 | 1212116.162 | 2644099.83 | 1212121.3311 | 2644070.1754 | 1212132.8299 | 2644053.2474 | 1212137.0408 | 2644038.7572 | 1212137.2673 | 2643969.5746 | 1212125.8618 | 2643950.4747 | 1212118.6058 | 2643934.8391 | 1212108.2625 | 2643923.5089 | 1212097.206 | 2643911.8415 | 1212079.3208 | 2643906.4608 | 1212063.0273 | 2643901.9513 | 1212035.7004 | 2643899.5693 | 1212026.9444 | 2643875.8182 | 1211986.7574 | 2643872.4449 | 1211977.4494 | 2643872.1048 | 1211967.908 | 2643875.0167 | 1211960.4028 | 2643882.1791 | 1211953.4848
33 | 2643882.1791 | 1211953.4848 | 2643901.9878 | 1211978.0781 | 2643904.6099 | 1211980.5301
34 | 2644003.0336 | 1211414.0579 | 2643995.3872 | 1211416.4269 | 2643985.3767 | 1211416.8756 | 2643974.8044 | 1211414.1628 | 2643966.5101 | 1211410.4192
35 | 2643430.75 | 1211822.0625 | 2643432.94 | 1211800.9439 | 2643432.4177 | 1211788.1438 | 2643432.2402 | 1211787.1412
36 | 2643430.75 | 1211822.0625 | 2643430.75 | 1211822.0625 | 2643426.4943 | 1211844.1 | 2643425.8102 | 1211846.0703
37 | 2643412.7271 | 1211874.3619 | 2643419.4322 | 1211864.4382 | 2643425.8102 | 1211846.0703
38 | 2644409.2856 | 1211528.3121 | 2644408.0437 | 1211532.8499
39 | 2644397.188 | 1211540.7071 | 2644408.0437 | 1211532.8499
40 | 2644397.188 | 1211540.7071 | 2644392.5345 | 1211535.0247 | 2644386.0392 | 1211529.7623 | 2644347.506 | 1211504.4834
41 | 2644397.188 | 1211540.7071 | 2644400.1956 | 1211547.0109 | 2644403.5605 | 1211560.4438 | 2644404.3199 | 1211566.6702
42 | 2644347.506 | 1211504.4834 | 2644344.0852 | 1211498.5656 | 2644338.622 | 1211493.4443 | 2644314.463 | 1211480.6686 | 2644286.092 | 1211461.0355 | 2644269.8626 | 1211448.6412 | 2644255.2963 | 1211434.3138 | 2644246.8222 | 1211422.2662 | 2644240.8264 | 1211406.9795 | 2644236.6782 | 1211388.4602 | 2644233.8703 | 1211358.2551 | 2644233.7258 | 1211346.9919 | 2644238.3276 | 1211330.9833 | 2644242.2705 | 1211321.8628 | 2644249.3908 | 1211313.0039
43 | 2644347.506 | 1211504.4834 | 2644326.4054 | 1211494.254 | 2644262.5438 | 1211476.5032 | 2644247.0952 | 1211470.4963 | 2644233.8971 | 1211464.306 | 2644220.1016 | 1211455.6766 | 2644157.8709 | 1211407.3878 | 2644145.3448 | 1211395.5883 | 2644126.9872 | 1211369.8598 | 2644119.9006 | 1211363.3036 | 2644112.3844 | 1211360.402 | 2644099.5376 | 1211361.1186 | 2644084.2246 | 1211364.463 | 2644068.4745 | 1211372.4736 | 2644015.4314 | 1211407.2248 | 2644004.9907 | 1211413.4515 | 2644003.0336 | 1211414.0579
44 | 2644509.8367 | 1211738.806 | 2644482.3802 | 1211731.2858 | 2644467.9204 | 1211730.3665 | 2644453.8465 | 1211731.6847 | 2644414.245 | 1211740.9398 | 2644404.4577 | 1211741.067 | 2644395.3055 | 1211738.5642 | 2644314.2271 | 1211704.7643 | 2644306.7218 | 1211699.4277 | 2644301.4776 | 1211692.4736 | 2644299.1141 | 1211681.2828 | 2644300.0488 | 1211667.9598 | 2644303.818 | 1211654.5799 | 2644307.9417 | 1211647.7065 | 2644313.2765 | 1211642.4653 | 2644330.2676 | 1211633.0415 | 2644396.5885 | 1211593.7114 | 2644402.9406 | 1211586.5655 | 2644405.6587 | 1211577.6472 | 2644404.3199 | 1211566.6702
45 | 2643521.3416 | 1212167.6572 | 2643543.0505 | 1212181.8349 | 2643566.6259 | 1212192.1796 | 2643587.8044 | 1212197.8153 | 2643603.6016 | 1212200.1668
46 | 2643616.0902 | 1212199.823 | 2643604.2198 | 1212200.2588 | 2643603.6016 | 1212200.1668
47 | 2643521.3416 | 1212167.6572 | 2643498.5898 | 1212141.2315 | 2643484.9267 | 1212116.6065 | 2643431.1312 | 1212001.4143 | 2643430.5558 | 1211995.9181 | 2643431.986 | 1211990.4475 | 2643436.8814 | 1211985.936 | 2643456.004 | 1211970.3995 | 2643461.5708 | 1211962.3798 | 2643465.739 | 1211952.3487 | 2643467.7175 | 1211923.7687 | 2643466.4072 | 1211914.865 | 2643462.6426 | 1211907.0219 | 2643453.8651 | 1211897.9194 | 2643412.7271 | 1211874.3619
48 | 2643521.3416 | 1212167.6572 | 2643256.809 | 1212554.805
49 | 2643616.0902 | 1212199.823 | 2643642.1549 | 1212198.8686
50 | 2643412.7271 | 1211874.3619 | 2643405.8021 | 1211880.0482 | 2643396.5763 | 1211884.9272
51 | 2643256.809 | 1212554.805 | 2643247.1989 | 1212571.5563 | 2643244.1561 | 1212581.54 | 2643242.0016 | 1212601.0358 | 2643242.72 | 1212607.7783 | 2643245.1717 | 1212615.4116 | 2643253.2196 | 1212634.9369 | 2643256.8099 | 1212645.8248 | 2643260.8614 | 1212654.9262 | 2643267.7231 | 1212664.1257 | 2643275.824 | 1212671.0885 | 2643285.3557 | 1212676.6387 | 2643300.1971 | 1212681.2156 | 2643316.8679 | 1212687.0289 | 2643337.215 | 1212690.8232 | 2643363.6948 | 1212692.2386 | 2643372.8592 | 1212692.9167 | 2643378.5464 | 1212695.3928 | 2643381.7787 | 1212699.074 | 2643382.9633 | 1212704.3634
52 | 2643256.809 | 1212554.805 | 2643258.4947 | 1212537.1069 | 2643260.4836 | 1212525.7813 | 2643267.6725 | 1212502.442 | 2643268.0972 | 1212494.1625 | 2643265.0993 | 1212486.4251 | 2643259.6303 | 1212482.1163 | 2643247.6578 | 1212479.9505 | 2643207.1335 | 1212477.0109 | 2643185.5714 | 1212471.9853 | 2643166.8963 | 1212461.6886 | 2643130.7265 | 1212448.0192 | 2643111.8358 | 1212439.1554 | 2643055.7804 | 1212413.358 | 2643036.0769 | 1212405.4891 | 2642997.2348 | 1212394.6473 | 2642984.6042 | 1212394.1561 | 2642946.6995 | 1212394.4834 | 2642941.0103 | 1212392.219 | 2642937.1755 | 1212386.6993 | 2642937.2223 | 1212380.1958 | 2642939.3064 | 1212373.518 | 2642944.4404 | 1212368.4742 | 2642974.9053 | 1212348.4262 | 2642981.3122 | 1212341.3647
53 | 2643645.7522 | 1212198.7369 | 2643642.1549 | 1212198.8686
54 | 2643665.1075 | 1212224.9182 | 2643667.1355 | 1212213.5709 | 2643666.6868 | 1212206.3745 | 2643664.298 | 1212200.587 | 2643658.1001 | 1212198.2848 | 2643645.7522 | 1212198.7369
55 | 2643943.4867 | 1211986.269 | 2643932.8858 | 1211988.6671 | 2643914.378 | 1211989.6649
56 | 2643943.4867 | 1211986.269 | 2643944.4993 | 1211986.04 | 2643951.6884 | 1211981.6903 | 2643961.4933 | 1211972.5486
57 | 2643914.378 | 1211989.6649 | 2643914.378 | 1211989.6649 | 2643904.6099 | 1211980.5301
58 | 2644214.908 | 1212043.7036 | 2644217.2357 | 1212056.6506 | 2644216.4116 | 1212063.2929 | 2644212.0267 | 1212072.6547 | 2644209.5585 | 1212080.7189 | 2644208.8541 | 1212087.9411
59 | 2644214.908 | 1212043.7036 | 2644225.0564 | 1212028.7211
60 | 2644250.4371 | 1212073.5722 | 2644253.3866 | 1212079.0094 | 2644253.9552 | 1212084.2944 | 2644250.5898 | 1212093.4637 | 2644246.7251 | 1212098.2601 | 2644242.84 | 1212099.6544 | 2644234.6928 | 1212098.9825 | 2644228.5311 | 1212100.0041 | 2644222.4683 | 1212099.4222
61 | 2644206.4259 | 1212112.8367 | 2644214.2683 | 1212100.2986 | 2644219.3674 | 1212099.1246 | 2644222.4683 | 1212099.4222
62 | 2644206.4259 | 1212112.8367 | 2644208.8541 | 1212087.9411
63 | 2644225.0564 | 1212028.7211 | 2644233.0066 | 1212016.9837
64 | 2642981.3122 | 1212341.3647 | 2642991.7913 | 1212329.8147 | 2642998.0982 | 1212325.4354 | 2642999.2677 | 1212324.8483
65 | 2642999.2677 | 1212324.8483 | 2643008.1631 | 1212320.3827 | 2643011.6595 | 1212315.9386 | 2643013.4172 | 1212311.2406
66 | 2643442.8525 | 1212846.7823 | 2643448.9524 | 1212842.6243 | 2643449.994 | 1212839.3855 | 2643448.398 | 1212835.3048 | 2643426.3552 | 1212811.9863 | 2643421.3275 | 1212802.4108 | 2643407.0111 | 1212760.1931 | 2643394.2608 | 1212714.6627 | 2643389.0562 | 1212707.454 | 2643382.9633 | 1212704.3634
67 | 2643349.621 | 1212798.4429 | 2643352.7773 | 1212792.7069 | 2643361.1909 | 1212756.6136 | 2643365.2979 | 1212746.5486 | 2643382.0704 | 1212709.0931 | 2643382.9633 | 1212704.3634
68 | 2643349.621 | 1212798.4429 | 2643413.7751 | 1212866.271 | 2643423.4462 | 1212875.9745
69 | 2644509.8367 | 1211738.806 | 2644521.2423 | 1211739.7027 | 2644532.0582 | 1211738.1602 | 2644541.8651 | 1211734.3756 | 2644547.1461 | 1211734.3261 | 2644549.8641 | 1211736.7353
70 | 2644549.8641 | 1211736.7353 | 2644550.3843 | 1211737.1964 | 2644550.3843 | 1211737.1964
71 | 2644550.3843 | 1211737.1964 | 2644548.2334 | 1211760.1457
72 | 2643665.1075 | 1212224.9182 | 2643665.4786 | 1212235.4604 | 2643667.4377 | 1212240.8001 | 2643673.6192 | 1212246.3708 | 2643689.1865 | 1212253.5889 | 2643704.5356 | 1212257.4146 | 2643716.1632 | 1212257.9556 | 2643739.7498 | 1212255.2824 | 2643757.1583 | 1212255.9215 | 2643762.9449 | 1212259.3881 | 2643767.2935 | 1212266.2462 | 2643768.9817 | 1212280.5225 | 2643765.4023 | 1212313.8157 | 2643766.1441 | 1212321.4367 | 2643768.2079 | 1212325.9434 | 2643777.7954 | 1212330.1161 | 2643805.7877 | 1212331.6557 | 2643838.7929 | 1212325.0942 | 2643861.9842 | 1212319.3278 | 2643872.7674 | 1212318.9735 | 2643877.0271 | 1212320.3278 | 2643881.0795 | 1212323.0147 | 2643883.2693 | 1212325.8658 | 2643884.4337 | 1212329.7322 | 2643883.8065 | 1212333.3964 | 2643882.9713 | 1212337.4593 | 2643881.1933 | 1212340.5925 | 2643877.5755 | 1212344.9351 | 2643872.0975 | 1212349.1195 | 2643860.9943 | 1212355.8085 | 2643855.7427 | 1212359.1608 | 2643852.7746 | 1212361.9406 | 2643850.0147 | 1212366.3562 | 2643848.7793 | 1212370.0827 | 2643847.9244 | 1212375.802 | 2643846.9435 | 1212398.6637 | 2643846.9435 | 1212398.6637
73 | 2644294.241 | 1212292.6105 | 2644288.3918 | 1212295.5733 | 2644279.9937 | 1212300.0804 | 2644271.9489 | 1212303.0558 | 2644262.2201 | 1212304.6401 | 2644254.2479 | 1212306.0151 | 2644249.531 | 1212307.9257 | 2644243.4024 | 1212311.6936 | 2644235.3974 | 1212317.5044 | 2644228.1016 | 1212321.9195 | 2644204.7799 | 1212333.9538 | 2644170.1685 | 1212359.3569 | 2644148.1855 | 1212371.2124 | 2644131.594 | 1212382.3962 | 2644125.2192 | 1212386.6071 | 2644115.907 | 1212388.3949 | 2644103.8825 | 1212389.162 | 2644088.2159 | 1212391.3809 | 2644077.0801 | 1212397.3133 | 2644069.3839 | 1212393.2319 | 2644063.8624 | 1212385.809 | 2644053.0214 | 1212380.637 | 2644049.0543 | 1212373.6148 | 2644041.3226 | 1212370.2224 | 2644031.6811 | 1212370.2958 | 2644027.465 | 1212369.2196 | 2644024.7009 | 1212363.8961 | 2644017.1912 | 1212360.2719 | 2644004.0727 | 1212351.7703 | 2643993.1501 | 1212337.0367 | 2643974.0264 | 1212318.6628 | 2643960.1598 | 1212316.8152 | 2643948.3187 | 1212314.3376 | 2643933.7473 | 1212323.5913 | 2643931.7467 | 1212329.0798 | 2643936.7766 | 1212335.2093 | 2643941.9931 | 1212339.717 | 2643950.1947 | 1212353.5966 | 2643964.5364 | 1212380.6625 | 2643967.4077 | 1212388.9663 | 2643970.4632 | 1212395.9929 | 2643971.1906 | 1212400.3675 | 2643970.0212 | 1212403.3828 | 2643967.419 | 1212405.9874 | 2643962.8734 | 1212406.3208 | 2643955.4229 | 1212404.9763 | 2643944.6373 | 1212397.4258 | 2643939.8899 | 1212395.2562 | 2643926.1811 | 1212395.7223 | 2643914.4948 | 1212398.0265 | 2643899.2797 | 1212402.9064 | 2643877.1011 | 1212398.0738 | 2643863.0408 | 1212397.7814 | 2643846.9435 | 1212398.6637
74 | 2643566.5676 | 1212906.5714 | 2643580.285 | 1212914.079 | 2643587.6273 | 1212913.5212 | 2643594.3003 | 1212920.3911
75 | 2643566.5676 | 1212906.5714 | 2643552.3329 | 1212898.7806
76 | 2643535.0668 | 1212922.9098 | 2643544.5008 | 1212903.256 | 2643551.8735 | 1212898.5292 | 2643552.3329 | 1212898.7806
77 | 2643460.4246 | 1212750.6873 | 2643456.9783 | 1212753.4528 | 2643455.0632 | 1212758.7753 | 2643455.0544 | 1212766.2351 | 2643457.4366 | 1212773.9681 | 2643468.3029 | 1212787.1104 | 2643470.3374 | 1212793.5624 | 2643471.0614 | 1212805.7525 | 2643472.8227 | 1212816.3271 | 2643476.8129 | 1212827.5294 | 2643488.07 | 1212843.3206 | 2643502.8219 | 1212860.0824 | 2643512.9831 | 1212868.8282 | 2643517.6329 | 1212873.9429 | 2643520.247 | 1212879.0316 | 2643521.9888 | 1212886.015 | 2643525.1793 | 1212900.6024 | 2643529.3761 | 1212912.6178 | 2643535.0668 | 1212922.9098
78 | 2643548.3663 | 1212946.0759 | 2643542.4217 | 1212936.2268 | 2643535.0668 | 1212922.9098
79 | 2643460.4246 | 1212750.6873 | 2643464.5346 | 1212750.6617 | 2643468.9588 | 1212753.3955 | 2643473.7537 | 1212757.7392
80 | 2643548.3663 | 1212946.0759 | 2643539.5267 | 1212941.5421 | 2643489.1106 | 1212925.6542 | 2643470.2268 | 1212917.1561 | 2643462.1784 | 1212911.9356
81 | 2643548.3663 | 1212946.0759 | 2643562.9047 | 1212953.5308 | 2643582.1586 | 1212966.2313
82 | 2643600.1553 | 1212979.7357 | 2643616.1134 | 1213052.4789
83 | 2643600.1553 | 1212979.7357 | 2643586.424 | 1212969.0449 | 2643582.1586 | 1212966.2313
84 | 2643512.1668 | 1212793.5535 | 2643507.0492 | 1212792.9295 | 2643502.0854 | 1212791.2812 | 2643497.6706 | 1212788.3029 | 2643495.2843 | 1212784.272 | 2643491.5995 | 1212773.9058 | 2643473.7537 | 1212757.7392
85 | 2643462.1784 | 1212911.9356 | 2643454.0013 | 1212906.6318 | 2643423.4462 | 1212875.9745

## bus_geodata
| x | y | coords
0 | 2642840.6317 | 1211254.8189
1 | 2642766.597 | 1211252.2589
2 | 2642568.8608 | 1211198.5722
3 | 2642776.4601 | 1211262.3922
4 | 2642778.3135 | 1211267.1737
5 | 2642532.6501 | 1211783.152
6 | 2643265.599 | 1211530.06
7 | 2642535.7735 | 1211809.6011
8 | 2642787.3855 | 1211281.0579
9 | 2643283.4584 | 1211538.6544
10 | 2643266.6297 | 1211529.3468
11 | 2643218.944 | 1211107.2357
12 | 2643206.5718 | 1211070.5977
13 | 2643366.0063 | 1211253.5608
14 | 2643534.863 | 1211093.2297
15 | 2643466.0176 | 1211131.302
16 | 2643611.3334 | 1210881.9177
17 | 2643298.4119 | 1211506.3605
18 | 2643326.1368 | 1211464.8833
19 | 2643413.6028 | 1211393.7105
20 | 2643285.6574 | 1211538.7188
21 | 2643615.353 | 1210863.0499
22 | 2643617.9673 | 1210854.7086
23 | 2643603.819 | 1210842.0196
24 | 2643403.9443 | 1211584.985
25 | 2643757.0439 | 1211062.4136
26 | 2643671.6672 | 1211605.8272
27 | 2643407.4802 | 1211594.9842
28 | 2643882.1791 | 1211953.4848
29 | 2643966.5101 | 1211410.4192
30 | 2643766.7727 | 1211047.5985
31 | 2643770.9529 | 1211075.4676
32 | 2643432.2402 | 1211787.1412
33 | 2643430.75 | 1211822.0625
34 | 2643425.8102 | 1211846.0703
35 | 2644409.2856 | 1211528.3121
36 | 2644408.0437 | 1211532.8499
37 | 2644397.188 | 1211540.7071
38 | 2644347.506 | 1211504.4834
39 | 2644404.3199 | 1211566.6702
40 | 2643603.6016 | 1212200.1668
41 | 2643521.3416 | 1212167.6572
42 | 2643616.0902 | 1212199.823
43 | 2643412.7271 | 1211874.3619
44 | 2643256.809 | 1212554.805
45 | 2643642.1549 | 1212198.8686
46 | 2643396.5763 | 1211884.9273
47 | 2643645.7522 | 1212198.7369
48 | 2643943.4867 | 1211986.269
49 | 2643914.378 | 1211989.6649
50 | 2643961.4933 | 1211972.5486
51 | 2643904.6099 | 1211980.5301
52 | 2644214.908 | 1212043.7036
53 | 2644250.4371 | 1212073.5722
54 | 2644222.4683 | 1212099.4222
55 | 2644206.4259 | 1212112.8367
56 | 2644208.8541 | 1212087.9411
57 | 2644233.0066 | 1212016.9837
58 | 2644225.0564 | 1212028.7211
59 | 2642981.3122 | 1212341.3647
60 | 2642999.2677 | 1212324.8483
61 | 2643013.4172 | 1212311.2406
62 | 2643382.9633 | 1212704.3634
63 | 2643442.8525 | 1212846.7823
64 | 2643349.621 | 1212798.4429
65 | 2644003.0336 | 1211414.0579
66 | 2644249.3908 | 1211313.0039
67 | 2644509.8367 | 1211738.806
68 | 2644549.8641 | 1211736.7353
69 | 2644550.3843 | 1211737.1964
70 | 2643665.1076 | 1212224.9182
71 | 2643846.9435 | 1212398.6637
72 | 2644294.241 | 1212292.6105
73 | 2644548.2334 | 1211760.1457
74 | 2643566.5676 | 1212906.5714
75 | 2643594.3003 | 1212920.3911
76 | 2643552.3329 | 1212898.7806
77 | 2643535.0668 | 1212922.9098
78 | 2643460.4246 | 1212750.6873
79 | 2643548.3663 | 1212946.0759
80 | 2643616.1134 | 1213052.4789
81 | 2643600.1553 | 1212979.7357
82 | 2643512.1668 | 1212793.5535
83 | 2643473.7537 | 1212757.7392
84 | 2643582.1586 | 1212966.2313
85 | 2643462.1784 | 1212911.9356
86 | 2643423.4462 | 1212875.9745
87 | 2643432.2402 | 1211787.1412

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98457 | -0.11194 | 0.00051493 | 0.00012905
1 | 0.98464 | -0.11143 | 0 | 0
2 | 0.98454 | -0.1121 | 0.00029906 | 7.4952e-05
3 | 0.98465 | -0.11129 | 0.0011849 | 0.00029696
4 | 0.98467 | -0.11119 | 0 | 0
5 | 0.98577 | -0.10335 | 0 | 0
6 | 0.98689 | -0.09501 | 0 | 0
7 | 0.98574 | -0.10358 | 0.00085272 | 0.00021371
8 | 0.98466 | -0.11125 | 0.0003628 | 9.0927e-05
9 | 0.98686 | -0.095188 | 0.00046547 | 0.00011666
10 | 0.98689 | -0.094955 | 0.001071 | 0.00026841
11 | 0.98491 | -0.10914 | 0.0013441 | 0.00033687
12 | 0.98489 | -0.10929 | 0.00037674 | 9.442e-05
13 | 0.98548 | -0.10511 | 0 | 0
14 | 0.9862 | -0.099819 | 0 | 0
15 | 0.98667 | -0.096464 | 0.0013214 | 0.00033117
16 | 0.98543 | -0.10534 | 0.0003108 | 7.7893e-05
17 | 0.98719 | -0.092807 | 0.0017141 | 0.00042959
18 | 0.98768 | -0.089188 | 0 | 0
19 | 0.9888 | -0.081058 | 0 | 0
20 | 0.98686 | -0.095197 | 0.00039427 | 9.8813e-05
21 | 0.98538 | -0.10569 | 0 | 0
22 | 0.98536 | -0.10584 | 0 | 0
23 | 0.98532 | -0.10618 | 0.0017135 | 0.00042944
24 | 0.99437 | -0.040702 | 0 | 0
25 | 0.98813 | -0.085906 | 0 | 0
26 | 0.99188 | -0.059216 | 0 | 0
27 | 0.99465 | -0.038665 | 0.00070741 | 0.00017729
28 | 0.99025 | -0.071126 | 0 | 0
29 | 0.98985 | -0.074292 | 0.0001163 | 2.9147e-05
30 | 0.98812 | -0.085973 | 0.00036821 | 9.2282e-05
31 | 0.98812 | -0.086019 | 0.00058072 | 0.00014554
32 | 1 | 0 | -0.026292 | -0.0062756
33 | 0.99969 | -0.0023025 | 0.00057248 | 0.00014348
34 | 0.99949 | -0.0037732 | 0.00014491 | 3.6318e-05
35 | 0.98811 | -0.087131 | 0.00021897 | 5.4879e-05
36 | 0.98811 | -0.08712 | 9.5207e-05 | 2.3861e-05
37 | 0.98812 | -0.087077 | 0 | 0
38 | 0.98832 | -0.08558 | 0 | 0
39 | 0.98804 | -0.087646 | 0.001207 | 0.0003025
40 | 0.99647 | -0.026465 | 0.00025606 | 6.4174e-05
41 | 0.99661 | -0.025322 | 0 | 0
42 | 0.99645 | -0.026591 | 0 | 0
43 | 0.99925 | -0.0056116 | 0 | 0
44 | 0.99395 | -0.044967 | 0 | 0
45 | 0.99642 | -0.026855 | 0.00065201 | 0.00016341
46 | 0.99924 | -0.0056818 | 0.00036134 | 9.0561e-05
47 | 0.99642 | -0.026868 | 8.438e-05 | 2.1148e-05
48 | 0.9901 | -0.072155 | 0.00096095 | 0.00024084
49 | 0.99015 | -0.071805 | 0.00013664 | 3.4246e-05
50 | 0.9901 | -0.072203 | 0.00020401 | 5.113e-05
51 | 0.99018 | -0.071627 | 9.1364e-05 | 2.2898e-05
52 | 0.98931 | -0.077952 | 0 | 0
53 | 0.9892 | -0.078788 | 0.00047141 | 0.00011815
54 | 0.98923 | -0.078536 | 9.9019e-05 | 2.4816e-05
55 | 0.98925 | -0.0784 | 0 | 0
56 | 0.98927 | -0.078252 | 5.9915e-05 | 1.5016e-05
57 | 0.98929 | -0.078109 | 0.00019585 | 4.9084e-05
58 | 0.98929 | -0.078081 | 0.00050071 | 0.00012549
59 | 0.99348 | -0.04846 | 0.00014879 | 3.7291e-05
60 | 0.99346 | -0.048593 | 0.00042686 | 0.00010698
61 | 0.99345 | -0.048615 | 0.00010688 | 2.6787e-05
62 | 0.9928 | -0.05339 | 0 | 0
63 | 0.99264 | -0.05453 | 0.00067153 | 0.0001683
64 | 0.99242 | -0.056119 | 0 | 0
65 | 0.98971 | -0.075347 | 0.00023234 | 5.823e-05
66 | 0.98831 | -0.085729 | 4.7274e-05 | 1.1848e-05
67 | 0.98757 | -0.091061 | 0 | 0
68 | 0.98752 | -0.091406 | 0.00015882 | 3.9805e-05
69 | 0.98752 | -0.091411 | 0.00039454 | 9.888e-05
70 | 0.99641 | -0.026986 | 0 | 0
71 | 0.99632 | -0.027958 | 0.00011152 | 2.795e-05
72 | 0.99627 | -0.028497 | 5.1889e-05 | 1.3005e-05
73 | 0.98751 | -0.09147 | 0.00024865 | 6.2317e-05
74 | 0.99144 | -0.063211 | 0.00068187 | 0.00017089
75 | 0.99143 | -0.063258 | 0.00013941 | 3.4938e-05
76 | 0.99146 | -0.063075 | 0.00013179 | 3.3029e-05
77 | 0.9915 | -0.062773 | 0 | 0
78 | 0.99138 | -0.063694 | 0 | 0
79 | 0.99156 | -0.062386 | 0 | 0
80 | 0.99146 | -0.063088 | 0.00037099 | 9.298e-05
81 | 0.9915 | -0.062805 | 0.00017893 | 4.4844e-05
82 | 0.99135 | -0.063897 | 0.00023169 | 5.8067e-05
83 | 0.99137 | -0.063765 | 0.00020876 | 5.2321e-05
84 | 0.99152 | -0.062677 | 0.00016757 | 4.1997e-05
85 | 0.99184 | -0.06034 | 0.00027634 | 6.9258e-05
86 | 0.99202 | -0.059023 | 0.00021981 | 5.509e-05
87 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00051493 | -0.00012905 | 0.00051496 | 0.00012786 | 3.5996e-08 | -1.1982e-06 | 0.00077823 | 0.0007778 | 0.00077823 | 0.98457 | -0.11194 | 0.98464 | -0.11143 | 0.28823
1 | 0.00029909 | 7.2259e-05 | -0.00029906 | -7.4952e-05 | 2.7038e-08 | -2.6927e-06 | 0.00045105 | 0.00045199 | 0.00045199 | 0.98464 | -0.11143 | 0.98454 | -0.1121 | 0.16741
2 | -0.00081405 | -0.00020011 | 0.00081407 | 0.00019993 | 1.4271e-08 | -1.8716e-07 | 0.0012288 | 0.0012288 | 0.0012288 | 0.98464 | -0.11143 | 0.98465 | -0.11129 | 0.45513
3 | -0.0019989 | -0.00049688 | 0.001999 | 0.00049683 | 2.9172e-08 | -5.4009e-08 | 0.0030194 | 0.0030193 | 0.0030194 | 0.98465 | -0.11129 | 0.98467 | -0.11119 | 1.1183
4 | 0.00036281 | 9.0718e-05 | -0.0003628 | -9.0927e-05 | 3.1082e-09 | -2.0961e-07 | 0.00054819 | 0.00054827 | 0.00054827 | 0.98467 | -0.11119 | 0.98466 | -0.11125 | 0.20306
5 | -0.0023618 | -0.00058755 | 0.0023669 | 0.00058125 | 5.1538e-06 | -6.2978e-06 | 0.0035675 | 0.0035646 | 0.0035675 | 0.98467 | -0.11119 | 0.98689 | -0.09501 | 1.3213
6 | -0.00085275 | -0.00021338 | 0.00085368 | 0.0002022 | 9.3216e-07 | -1.1187e-05 | 0.0012871 | 0.0012831 | 0.0012871 | 0.98577 | -0.10335 | 0.98689 | -0.09501 | 0.4767
7 | 0.00085275 | 0.00021338 | -0.00085272 | -0.00021371 | 2.7534e-08 | -3.2893e-07 | 0.0012871 | 0.0012872 | 0.0012872 | 0.98577 | -0.10335 | 0.98574 | -0.10358 | 0.47675
8 | 0.00085976 | 0.00021519 | -0.00085974 | -0.00021544 | 2.121e-08 | -2.503e-07 | 0.0012962 | 0.0012963 | 0.0012963 | 0.98689 | -0.09501 | 0.98686 | -0.095188 | 0.48012
9 | -0.0040804 | -0.00099864 | 0.0040804 | 0.00099863 | 2.9522e-08 | -4.6601e-09 | 0.0061439 | 0.0061439 | 0.0061439 | 0.98689 | -0.09501 | 0.98689 | -0.094955 | 2.2755
10 | 0.00039427 | 9.8785e-05 | -0.00039427 | -9.8813e-05 | 4.8511e-10 | -2.7921e-08 | 0.00059448 | 0.00059449 | 0.00059449 | 0.98686 | -0.095188 | 0.98686 | -0.095197 | 0.22018
11 | -0.0051514 | -0.001267 | 0.0051529 | 0.0012671 | 1.4772e-06 | 6.5501e-08 | 0.0077587 | 0.0077585 | 0.0077587 | 0.98689 | -0.094955 | 0.98719 | -0.092807 | 2.8736
12 | 0.00037675 | 9.3924e-05 | -0.00037674 | -9.442e-05 | 7.9183e-09 | -4.9556e-07 | 0.00056902 | 0.00056919 | 0.00056919 | 0.98491 | -0.10914 | 0.98489 | -0.10929 | 0.21081
13 | -0.0017209 | -0.00043079 | 0.0017218 | 0.00042828 | 9.5252e-07 | -2.5108e-06 | 0.0025997 | 0.0025987 | 0.0025997 | 0.98491 | -0.10914 | 0.98548 | -0.10511 | 0.96286
14 | -0.0017218 | -0.00042828 | 0.001723 | 0.00042502 | 1.2327e-06 | -3.2575e-06 | 0.0025987 | 0.0025974 | 0.0025987 | 0.98548 | -0.10511 | 0.9862 | -0.099819 | 0.96248
15 | -0.0037491 | -0.00092906 | 0.0037508 | 0.00092862 | 1.702e-06 | -4.3507e-07 | 0.005653 | 0.0056526 | 0.005653 | 0.9862 | -0.099819 | 0.98667 | -0.096464 | 2.0937
16 | 0.002026 | 0.00050403 | -0.0020245 | -0.0005068 | 1.5362e-06 | -2.7696e-06 | 0.0030556 | 0.0030568 | 0.0030568 | 0.9862 | -0.099819 | 0.98543 | -0.10534 | 1.1321
17 | -0.0050721 | -0.0012598 | 0.0050828 | 0.0012601 | 1.062e-05 | 3.5724e-07 | 0.0076454 | 0.0076441 | 0.0076454 | 0.98667 | -0.096464 | 0.9888 | -0.081058 | 2.8316
18 | 0.0017137 | 0.00042891 | -0.0017136 | -0.00042913 | 8.0732e-08 | -2.1512e-07 | 0.0025875 | 0.0025876 | 0.0025876 | 0.98543 | -0.10534 | 0.98538 | -0.10569 | 0.95836
19 | -0.006867 | -0.0016967 | 0.0068703 | 0.0016974 | 3.3468e-06 | 6.4578e-07 | 0.010342 | 0.010342 | 0.010342 | 0.98719 | -0.092807 | 0.98768 | -0.089188 | 3.8304
20 | -0.0068703 | -0.0016974 | 0.0068778 | 0.0016988 | 7.5212e-06 | 1.4488e-06 | 0.010342 | 0.010341 | 0.010342 | 0.98768 | -0.089188 | 0.9888 | -0.081058 | 3.8304
21 | -0.01291 | -0.0031903 | 0.012981 | 0.0032136 | 7.0486e-05 | 2.3243e-05 | 0.019412 | 0.019411 | 0.019412 | 0.9888 | -0.081058 | 0.99437 | -0.040702 | 7.1897
22 | 0.00094956 | 0.00023136 | -0.00094894 | -0.00023736 | 6.1867e-07 | -5.9967e-06 | 0.0014267 | 0.0014288 | 0.0014288 | 0.9888 | -0.081058 | 0.98813 | -0.085906 | 0.5292
23 | 0.0017136 | 0.00042913 | -0.0017136 | -0.00042922 | 3.652e-08 | -9.7299e-08 | 0.0025876 | 0.0025876 | 0.0025876 | 0.98538 | -0.10569 | 0.98536 | -0.10584 | 0.95837
24 | 0.0017136 | 0.00042922 | -0.0017135 | -0.00042944 | 8.1222e-08 | -2.1636e-07 | 0.0025876 | 0.0025877 | 0.0025877 | 0.98536 | -0.10584 | 0.98532 | -0.10618 | 0.95841
25 | 0.005468 | 0.001332 | -0.0054548 | -0.0013311 | 1.3278e-05 | 9.8193e-07 | 0.0081692 | 0.0081707 | 0.0081707 | 0.99437 | -0.040702 | 0.99188 | -0.059216 | 3.0262
26 | -0.018449 | -0.0045456 | 0.018454 | 0.0045474 | 5.0341e-06 | 1.7986e-06 | 0.02758 | 0.02758 | 0.02758 | 0.99437 | -0.040702 | 0.99465 | -0.038665 | 10.2148
27 | 0.00036821 | 9.2057e-05 | -0.00036821 | -9.2282e-05 | 3.3974e-09 | -2.2557e-07 | 0.00055441 | 0.00055449 | 0.00055449 | 0.98813 | -0.085906 | 0.98812 | -0.085973 | 0.20537
28 | 0.00058073 | 0.0001453 | -0.00058072 | -0.00014554 | 9.0887e-09 | -2.4049e-07 | 0.00087443 | 0.00087451 | 0.00087451 | 0.98813 | -0.085906 | 0.98812 | -0.086019 | 0.32389
29 | 0.0027257 | 0.00066865 | -0.0027213 | -0.00067235 | 4.3375e-06 | -3.6996e-06 | 0.004084 | 0.0040859 | 0.0040859 | 0.99188 | -0.059216 | 0.99025 | -0.071126 | 1.5133
30 | 0.0027291 | 0.00066241 | -0.0027237 | -0.000667 | 5.3977e-06 | -4.5917e-06 | 0.0040867 | 0.004089 | 0.004089 | 0.99188 | -0.059216 | 0.98985 | -0.074292 | 1.5144
31 | -0.019161 | -0.0047247 | 0.019261 | 0.0047605 | 9.9852e-05 | 3.5859e-05 | 0.028638 | 0.028637 | 0.028638 | 0.99465 | -0.038665 | 1 | 0 | 10.6068
32 | 0.0013282 | 0.00032446 | -0.001327 | -0.00033029 | 1.2157e-06 | -5.8301e-06 | 0.0019929 | 0.0019951 | 0.0019951 | 0.99025 | -0.071126 | 0.98931 | -0.077952 | 0.73892
33 | 0.0013931 | 0.00034788 | -0.0013931 | -0.0003483 | 9.6141e-08 | -4.1542e-07 | 0.002093 | 0.0020932 | 0.0020932 | 0.99025 | -0.071126 | 0.99018 | -0.071627 | 0.77524
34 | 0.0026074 | 0.00063786 | -0.002607 | -0.00063821 | 3.6368e-07 | -3.4904e-07 | 0.0039141 | 0.0039143 | 0.0039143 | 0.98985 | -0.074292 | 0.98971 | -0.075347 | 1.4497
35 | 0.0062311 | 0.001515 | -0.0062292 | -0.0015147 | 1.8743e-06 | 2.6106e-07 | 0.0092558 | 0.009256 | 0.009256 | 1 | 0 | 0.99969 | -0.0023025 | 3.4281
36 | 0.0056568 | 0.0013712 | -0.0056557 | -0.0013711 | 1.0811e-06 | 9.424e-08 | 0.0084039 | 0.008404 | 0.008404 | 0.99969 | -0.0023025 | 0.99949 | -0.0037732 | 3.1126
37 | 0.0055108 | 0.0013348 | -0.0055095 | -0.0013347 | 1.3146e-06 | 9.3915e-08 | 0.0081883 | 0.0081884 | 0.0081884 | 0.99949 | -0.0037732 | 0.99925 | -0.0056116 | 3.0327
38 | -0.00021897 | -5.4879e-05 | 0.00021897 | 5.4819e-05 | 3.192e-10 | -6.0141e-08 | 0.00032975 | 0.00032973 | 0.00032975 | 0.98811 | -0.087131 | 0.98811 | -0.08712 | 0.12213
39 | -0.00031418 | -7.868e-05 | 0.00031418 | 7.8509e-05 | 1.8714e-09 | -1.7093e-07 | 0.00047311 | 0.00047304 | 0.00047311 | 0.98811 | -0.08712 | 0.98812 | -0.087077 | 0.17522
40 | -0.0023237 | -0.00057587 | 0.0023242 | 0.00057526 | 4.706e-07 | -6.0918e-07 | 0.003497 | 0.0034967 | 0.003497 | 0.98812 | -0.087077 | 0.98832 | -0.08558 | 1.2952
41 | 0.0020095 | 0.00049736 | -0.0020094 | -0.00049765 | 1.5467e-07 | -2.8768e-07 | 0.003024 | 0.0030241 | 0.0030241 | 0.98812 | -0.087077 | 0.98804 | -0.087646 | 1.12
42 | 4.7275e-05 | 8.6872e-06 | -4.7274e-05 | -1.1848e-05 | 7.684e-10 | -3.1609e-06 | 7.0198e-05 | 7.1178e-05 | 7.1178e-05 | 0.98832 | -0.08558 | 0.98831 | -0.085729 | 0.026362
43 | -0.0023715 | -0.00058395 | 0.0023747 | 0.00057998 | 3.2237e-06 | -3.9738e-06 | 0.0035668 | 0.003565 | 0.0035668 | 0.98832 | -0.08558 | 0.98971 | -0.075347 | 1.321
44 | 0.00080242 | 0.00019516 | -0.00080205 | -0.00020018 | 3.6695e-07 | -5.0237e-06 | 0.0012064 | 0.0012082 | 0.0012082 | 0.98804 | -0.087646 | 0.98757 | -0.091061 | 0.44748
45 | -0.0011559 | -0.00027506 | 0.0011561 | 0.00027396 | 1.6551e-07 | -1.1032e-06 | 0.0017211 | 0.0017207 | 0.0017211 | 0.99647 | -0.026465 | 0.99661 | -0.025322 | 0.63744
46 | 0.00089986 | 0.00021089 | -0.00089985 | -0.00021105 | 1.3984e-08 | -1.575e-07 | 0.0013388 | 0.0013388 | 0.0013388 | 0.99647 | -0.026465 | 0.99645 | -0.026591 | 0.49586
47 | -0.005135 | -0.0012441 | 0.0051481 | 0.0012444 | 1.3128e-05 | 3.5393e-07 | 0.007652 | 0.0076504 | 0.007652 | 0.99661 | -0.025322 | 0.99925 | -0.0056116 | 2.8341
48 | 0.0039789 | 0.00097009 | -0.0039686 | -0.00097222 | 1.0297e-05 | -2.1332e-06 | 0.0059313 | 0.0059334 | 0.0059334 | 0.99661 | -0.025322 | 0.99395 | -0.044967 | 2.1976
49 | 0.00089985 | 0.00021105 | -0.00089982 | -0.00021138 | 2.9175e-08 | -3.2852e-07 | 0.0013388 | 0.0013389 | 0.0013389 | 0.99645 | -0.026591 | 0.99642 | -0.026855 | 0.4959
50 | 0.00036134 | 9.0308e-05 | -0.00036134 | -9.0561e-05 | 3.504e-09 | -2.5274e-07 | 0.000538 | 0.00053809 | 0.00053809 | 0.99925 | -0.0056116 | 0.99924 | -0.0056818 | 0.19929
51 | 0.0032857 | 0.00080793 | -0.003282 | -0.00080968 | 3.7019e-06 | -1.7567e-06 | 0.0049135 | 0.0049146 | 0.0049146 | 0.99395 | -0.044967 | 0.9928 | -0.05339 | 1.8202
52 | 0.00068286 | 0.0001643 | -0.00068254 | -0.00017048 | 3.1639e-07 | -6.1794e-06 | 0.0010199 | 0.0010221 | 0.0010221 | 0.99395 | -0.044967 | 0.99348 | -0.04846 | 0.37855
53 | 0.00024781 | 4.7965e-05 | -0.00024781 | -4.8012e-05 | 3.0029e-10 | -4.6772e-08 | 0.00036563 | 0.00036564 | 0.00036564 | 0.99642 | -0.026855 | 0.99642 | -0.026868 | 0.13542
54 | 0.00016343 | 2.6864e-05 | -0.00016343 | -2.7436e-05 | 1.58e-09 | -5.7207e-07 | 0.00023991 | 0.00024005 | 0.00024005 | 0.99642 | -0.026868 | 0.99641 | -0.026986 | 0.088907
55 | -0.001165 | -0.00029167 | 0.001165 | 0.00029132 | 5.6231e-08 | -3.5655e-07 | 0.0017507 | 0.0017506 | 0.0017507 | 0.9901 | -0.072155 | 0.99015 | -0.071805 | 0.64841
56 | 0.00020401 | 5.0837e-05 | -0.00020401 | -5.113e-05 | 1.3397e-09 | -2.933e-07 | 0.0003065 | 0.00030661 | 0.00030661 | 0.9901 | -0.072155 | 0.9901 | -0.072203 | 0.11356
57 | -0.0013017 | -0.00032556 | 0.0013017 | 0.0003254 | 3.1925e-08 | -1.5974e-07 | 0.0019559 | 0.0019559 | 0.0019559 | 0.99015 | -0.071805 | 0.99018 | -0.071627 | 0.72441
58 | 0.00063041 | 0.00015613 | -0.00063038 | -0.00015671 | 2.5707e-08 | -5.7915e-07 | 0.00094754 | 0.00094774 | 0.00094774 | 0.98931 | -0.077952 | 0.98927 | -0.078252 | 0.35102
59 | 0.00069657 | 0.00017416 | -0.00069655 | -0.00017439 | 1.2392e-08 | -2.2759e-07 | 0.0010476 | 0.0010476 | 0.0010476 | 0.98931 | -0.077952 | 0.98929 | -0.078081 | 0.38801
60 | -0.00047141 | -0.00011815 | 0.00047143 | 0.00011748 | 1.6333e-08 | -6.6215e-07 | 0.00070913 | 0.00070889 | 0.00070913 | 0.9892 | -0.078788 | 0.98923 | -0.078536 | 0.26264
61 | -0.00057045 | -0.0001423 | 0.00057046 | 0.00014201 | 1.0623e-08 | -2.9295e-07 | 0.00085784 | 0.00085774 | 0.00085784 | 0.98923 | -0.078536 | 0.98925 | -0.0784 | 0.31772
62 | -0.00057046 | -0.00014201 | 0.00057047 | 0.00014169 | 1.1482e-08 | -3.1674e-07 | 0.00085774 | 0.00085762 | 0.00085774 | 0.98925 | -0.0784 | 0.98927 | -0.078252 | 0.31768
63 | -0.00019585 | -4.9084e-05 | 0.00019585 | 4.8902e-05 | 7.6746e-10 | -1.8173e-07 | 0.00029458 | 0.00029451 | 0.00029458 | 0.98929 | -0.078109 | 0.98929 | -0.078081 | 0.1091
64 | 0.00053375 | 0.00013319 | -0.00053374 | -0.0001335 | 9.7998e-09 | -3.1453e-07 | 0.00079924 | 0.00079935 | 0.00079935 | 0.99348 | -0.04846 | 0.99346 | -0.048593 | 0.29606
65 | 0.00010688 | 2.652e-05 | -0.00010688 | -2.6787e-05 | 3.2963e-10 | -2.6692e-07 | 0.00015999 | 0.00016009 | 0.00016009 | 0.99346 | -0.048593 | 0.99345 | -0.048615 | 0.059291
66 | 0.00067164 | 0.0001662 | -0.00067153 | -0.0001683 | 1.0461e-07 | -2.1003e-06 | 0.0010059 | 0.0010067 | 0.0010067 | 0.9928 | -0.05339 | 0.99264 | -0.05453 | 0.37284
67 | 0.0026104 | 0.00064348 | -0.0026094 | -0.00064441 | 9.5648e-07 | -9.2882e-07 | 0.0039087 | 0.0039092 | 0.0039092 | 0.9928 | -0.05339 | 0.99242 | -0.056119 | 1.4478
68 | 0.0026094 | 0.00064441 | -0.0026084 | -0.0006454 | 1.021e-06 | -9.901e-07 | 0.0039092 | 0.0039097 | 0.0039097 | 0.99242 | -0.056119 | 0.99202 | -0.059023 | 1.448
69 | 0.00080205 | 0.00020018 | -0.00080201 | -0.0002007 | 3.8072e-08 | -5.2006e-07 | 0.0012082 | 0.0012084 | 0.0012084 | 0.98757 | -0.091061 | 0.98752 | -0.091406 | 0.44755
70 | 0.00064319 | 0.00016089 | -0.00064319 | -0.0001609 | 4.0731e-10 | -8.7371e-09 | 0.00096906 | 0.00096906 | 0.00096906 | 0.98752 | -0.091406 | 0.98752 | -0.091411 | 0.35891
71 | 0.00024865 | 6.2023e-05 | -0.00024865 | -6.2317e-05 | 2.0185e-09 | -2.9412e-07 | 0.00037457 | 0.00037467 | 0.00037467 | 0.98752 | -0.091411 | 0.98751 | -0.09147 | 0.13877
72 | 0.00016343 | 2.7436e-05 | -0.00016341 | -3.2569e-05 | 1.4263e-08 | -5.133e-06 | 0.00024005 | 0.00024139 | 0.00024139 | 0.99641 | -0.026986 | 0.99632 | -0.027958 | 0.089405
73 | 5.1891e-05 | 4.6197e-06 | -5.1889e-05 | -1.3005e-05 | 2.3364e-09 | -8.3849e-06 | 7.5473e-05 | 7.7501e-05 | 7.7501e-05 | 0.99632 | -0.027958 | 0.99627 | -0.028497 | 0.028704
74 | 0.00013941 | 3.4518e-05 | -0.00013941 | -3.4938e-05 | 8.893e-10 | -4.1977e-07 | 0.00020908 | 0.00020923 | 0.00020923 | 0.99144 | -0.063211 | 0.99143 | -0.063258 | 0.077492
75 | -0.00082128 | -0.00020541 | 0.00082129 | 0.00020521 | 1.538e-08 | -2.0335e-07 | 0.0012325 | 0.0012324 | 0.0012325 | 0.99144 | -0.063211 | 0.99146 | -0.063075 | 0.45647
76 | -0.00095308 | -0.00023824 | 0.00095312 | 0.00023785 | 3.9668e-08 | -3.856e-07 | 0.0014302 | 0.0014301 | 0.0014302 | 0.99146 | -0.063075 | 0.9915 | -0.062773 | 0.5297
77 | 0.00044052 | 0.00010693 | -0.00044046 | -0.00010947 | 5.4021e-08 | -2.5395e-06 | 0.0006599 | 0.00066079 | 0.00066079 | 0.9915 | -0.062773 | 0.99138 | -0.063694 | 0.24474
78 | -0.0013936 | -0.00034479 | 0.0013937 | 0.00034447 | 7.2774e-08 | -3.1641e-07 | 0.0020899 | 0.0020898 | 0.0020899 | 0.9915 | -0.062773 | 0.99156 | -0.062386 | 0.77405
79 | 0.00044046 | 0.00010947 | -0.00044046 | -0.00010967 | 4.3002e-09 | -2.0182e-07 | 0.00066079 | 0.00066086 | 0.00066086 | 0.99138 | -0.063694 | 0.99137 | -0.063765 | 0.24476
80 | -0.0021113 | -0.00052255 | 0.0021118 | 0.00052157 | 5.8222e-07 | -9.7723e-07 | 0.003166 | 0.0031656 | 0.003166 | 0.99156 | -0.062386 | 0.99184 | -0.06034 | 1.1726
81 | 0.00071755 | 0.00017808 | -0.00071752 | -0.00017858 | 2.8482e-08 | -4.9728e-07 | 0.0010762 | 0.0010764 | 0.0010764 | 0.99156 | -0.062386 | 0.99152 | -0.062677 | 0.39866
82 | -0.00037099 | -9.298e-05 | 0.00037101 | 9.2025e-05 | 1.4399e-08 | -9.5491e-07 | 0.0005568 | 0.00055646 | 0.0005568 | 0.99146 | -0.063088 | 0.9915 | -0.062805 | 0.20622
83 | -0.00054994 | -0.00013687 | 0.00054995 | 0.00013658 | 9.5598e-09 | -2.8667e-07 | 0.000825 | 0.00082489 | 0.000825 | 0.9915 | -0.062805 | 0.99152 | -0.062677 | 0.30555
84 | -0.00023169 | -5.8067e-05 | 0.00023169 | 5.7353e-05 | 4.1836e-09 | -7.1368e-07 | 0.00034776 | 0.00034751 | 0.00034776 | 0.99135 | -0.063897 | 0.99137 | -0.063765 | 0.1288
85 | -0.0023882 | -0.00059083 | 0.0023886 | 0.00059031 | 4.2412e-07 | -5.2141e-07 | 0.0035802 | 0.0035799 | 0.0035802 | 0.99184 | -0.06034 | 0.99202 | -0.059023 | 1.326

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.026717 | 0.0063821

## res_load
| p_mw | q_mvar
0 | 0.00051493 | 0.00012905
1 | 0.00029906 | 7.4952e-05
2 | 0.0011849 | 0.00029696
3 | 0.00085272 | 0.00021371
4 | 0.0003628 | 9.0927e-05
5 | 0.00046547 | 0.00011666
6 | 0.001071 | 0.00026841
7 | 0.0013441 | 0.00033687
8 | 0.00037674 | 9.442e-05
9 | 0.0013214 | 0.00033117
10 | 0.0003108 | 7.7893e-05
11 | 0.0017141 | 0.00042959
12 | 0.00039427 | 9.8813e-05
13 | 0.0017135 | 0.00042944
14 | 0.00070741 | 0.00017729
15 | 0.0001163 | 2.9147e-05
16 | 0.00036821 | 9.2282e-05
17 | 0.00058072 | 0.00014554
18 | 0.0004252 | 0.00010657
19 | 0.00057248 | 0.00014348
20 | 0.00014491 | 3.6318e-05
21 | 0.00021897 | 5.4879e-05
22 | 9.5207e-05 | 2.3861e-05
23 | 0.001207 | 0.0003025
24 | 0.00025606 | 6.4174e-05
25 | 0.00065201 | 0.00016341
26 | 0.00036134 | 9.0561e-05
27 | 8.438e-05 | 2.1148e-05
28 | 0.00096095 | 0.00024084
29 | 0.00013664 | 3.4246e-05
30 | 0.00020401 | 5.113e-05
31 | 9.1364e-05 | 2.2898e-05
32 | 0.00047141 | 0.00011815
33 | 9.9019e-05 | 2.4816e-05
34 | 5.9915e-05 | 1.5016e-05
35 | 0.00019585 | 4.9084e-05
36 | 0.00050071 | 0.00012549
37 | 0.00014879 | 3.7291e-05
38 | 0.00042686 | 0.00010698
39 | 0.00010688 | 2.6787e-05
40 | 0.00067153 | 0.0001683
41 | 0.00023234 | 5.823e-05
42 | 4.7274e-05 | 1.1848e-05
43 | 0.00015882 | 3.9805e-05
44 | 0.00039454 | 9.888e-05
45 | 0.00011152 | 2.795e-05
46 | 5.1889e-05 | 1.3005e-05
47 | 0.00024865 | 6.2317e-05
48 | 0.00068187 | 0.00017089
49 | 0.00013941 | 3.4938e-05
50 | 0.00013179 | 3.3029e-05
51 | 0.00037099 | 9.298e-05
52 | 0.00017893 | 4.4844e-05
53 | 0.00023169 | 5.8067e-05
54 | 0.00020876 | 5.2321e-05
55 | 0.00016757 | 4.1997e-05
56 | 0.00027634 | 6.9258e-05
57 | 0.00021981 | 5.509e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1