## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1137-2_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1137-2_0_3_node_11 | 0.4 | n |  | TRUE
2 | bus_LV_1137-2_0_3_node_25 | 0.4 | n |  | TRUE
3 | bus_LV_1137-2_0_3_node_35 | 0.4 | n |  | TRUE
4 | bus_LV_1137-2_0_3_node_23 | 0.4 | n |  | TRUE
5 | bus_LV_1137-2_0_3_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_1137-2_0_3_node_27 | 0.4 | n |  | TRUE
7 | bus_LV_1137-2_0_3_node_39 | 0.4 | n |  | TRUE
8 | bus_LV_1137-2_0_3_node_31 | 0.4 | n |  | TRUE
9 | bus_LV_1137-2_0_3_node_32 | 0.4 | n |  | TRUE
10 | bus_LV_1137-2_0_3_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_1137-2_0_3_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1137-2_0_3_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_1137-2_0_3_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_1137-2_0_3_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_1137-2_0_3_node_1 | 0.4 | n |  | TRUE
16 | bus_LV_1137-2_0_3_node_2 | 0.4 | n |  | TRUE
17 | bus_LV_1137-2_0_3_node_4 | 0.4 | n |  | TRUE
18 | bus_LV_1137-2_0_3_node_3 | 0.4 | n |  | TRUE
19 | bus_LV_1137-2_0_3_node_5 | 0.4 | n |  | TRUE
20 | bus_LV_1137-2_0_3_node_6 | 0.4 | n |  | TRUE
21 | bus_LV_1137-2_0_3_node_7 | 0.4 | n |  | TRUE
22 | bus_LV_1137-2_0_3_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_1137-2_0_3_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1137-2_0_3_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_1137-2_0_3_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1137-2_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_1137-2_0_3_node_8 | 0.4 | n |  | TRUE
28 | bus_LV_1137-2_0_3_node_9 | 0.4 | n |  | TRUE
29 | bus_LV_1137-2_0_3_node_10 | 0.4 | n |  | TRUE
30 | bus_LV_1137-2_0_3_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_1137-2_0_3_node_16 | 0.4 | n |  | TRUE
32 | bus_LV_1137-2_0_3_node_14 | 0.4 | n |  | TRUE
33 | bus_LV_1137-2_0_3_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_1137-2_0_3_node_29 | 0.4 | n |  | TRUE
35 | bus_MV_131_0_node_29 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1137-2_0_3_load_0 | 0 | 0.067544 | 0.016928 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1137-2_0_3_load_11 | 1 | 0.012945 | 0.0032443 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1137-2_0_3_load_35 | 3 | 0.013882 | 0.0034792 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1137-2_0_3_load_23 | 4 | 0.037883 | 0.0094944 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1137-2_0_3_load_24 | 5 | 0.0038719 | 0.00097038 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1137-2_0_3_load_27 | 6 | 0.0057801 | 0.0014486 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1137-2_0_3_load_39 | 7 | 0.0062056 | 0.0015553 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1137-2_0_3_load_31 | 8 | 0.0018416 | 0.00046154 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1137-2_0_3_load_32 | 9 | 0.0037675 | 0.00094423 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1137-2_0_3_load_33 | 11 | 0.0033473 | 0.00083891 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1137-2_0_3_load_34 | 12 | 0.0055771 | 0.0013978 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1137-2_0_3_load_36 | 13 | 0.0056477 | 0.0014154 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1137-2_0_3_load_37 | 14 | 0.0056044 | 0.0014046 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1137-2_0_3_load_1 | 15 | 0.00069105 | 0.00017319 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1137-2_0_3_load_2 | 16 | 0.021014 | 0.0052665 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1137-2_0_3_load_4 | 17 | 0.00067674 | 0.00016961 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1137-2_0_3_load_6 | 20 | 0.0018193 | 0.00045596 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1137-2_0_3_load_22 | 22 | 0.0074468 | 0.0018664 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1137-2_0_3_load_21 | 23 | 0.010188 | 0.0025533 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1137-2_0_3_load_20 | 24 | 0.0041137 | 0.001031 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1137-2_0_3_load_15 | 25 | 0.00066794 | 0.0001674 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1137-2_0_3_load_18 | 26 | 0.0018052 | 0.00045242 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1137-2_0_3_load_8 | 27 | 0.0016518 | 0.00041397 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1137-2_0_3_load_17 | 30 | 0.0059448 | 0.0014899 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1137-2_0_3_load_16 | 31 | 0.0036588 | 0.00091698 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1137-2_0_3_load_14 | 32 | 0.00048261 | 0.00012095 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1137-2_0_3_load_29 | 34 | 0.0035568 | 0.00089143 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1137-2_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.049096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1137-2_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.071674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
2 | LV_1137-2_0_3_line_2 | NAYY 4x150 SE | 0 | 3 | 0.091071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1137-2_0_3_line_3 | NAYY 4x150 SE | 2 | 6 | 0.021804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1137-2_0_3_line_4 | NAYY 4x150 SE | 2 | 4 | 0.0095809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1137-2_0_3_line_5 | NAYY 4x150 SE | 3 | 13 | 0.010302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1137-2_0_3_line_6 | NAYY 4x150 SE | 3 | 12 | 0.018722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1137-2_0_3_line_7 | NAYY 4x150 SE | 4 | 5 | 0.031319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1137-2_0_3_line_8 | NAYY 4x150 SE | 5 | 33 | 0.0075541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1137-2_0_3_line_9 | NAYY 4x150 SE | 5 | 31 | 0.095295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
10 | LV_1137-2_0_3_line_10 | NAYY 4x150 SE | 6 | 7 | 0.033518 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1137-2_0_3_line_11 | NAYY 4x150 SE | 8 | 9 | 0.019958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1137-2_0_3_line_12 | NAYY 4x150 SE | 8 | 10 | 0.1245 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1137-2_0_3_line_13 | NAYY 4x150 SE | 9 | 11 | 0.013162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1137-2_0_3_line_14 | NAYY 4x150 SE | 10 | 33 | 0.12601 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1137-2_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.028315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1137-2_0_3_line_16 | NAYY 4x150 SE | 15 | 16 | 0.020519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1137-2_0_3_line_17 | NAYY 4x150 SE | 16 | 17 | 0.0098071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1137-2_0_3_line_18 | NAYY 4x150 SE | 17 | 21 | 0.005759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1137-2_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.003443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1137-2_0_3_line_20 | NAYY 4x150 SE | 18 | 20 | 0.015098 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1137-2_0_3_line_21 | NAYY 4x150 SE | 19 | 22 | 0.045628 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1137-2_0_3_line_22 | NAYY 4x150 SE | 19 | 23 | 0.018739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1137-2_0_3_line_23 | NAYY 4x150 SE | 21 | 24 | 0.018854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1137-2_0_3_line_24 | NAYY 4x150 SE | 21 | 25 | 0.017001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1137-2_0_3_line_25 | NAYY 4x150 SE | 21 | 26 | 0.021712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1137-2_0_3_line_26 | NAYY 4x150 SE | 23 | 24 | 0.027485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1137-2_0_3_line_27 | NAYY 4x150 SE | 25 | 29 | 0.032099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1137-2_0_3_line_28 | NAYY 4x150 SE | 26 | 30 | 0.015708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1137-2_0_3_line_29 | NAYY 4x150 SE | 27 | 28 | 0.011233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1137-2_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.004248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1137-2_0_3_line_31 | NAYY 4x150 SE | 29 | 31 | 0.086993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1137-2_0_3_line_32 | NAYY 4x150 SE | 29 | 32 | 0.015211 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1137-2_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.0079256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1137-2_0_3_trafo_16 | 0.25 MVA 20/0.4 kV | 35 | 31 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2640842.4028 | 1226885.3905 | 2640862.5464 | 1226930.164
1 | 2640862.5464 | 1226930.164 | 2640923.8315 | 1226892.9985
2 | 2640862.5464 | 1226930.164 | 2640952.6639 | 1226943.3064
3 | 2640923.8315 | 1226892.9985 | 2640945.1084 | 1226897.7647
4 | 2640923.8315 | 1226892.9985 | 2640926.6822 | 1226884.0126 | 2640926.7288 | 1226883.8662
5 | 2640951.2413 | 1226953.5094 | 2640952.6639 | 1226943.3064
6 | 2640955.2494 | 1226924.7643 | 2640952.6639 | 1226943.3064
7 | 2640926.7288 | 1226883.8662 | 2640927.3174 | 1226882.0158 | 2640933.3026 | 1226867.9706 | 2640939.4907 | 1226855.2905
8 | 2640942.8038 | 1226848.5017 | 2640939.4907 | 1226855.2905
9 | 2640844.5583 | 1226863.5943 | 2640939.4907 | 1226855.2905
10 | 2640945.1084 | 1226897.7647 | 2640955.015 | 1226899.9838 | 2640958.7543 | 1226900.6544 | 2640962.0233 | 1226900.2766 | 2640964.8377 | 1226898.7729 | 2640969.1657 | 1226889.8861 | 2640971.4638 | 1226887.6583
11 | 2641021.3963 | 1226933.5863 | 2641022.8933 | 1226940.1088 | 2641027.1451 | 1226952.6749
12 | 2641048.7728 | 1226812.8316 | 2641024.7907 | 1226901.2204 | 2641020.8041 | 1226918.8481 | 2641020.5241 | 1226929.7862 | 2641021.3963 | 1226933.5863
13 | 2641027.1451 | 1226952.6749 | 2641031.3636 | 1226965.1424
14 | 2640942.8038 | 1226848.5017 | 2640951.5025 | 1226833.3078 | 2640961.263 | 1226823.5356 | 2640976.5635 | 1226813.7683 | 2640994.0339 | 1226806.9732 | 2641007.195 | 1226800.8379 | 2641048.7728 | 1226812.8316
15 | 2640947.331 | 1226981.5526 | 2640951.2413 | 1226953.5094
16 | 2640792.3438 | 1226708.9082 | 2640803.8844 | 1226725.874
17 | 2640809.4002 | 1226733.9829 | 2640803.8844 | 1226725.874
18 | 2640809.4002 | 1226733.9829 | 2640804.9415 | 1226737.6435
19 | 2640773.3287 | 1226680.3253 | 2640770.5709 | 1226682.3966
20 | 2640773.3287 | 1226680.3253 | 2640783.6651 | 1226669.3211
21 | 2640770.5709 | 1226682.3966 | 2640734.0789 | 1226709.7869
22 | 2640770.5709 | 1226682.3966 | 2640774.7258 | 1226689.8963 | 2640780.1619 | 1226698.4864
23 | 2640804.9415 | 1226737.6435 | 2640794.8593 | 1226721.7115
24 | 2640804.9415 | 1226737.6435 | 2640814.1494 | 1226751.9351
25 | 2640804.9415 | 1226737.6435 | 2640788.1616 | 1226751.4216
26 | 2640780.1619 | 1226698.4864 | 2640794.8593 | 1226721.7115
27 | 2640831.0535 | 1226779.2145 | 2640823.9215 | 1226767.1027 | 2640814.1494 | 1226751.9351
28 | 2640788.1616 | 1226751.4216 | 2640784.1952 | 1226754.6785 | 2640776.0437 | 1226761.4162
29 | 2640835.2277 | 1226778.3648 | 2640833.9693 | 1226776.1993 | 2640829.5789 | 1226768.6554
30 | 2640835.2277 | 1226778.3648 | 2640831.0535 | 1226779.2145
31 | 2640831.0535 | 1226779.2145 | 2640836.1595 | 1226789.4558 | 2640840.3332 | 1226800.8358 | 2640844.3249 | 1226817.7401 | 2640846.2377 | 1226832.7624 | 2640845.9656 | 1226851.4275 | 2640844.5583 | 1226863.5943
32 | 2640831.0535 | 1226779.2145 | 2640825.8016 | 1226780.2903 | 2640816.5223 | 1226783.5939
33 | 2640942.8038 | 1226848.5017 | 2640940.2651 | 1226840.9938

## bus_geodata
| x | y | coords
0 | 2640862.5464 | 1226930.164
1 | 2640842.4028 | 1226885.3905
2 | 2640923.8315 | 1226892.9985
3 | 2640952.6639 | 1226943.3064
4 | 2640926.7288 | 1226883.8662
5 | 2640939.4907 | 1226855.2905
6 | 2640945.1084 | 1226897.7647
7 | 2640971.4638 | 1226887.6583
8 | 2641021.3963 | 1226933.5863
9 | 2641027.1451 | 1226952.6749
10 | 2641048.7728 | 1226812.8316
11 | 2641031.3636 | 1226965.1424
12 | 2640955.2494 | 1226924.7643
13 | 2640951.2413 | 1226953.5094
14 | 2640947.331 | 1226981.5526
15 | 2640792.3438 | 1226708.9082
16 | 2640803.8844 | 1226725.874
17 | 2640809.4002 | 1226733.9829
18 | 2640773.3287 | 1226680.3253
19 | 2640770.5709 | 1226682.3966
20 | 2640783.6651 | 1226669.3211
21 | 2640804.9415 | 1226737.6435
22 | 2640734.0789 | 1226709.7869
23 | 2640780.1619 | 1226698.4864
24 | 2640794.8593 | 1226721.7115
25 | 2640814.1494 | 1226751.9351
26 | 2640788.1616 | 1226751.4216
27 | 2640829.5789 | 1226768.6554
28 | 2640835.2277 | 1226778.3648
29 | 2640831.0535 | 1226779.2145
30 | 2640776.0437 | 1226761.4162
31 | 2640844.5583 | 1226863.5943
32 | 2640816.5223 | 1226783.5939
33 | 2640942.8038 | 1226848.5017
34 | 2640940.2651 | 1226840.9938
35 | 2640831.0535 | 1226779.2145

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97733 | -0.15888 | 0.067544 | 0.016928
1 | 0.97641 | -0.16552 | 0.012945 | 0.0032443
2 | 0.98315 | -0.11747 | 0 | 0
3 | 0.97324 | -0.18823 | 0.013882 | 0.0034792
4 | 0.98401 | -0.11138 | 0.037883 | 0.0094944
5 | 0.98769 | -0.085478 | 0.0038719 | 0.00097038
6 | 0.98277 | -0.12017 | 0.0057801 | 0.0014486
7 | 0.98247 | -0.12233 | 0.0062056 | 0.0015553
8 | 0.9843 | -0.10952 | 0.0018416 | 0.00046154
9 | 0.9841 | -0.11099 | 0.0037675 | 0.00094423
10 | 0.98592 | -0.098043 | 0 | 0
11 | 0.98403 | -0.11144 | 0.0033473 | 0.00083891
12 | 0.97308 | -0.18933 | 0.0055771 | 0.0013978
13 | 0.97307 | -0.18945 | 0.0056477 | 0.0014154
14 | 0.97283 | -0.19113 | 0.0056044 | 0.0014046
15 | 0.98856 | -0.08009 | 0.00069105 | 0.00017319
16 | 0.98858 | -0.079945 | 0.021014 | 0.0052665
17 | 0.98889 | -0.077772 | 0.00067674 | 0.00016961
18 | 0.9874 | -0.088306 | 0 | 0
19 | 0.98741 | -0.088242 | 0 | 0
20 | 0.98736 | -0.088587 | 0.0018193 | 0.00045596
21 | 0.98908 | -0.076456 | 0 | 0
22 | 0.98692 | -0.091723 | 0.0074468 | 0.0018664
23 | 0.98766 | -0.086464 | 0.010188 | 0.0025533
24 | 0.98844 | -0.080995 | 0.0041137 | 0.001031
25 | 0.99039 | -0.067151 | 0.00066794 | 0.0001674
26 | 0.98883 | -0.078174 | 0.0018052 | 0.00045242
27 | 0.99287 | -0.049692 | 0.0016518 | 0.00041397
28 | 0.9929 | -0.049504 | 0 | 0
29 | 0.99291 | -0.049433 | 0 | 0
30 | 0.9887 | -0.079127 | 0.0059448 | 0.0014899
31 | 1 | 0 | -0.23908 | -0.06028
32 | 0.9929 | -0.049507 | 0.00048261 | 0.00012095
33 | 0.98755 | -0.086447 | 0 | 0
34 | 0.98751 | -0.086735 | 0.0035568 | 0.00089143
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.012957 | 0.0032483 | -0.012945 | -0.0032443 | 1.1923e-05 | 3.971e-06 | 0.019727 | 0.019728 | 0.019728 | 0.97733 | -0.15888 | 0.97641 | -0.16552 | 7.3065
1 | -0.11134 | -0.027921 | 0.11198 | 0.028167 | 0.00064267 | 0.00024537 | 0.16953 | 0.16953 | 0.16953 | 0.97733 | -0.15888 | 0.98315 | -0.11747 | 31.3938
2 | 0.030841 | 0.0077449 | -0.030715 | -0.0076978 | 0.00012533 | 4.7066e-05 | 0.046961 | 0.046962 | 0.046962 | 0.97733 | -0.15888 | 0.97324 | -0.18823 | 17.3932
3 | 0.011992 | 0.0030056 | -0.011988 | -0.0030042 | 4.4822e-06 | 1.4475e-06 | 0.01815 | 0.01815 | 0.01815 | 0.98315 | -0.11747 | 0.98277 | -0.12017 | 6.7223
4 | -0.12398 | -0.031172 | 0.12408 | 0.031213 | 0.00010529 | 4.0252e-05 | 0.18768 | 0.18768 | 0.18768 | 0.98315 | -0.11747 | 0.98401 | -0.11138 | 34.7549
5 | 0.011255 | 0.0028208 | -0.011253 | -0.0028202 | 1.9036e-06 | 6.0418e-07 | 0.017209 | 0.017209 | 0.017209 | 0.97324 | -0.18823 | 0.97307 | -0.18945 | 6.3736
6 | 0.0055779 | 0.0013978 | -0.0055771 | -0.0013978 | 8.4968e-07 | 9.4193e-08 | 0.0085283 | 0.0085284 | 0.0085284 | 0.97324 | -0.18823 | 0.97308 | -0.18933 | 3.1587
7 | -0.16196 | -0.040707 | 0.16255 | 0.040932 | 0.00058635 | 0.00022472 | 0.24496 | 0.24496 | 0.24496 | 0.98401 | -0.11138 | 0.98769 | -0.085478 | 45.3635
8 | 0.012545 | 0.0031447 | -0.012544 | -0.0031441 | 1.6839e-06 | 5.5099e-07 | 0.018901 | 0.018901 | 0.018901 | 0.98769 | -0.085478 | 0.98755 | -0.086447 | 7.0002
9 | -0.17897 | -0.045047 | 0.18113 | 0.045876 | 0.0021626 | 0.00082929 | 0.2697 | 0.2697 | 0.2697 | 0.98769 | -0.085478 | 1 | 0 | 49.9437
10 | 0.0062075 | 0.0015556 | -0.0062056 | -0.0015553 | 1.8476e-06 | 2.8602e-07 | 0.0093987 | 0.0093988 | 0.0093988 | 0.98277 | -0.12017 | 0.98247 | -0.12233 | 3.481
11 | 0.0071165 | 0.0017834 | -0.007115 | -0.0017831 | 1.4414e-06 | 3.0076e-07 | 0.010758 | 0.010758 | 0.010758 | 0.9843 | -0.10952 | 0.9841 | -0.11099 | 3.9846
12 | -0.008958 | -0.0022449 | 0.0089723 | 0.0022488 | 1.4246e-05 | 3.8943e-06 | 0.013542 | 0.013542 | 0.013542 | 0.9843 | -0.10952 | 0.98592 | -0.098043 | 5.0156
13 | 0.0033475 | 0.00083883 | -0.0033473 | -0.00083891 | 2.1042e-07 | -8.6285e-08 | 0.0050616 | 0.0050617 | 0.0050617 | 0.9841 | -0.11099 | 0.98403 | -0.11144 | 1.8747
14 | -0.0089723 | -0.0022488 | 0.0089867 | 0.0022527 | 1.4418e-05 | 3.9359e-06 | 0.013542 | 0.013541 | 0.013542 | 0.98592 | -0.098043 | 0.98755 | -0.086447 | 5.0154
15 | 0.0056057 | 0.0014047 | -0.0056044 | -0.0014046 | 1.2983e-06 | 1.4771e-07 | 0.0085721 | 0.0085723 | 0.0085723 | 0.97307 | -0.18945 | 0.97283 | -0.19113 | 3.1749
16 | -0.00069105 | -0.00017319 | 0.00069106 | 0.00017294 | 1.3852e-08 | -2.5775e-07 | 0.0010402 | 0.0010401 | 0.0010402 | 0.98856 | -0.08009 | 0.98858 | -0.079945 | 0.38526
17 | -0.021705 | -0.0054395 | 0.021711 | 0.0054419 | 6.5316e-06 | 2.3864e-06 | 0.03267 | 0.03267 | 0.03267 | 0.98858 | -0.079945 | 0.98889 | -0.077772 | 12.1
18 | -0.022388 | -0.0056115 | 0.022392 | 0.005613 | 4.0784e-06 | 1.4947e-06 | 0.033688 | 0.033688 | 0.033688 | 0.98889 | -0.077772 | 0.98908 | -0.076456 | 12.4771
19 | -0.0018194 | -0.0004558 | 0.0018194 | 0.00045576 | 1.615e-08 | -3.7828e-08 | 0.0027417 | 0.0027417 | 0.0027417 | 0.9874 | -0.088306 | 0.98741 | -0.088242 | 1.0155
20 | 0.0018194 | 0.0004558 | -0.0018193 | -0.00045596 | 7.0819e-08 | -1.6586e-07 | 0.0027417 | 0.0027418 | 0.0027418 | 0.9874 | -0.088306 | 0.98736 | -0.088587 | 1.0155
21 | 0.0074504 | 0.0018671 | -0.0074468 | -0.0018664 | 3.5892e-06 | 7.9712e-07 | 0.011228 | 0.011228 | 0.011228 | 0.98741 | -0.088242 | 0.98692 | -0.091723 | 4.1585
22 | -0.0092698 | -0.0023229 | 0.0092721 | 0.0023235 | 2.2819e-06 | 6.3788e-07 | 0.013969 | 0.013969 | 0.013969 | 0.98741 | -0.088242 | 0.98766 | -0.086464 | 5.1738
23 | 0.023603 | 0.0059186 | -0.023588 | -0.0059132 | 1.4836e-05 | 5.4643e-06 | 0.035511 | 0.035511 | 0.035511 | 0.98908 | -0.076456 | 0.98844 | -0.080995 | 13.1522
24 | -0.053748 | -0.013474 | 0.053817 | 0.013501 | 6.9367e-05 | 2.6461e-05 | 0.080862 | 0.080862 | 0.080862 | 0.98908 | -0.076456 | 0.99039 | -0.067151 | 29.949
25 | 0.0077526 | 0.0019429 | -0.0077508 | -0.0019424 | 1.843e-06 | 4.3027e-07 | 0.011663 | 0.011663 | 0.011663 | 0.98908 | -0.076456 | 0.98883 | -0.078174 | 4.3198
26 | -0.01946 | -0.0048769 | 0.019475 | 0.0048822 | 1.4742e-05 | 5.3179e-06 | 0.029318 | 0.029318 | 0.029318 | 0.98766 | -0.086464 | 0.98844 | -0.080995 | 10.8586
27 | -0.054485 | -0.013668 | 0.054619 | 0.01372 | 0.00013424 | 5.1216e-05 | 0.081866 | 0.081866 | 0.081866 | 0.99039 | -0.067151 | 0.99291 | -0.049433 | 30.3207
28 | 0.0059456 | 0.00149 | -0.0059448 | -0.0014899 | 7.8462e-07 | 1.003e-07 | 0.008947 | 0.0089471 | 0.0089471 | 0.98883 | -0.078174 | 0.9887 | -0.079127 | 3.3137
29 | -0.0016518 | -0.00041397 | 0.0016518 | 0.00041385 | 4.2954e-08 | -1.2876e-07 | 0.0024755 | 0.0024755 | 0.0024755 | 0.99287 | -0.049692 | 0.9929 | -0.049504 | 0.91686
30 | -0.0016518 | -0.00041385 | 0.0016518 | 0.0004138 | 1.6243e-08 | -4.8695e-08 | 0.0024755 | 0.0024754 | 0.0024755 | 0.9929 | -0.049504 | 0.99291 | -0.049433 | 0.91684
31 | -0.056754 | -0.014254 | 0.057147 | 0.014404 | 0.00039279 | 0.00014994 | 0.085064 | 0.085064 | 0.085064 | 0.99291 | -0.049433 | 1 | 0 | 31.5053
32 | 0.00048261 | 0.00012076 | -0.00048261 | -0.00012095 | 4.9646e-09 | -1.9482e-07 | 0.00072319 | 0.00072326 | 0.00072326 | 0.99291 | -0.049433 | 0.9929 | -0.049507 | 0.26787
33 | 0.003557 | 0.00089138 | -0.0035568 | -0.00089143 | 1.4206e-07 | -4.6763e-08 | 0.0053595 | 0.0053596 | 0.0053596 | 0.98755 | -0.086447 | 0.98751 | -0.086735 | 1.985

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24274 | 0.061197

## res_load
| p_mw | q_mvar
0 | 0.067544 | 0.016928
1 | 0.012945 | 0.0032443
2 | 0.013882 | 0.0034792
3 | 0.037883 | 0.0094944
4 | 0.0038719 | 0.00097038
5 | 0.0057801 | 0.0014486
6 | 0.0062056 | 0.0015553
7 | 0.0018416 | 0.00046154
8 | 0.0037675 | 0.00094423
9 | 0.0033473 | 0.00083891
10 | 0.0055771 | 0.0013978
11 | 0.0056477 | 0.0014154
12 | 0.0056044 | 0.0014046
13 | 0.00069105 | 0.00017319
14 | 0.021014 | 0.0052665
15 | 0.00067674 | 0.00016961
16 | 0.0018193 | 0.00045596
17 | 0.0074468 | 0.0018664
18 | 0.010188 | 0.0025533
19 | 0.0041137 | 0.001031
20 | 0.00066794 | 0.0001674
21 | 0.0018052 | 0.00045242
22 | 0.0016518 | 0.00041397
23 | 0.0059448 | 0.0014899
24 | 0.0036588 | 0.00091698
25 | 0.00048261 | 0.00012095
26 | 0.0035568 | 0.00089143

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1