## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_114-4_1_6_node_18 | 0.4 | n |  | TRUE
1 | bus_LV_114-4_1_6_node_19 | 0.4 | n |  | TRUE
2 | bus_LV_114-4_1_6_node_20 | 0.4 | n |  | TRUE
3 | bus_LV_114-4_1_6_node_21 | 0.4 | n |  | TRUE
4 | bus_LV_114-4_1_6_node_282 | 0.4 | n |  | TRUE
5 | bus_LV_114-4_1_6_node_22 | 0.4 | n |  | TRUE
6 | bus_LV_114-4_1_6_node_51 | 0.4 | n |  | TRUE
7 | bus_LV_114-4_1_6_node_69 | 0.4 | n |  | TRUE
8 | bus_LV_114-4_1_6_node_67 | 0.4 | n |  | TRUE
9 | bus_LV_114-4_1_6_node_68 | 0.4 | n |  | TRUE
10 | bus_LV_114-4_1_6_node_70 | 0.4 | n |  | TRUE
11 | bus_LV_114-4_1_6_node_178 | 0.4 | n |  | TRUE
12 | bus_LV_114-4_1_6_node_183 | 0.4 | n |  | TRUE
13 | bus_LV_114-4_1_6_node_73 | 0.4 | n |  | TRUE
14 | bus_LV_114-4_1_6_node_79 | 0.4 | n |  | TRUE
15 | bus_LV_114-4_1_6_node_179 | 0.4 | n |  | TRUE
16 | bus_LV_114-4_1_6_node_78 | 0.4 | n |  | TRUE
17 | bus_LV_114-4_1_6_node_80 | 0.4 | n |  | TRUE
18 | bus_LV_114-4_1_6_node_81 | 0.4 | n |  | TRUE
19 | bus_LV_114-4_1_6_node_82 | 0.4 | n |  | TRUE
20 | bus_LV_114-4_1_6_node_83 | 0.4 | n |  | TRUE
21 | bus_LV_114-4_1_6_node_219 | 0.4 | n |  | TRUE
22 | bus_LV_114-4_1_6_node_212 | 0.4 | n |  | TRUE
23 | bus_LV_114-4_1_6_node_132 | 0.4 | n |  | TRUE
24 | bus_LV_114-4_1_6_node_133 | 0.4 | n |  | TRUE
25 | bus_LV_114-4_1_6_node_135 | 0.4 | n |  | TRUE
26 | bus_LV_114-4_1_6_node_136 | 0.4 | n |  | TRUE
27 | bus_LV_114-4_1_6_node_134 | 0.4 | n |  | TRUE
28 | bus_LV_114-4_1_6_node_141 | 0.4 | n |  | TRUE
29 | bus_LV_114-4_1_6_node_159 | 0.4 | n |  | TRUE
30 | bus_LV_114-4_1_6_node_147 | 0.4 | n |  | TRUE
31 | bus_LV_114-4_1_6_node_144 | 0.4 | n |  | TRUE
32 | bus_LV_114-4_1_6_node_137 | 0.4 | n |  | TRUE
33 | bus_LV_114-4_1_6_node_138 | 0.4 | n |  | TRUE
34 | bus_LV_114-4_1_6_node_139 | 0.4 | n |  | TRUE
35 | bus_LV_114-4_1_6_node_140 | 0.4 | n |  | TRUE
36 | bus_LV_114-4_1_6_node_143 | 0.4 | n |  | TRUE
37 | bus_LV_114-4_1_6_node_246 | 0.4 | n |  | TRUE
38 | bus_LV_114-4_1_6_node_254 | 0.4 | n |  | TRUE
39 | bus_LV_114-4_1_6_node_149 | 0.4 | n |  | TRUE
40 | bus_LV_114-4_1_6_node_148 | 0.4 | n |  | TRUE
41 | bus_LV_114-4_1_6_node_142 | 0.4 | n |  | TRUE
42 | bus_LV_114-4_1_6_node_166 | 0.4 | n |  | TRUE
43 | bus_LV_114-4_1_6_node_145 | 0.4 | n |  | TRUE
44 | bus_LV_114-4_1_6_node_146 | 0.4 | n |  | TRUE
45 | bus_LV_114-4_1_6_node_165 | 0.4 | n |  | TRUE
46 | bus_LV_114-4_1_6_node_150 | 0.4 | n |  | TRUE
47 | bus_LV_114-4_1_6_node_151 | 0.4 | n |  | TRUE
48 | bus_LV_114-4_1_6_node_152 | 0.4 | n |  | TRUE
49 | bus_LV_114-4_1_6_node_153 | 0.4 | n |  | TRUE
50 | bus_LV_114-4_1_6_node_154 | 0.4 | n |  | TRUE
51 | bus_LV_114-4_1_6_node_232 | 0.4 | n |  | TRUE
52 | bus_LV_114-4_1_6_node_249 | 0.4 | n |  | TRUE
53 | bus_LV_114-4_1_6_node_155 | 0.4 | n |  | TRUE
54 | bus_LV_114-4_1_6_node_156 | 0.4 | n |  | TRUE
55 | bus_LV_114-4_1_6_node_157 | 0.4 | n |  | TRUE
56 | bus_LV_114-4_1_6_node_158 | 0.4 | n |  | TRUE
57 | bus_LV_114-4_1_6_node_230 | 0.4 | n |  | TRUE
58 | bus_LV_114-4_1_6_node_248 | 0.4 | n |  | TRUE
59 | bus_LV_114-4_1_6_node_250 | 0.4 | n |  | TRUE
60 | bus_LV_114-4_1_6_node_160 | 0.4 | n |  | TRUE
61 | bus_LV_114-4_1_6_node_161 | 0.4 | n |  | TRUE
62 | bus_LV_114-4_1_6_node_162 | 0.4 | n |  | TRUE
63 | bus_LV_114-4_1_6_node_163 | 0.4 | n |  | TRUE
64 | bus_LV_114-4_1_6_node_229 | 0.4 | n |  | TRUE
65 | bus_LV_114-4_1_6_node_228 | 0.4 | n |  | TRUE
66 | bus_LV_114-4_1_6_node_164 | 0.4 | n |  | TRUE
67 | bus_LV_114-4_1_6_node_167 | 0.4 | n |  | TRUE
68 | bus_LV_114-4_1_6_node_255 | 0.4 | n |  | TRUE
69 | bus_LV_114-4_1_6_node_173 | 0.4 | n |  | TRUE
70 | bus_LV_114-4_1_6_node_174 | 0.4 | n |  | TRUE
71 | bus_LV_114-4_1_6_node_175 | 0.4 | n |  | TRUE
72 | bus_LV_114-4_1_6_node_176 | 0.4 | n |  | TRUE
73 | bus_LV_114-4_1_6_node_238 | 0.4 | n |  | TRUE
74 | bus_LV_114-4_1_6_node_239 | 0.4 | n |  | TRUE
75 | bus_LV_114-4_1_6_node_236 | 0.4 | n |  | TRUE
76 | bus_LV_114-4_1_6_node_177 | 0.4 | n |  | TRUE
77 | bus_LV_114-4_1_6_node_180 | 0.4 | n |  | TRUE
78 | bus_LV_114-4_1_6_node_266 | 0.4 | n |  | TRUE
79 | bus_LV_114-4_1_6_node_181 | 0.4 | n |  | TRUE
80 | bus_LV_114-4_1_6_node_231 | 0.4 | n |  | TRUE
81 | bus_LV_114-4_1_6_node_182 | 0.4 | n |  | TRUE
82 | bus_LV_114-4_1_6_node_200 | 0.4 | n |  | TRUE
83 | bus_LV_114-4_1_6_node_201 | 0.4 | n |  | TRUE
84 | bus_LV_114-4_1_6_node_220 | 0.4 | n |  | TRUE
85 | bus_LV_114-4_1_6_node_203 | 0.4 | n |  | TRUE
86 | bus_LV_114-4_1_6_node_204 | 0.4 | n |  | TRUE
87 | bus_LV_114-4_1_6_node_205 | 0.4 | n |  | TRUE
88 | bus_LV_114-4_1_6_node_206 | 0.4 | n |  | TRUE
89 | bus_LV_114-4_1_6_node_211 | 0.4 | n |  | TRUE
90 | bus_LV_114-4_1_6_node_209 | 0.4 | n |  | TRUE
91 | bus_LV_114-4_1_6_node_210 | 0.4 | n |  | TRUE
92 | bus_LV_114-4_1_6_node_213 | 0.4 | n |  | TRUE
93 | bus_LV_114-4_1_6_node_214 | 0.4 | n |  | TRUE
94 | bus_LV_114-4_1_6_node_215 | 0.4 | n |  | TRUE
95 | bus_LV_114-4_1_6_node_216 | 0.4 | n |  | TRUE
96 | bus_LV_114-4_1_6_node_217 | 0.4 | n |  | TRUE
97 | bus_LV_114-4_1_6_node_218 | 0.4 | n |  | TRUE
98 | bus_LV_114-4_1_6_node_221 | 0.4 | n |  | TRUE
99 | bus_LV_114-4_1_6_node_243 | 0.4 | n |  | TRUE
100 | bus_LV_114-4_1_6_node_240 | 0.4 | n |  | TRUE
101 | bus_LV_114-4_1_6_node_233 | 0.4 | n |  | TRUE
102 | bus_LV_114-4_1_6_node_234 | 0.4 | n |  | TRUE
103 | bus_LV_114-4_1_6_node_244 | 0.4 | n |  | TRUE
104 | bus_LV_114-4_1_6_node_237 | 0.4 | n |  | TRUE
105 | bus_LV_114-4_1_6_node_242 | 0.4 | n |  | TRUE
106 | bus_LV_114-4_1_6_node_241 | 0.4 | n |  | TRUE
107 | bus_LV_114-4_1_6_node_245 | 0.4 | n |  | TRUE
108 | bus_LV_114-4_1_6_node_247 | 0.4 | n |  | TRUE
109 | bus_LV_114-4_1_6_node_251 | 0.4 | n |  | TRUE
110 | bus_LV_114-4_1_6_node_252 | 0.4 | n |  | TRUE
111 | bus_LV_114-4_1_6_node_253 | 0.4 | n |  | TRUE
112 | bus_MV_6_0_node_169 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_114-4_1_6_load_18 | 0 | 0.0010452 | 0.00026194 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_114-4_1_6_load_19 | 1 | 0.001114 | 0.00027921 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_114-4_1_6_load_20 | 2 | 0.0028756 | 0.00072069 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_114-4_1_6_load_282 | 4 | 0.0072283 | 0.0018116 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_114-4_1_6_load_22 | 5 | 0.00026007 | 6.518e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_114-4_1_6_load_51 | 6 | 0.0015319 | 0.00038393 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_114-4_1_6_load_67 | 8 | 0.0012641 | 0.00031682 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_114-4_1_6_load_68 | 9 | 0.00053137 | 0.00013317 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_114-4_1_6_load_178 | 11 | 0.0032069 | 0.00080373 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_114-4_1_6_load_183 | 12 | 0.0020897 | 0.00052373 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_114-4_1_6_load_79 | 14 | 0.001001 | 0.00025088 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_114-4_1_6_load_78 | 16 | 0.0021724 | 0.00054446 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_114-4_1_6_load_80 | 17 | 0.0014624 | 0.00036652 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_114-4_1_6_load_82 | 19 | 0.00039627 | 9.9314e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_114-4_1_6_load_83 | 20 | 0.0015067 | 0.0003776 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_114-4_1_6_load_219 | 21 | 0.0005419 | 0.00013581 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_114-4_1_6_load_132 | 23 | 0.0035282 | 0.00088425 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_114-4_1_6_load_136 | 26 | 0.0012993 | 0.00032565 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_114-4_1_6_load_159 | 29 | 0.00066946 | 0.00016778 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_114-4_1_6_load_147 | 30 | 0.0026933 | 0.000675 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_114-4_1_6_load_144 | 31 | 0.010872 | 0.0027247 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_114-4_1_6_load_137 | 32 | 0.00042296 | 0.000106 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_114-4_1_6_load_246 | 37 | 0.00057131 | 0.00014318 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_114-4_1_6_load_149 | 39 | 0.00026167 | 6.558e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_114-4_1_6_load_148 | 40 | 0.0014458 | 0.00036236 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_114-4_1_6_load_142 | 41 | 0.001705 | 0.00042731 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_114-4_1_6_load_145 | 43 | 0.0019941 | 0.00049977 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_114-4_1_6_load_150 | 46 | 0.0054232 | 0.0013592 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_114-4_1_6_load_151 | 47 | 0.0042328 | 0.0010608 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_114-4_1_6_load_154 | 50 | 0.0014444 | 0.00036201 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_114-4_1_6_load_232 | 51 | 0.00063353 | 0.00015878 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_114-4_1_6_load_249 | 52 | 0.0023208 | 0.00058164 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_114-4_1_6_load_155 | 53 | 0.0063577 | 0.0015934 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_114-4_1_6_load_157 | 55 | 0.0031199 | 0.00078192 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_114-4_1_6_load_230 | 57 | 0.00076062 | 0.00019063 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_114-4_1_6_load_250 | 59 | 0.0038917 | 0.00097534 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_114-4_1_6_load_160 | 60 | 0.019969 | 0.0050046 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_114-4_1_6_load_163 | 63 | 0.0021435 | 0.00053721 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_114-4_1_6_load_228 | 65 | 0.0019075 | 0.00047807 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_114-4_1_6_load_164 | 66 | 0.00097865 | 0.00024527 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_114-4_1_6_load_167 | 67 | 0.0027773 | 0.00069606 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_114-4_1_6_load_255 | 68 | 0.0073672 | 0.0018464 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_114-4_1_6_load_173 | 69 | 0.00012204 | 3.0586e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_114-4_1_6_load_175 | 71 | 0.00046448 | 0.00011641 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_114-4_1_6_load_238 | 73 | 0.00069792 | 0.00017492 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_114-4_1_6_load_239 | 74 | 0.00054944 | 0.0001377 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_114-4_1_6_load_236 | 75 | 0.00061401 | 0.00015388 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_114-4_1_6_load_177 | 76 | 0.0010335 | 0.00025901 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_114-4_1_6_load_266 | 78 | 0.0010951 | 0.00027445 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_114-4_1_6_load_231 | 80 | 0.0010714 | 0.00026852 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_114-4_1_6_load_182 | 81 | 0.0077992 | 0.0019547 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_114-4_1_6_load_200 | 82 | 0.00081279 | 0.0002037 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_114-4_1_6_load_201 | 83 | 0.0016944 | 0.00042466 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_114-4_1_6_load_220 | 84 | 0.0004587 | 0.00011496 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_114-4_1_6_load_203 | 85 | 0.00039904 | 0.00010001 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_114-4_1_6_load_205 | 87 | 0.00093779 | 0.00023503 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_114-4_1_6_load_206 | 88 | 0.0008943 | 0.00022413 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_114-4_1_6_load_209 | 90 | 0.00052016 | 0.00013036 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_114-4_1_6_load_213 | 92 | 0.00045728 | 0.0001146 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_114-4_1_6_load_215 | 94 | 0.00079073 | 0.00019818 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_114-4_1_6_load_216 | 95 | 0.00024349 | 6.1025e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_114-4_1_6_load_218 | 97 | 0.001165 | 0.00029197 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_114-4_1_6_load_221 | 98 | 0.00071972 | 0.00018038 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_114-4_1_6_load_243 | 99 | 0.0052329 | 0.0013115 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_114-4_1_6_load_240 | 100 | 0.00012464 | 3.1237e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_114-4_1_6_load_234 | 102 | 0.0013392 | 0.00033563 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_114-4_1_6_load_244 | 103 | 0.0016389 | 0.00041074 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_114-4_1_6_load_237 | 104 | 0.0039069 | 0.00097915 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_114-4_1_6_load_241 | 106 | 0.0012298 | 0.00030821 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_114-4_1_6_load_245 | 107 | 0.0001319 | 3.3057e-05 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_114-4_1_6_load_247 | 108 | 0.004698 | 0.0011774 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_114-4_1_6_load_252 | 110 | 0.0011137 | 0.00027913 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_114-4_1_6_load_253 | 111 | 0.0011419 | 0.00028619 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_114-4_1_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.16666 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_114-4_1_6_line_1 | NAYY 4x150 SE | 0 | 2 | 0.021739 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_114-4_1_6_line_2 | NAYY 4x150 SE | 1 | 3 | 0.1855 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_114-4_1_6_line_3 | NAYY 4x150 SE | 1 | 4 | 0.18636 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_114-4_1_6_line_4 | NAYY 4x150 SE | 2 | 5 | 0.004538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_114-4_1_6_line_5 | NAYY 4x150 SE | 3 | 6 | 0.0061432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_114-4_1_6_line_6 | NAYY 4x150 SE | 5 | 7 | 0.207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_114-4_1_6_line_7 | NAYY 4x150 SE | 7 | 10 | 0.22864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_114-4_1_6_line_8 | NAYY 4x150 SE | 7 | 8 | 0.3195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_114-4_1_6_line_9 | NAYY 4x150 SE | 8 | 9 | 0.18988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_114-4_1_6_line_10 | NAYY 4x150 SE | 10 | 11 | 0.19082 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_114-4_1_6_line_11 | NAYY 4x150 SE | 10 | 12 | 0.055121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_114-4_1_6_line_12 | NAYY 4x150 SE | 11 | 76 | 0.12391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
13 | LV_114-4_1_6_line_13 | NAYY 4x150 SE | 12 | 81 | 0.064472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_114-4_1_6_line_14 | NAYY 4x150 SE | 13 | 14 | 0.18356 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_114-4_1_6_line_15 | NAYY 4x150 SE | 13 | 15 | 0.26029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_114-4_1_6_line_16 | NAYY 4x150 SE | 14 | 16 | 0.02549 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_114-4_1_6_line_17 | NAYY 4x150 SE | 15 | 63 | 0.17604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_114-4_1_6_line_18 | NAYY 4x150 SE | 15 | 76 | 0.18429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_114-4_1_6_line_19 | NAYY 4x150 SE | 17 | 18 | 0.24767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_114-4_1_6_line_20 | NAYY 4x150 SE | 18 | 19 | 0.017588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_114-4_1_6_line_21 | NAYY 4x150 SE | 18 | 20 | 0.017248 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_114-4_1_6_line_22 | NAYY 4x150 SE | 19 | 21 | 0.024178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_114-4_1_6_line_23 | NAYY 4x150 SE | 20 | 22 | 0.061029 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_114-4_1_6_line_24 | NAYY 4x150 SE | 21 | 36 | 0.054229 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_114-4_1_6_line_25 | NAYY 4x150 SE | 22 | 91 | 0.23042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_114-4_1_6_line_26 | NAYY 4x150 SE | 23 | 24 | 0.030427 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_114-4_1_6_line_27 | NAYY 4x150 SE | 24 | 25 | 0.040768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_114-4_1_6_line_28 | NAYY 4x150 SE | 24 | 26 | 0.053391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_114-4_1_6_line_29 | NAYY 4x150 SE | 25 | 30 | 0.021929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_114-4_1_6_line_30 | NAYY 4x150 SE | 25 | 31 | 0.087516 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_114-4_1_6_line_31 | NAYY 4x150 SE | 26 | 29 | 0.031646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_114-4_1_6_line_32 | NAYY 4x150 SE | 27 | 28 | 0.051189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_114-4_1_6_line_33 | NAYY 4x150 SE | 27 | 29 | 0.018399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_114-4_1_6_line_34 | NAYY 4x150 SE | 28 | 39 | 0.063815 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_114-4_1_6_line_35 | NAYY 4x150 SE | 28 | 40 | 0.027545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_114-4_1_6_line_36 | NAYY 4x150 SE | 28 | 33 | 0.075505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_114-4_1_6_line_37 | NAYY 4x150 SE | 30 | 46 | 0.0089275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_114-4_1_6_line_38 | NAYY 4x150 SE | 31 | 43 | 0.055412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_114-4_1_6_line_39 | NAYY 4x150 SE | 32 | 33 | 0.020538 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_114-4_1_6_line_40 | NAYY 4x150 SE | 32 | 34 | 0.19146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_114-4_1_6_line_41 | NAYY 4x150 SE | 33 | 35 | 0.031436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_114-4_1_6_line_42 | NAYY 4x150 SE | 34 | 36 | 0.10153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_114-4_1_6_line_43 | NAYY 4x150 SE | 35 | 37 | 0.0031132 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_114-4_1_6_line_44 | NAYY 4x150 SE | 35 | 38 | 0.012009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_114-4_1_6_line_45 | NAYY 4x150 SE | 37 | 107 | 0.020171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_114-4_1_6_line_46 | NAYY 4x150 SE | 38 | 105 | 0.008151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_114-4_1_6_line_47 | NAYY 4x150 SE | 38 | 111 | 0.047077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_114-4_1_6_line_48 | NAYY 4x150 SE | 41 | 42 | 0.011915 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_114-4_1_6_line_49 | NAYY 4x150 SE | 42 | 67 | 0.036302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_114-4_1_6_line_50 | NAYY 4x150 SE | 42 | 44 | 0.009587 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_114-4_1_6_line_51 | NAYY 4x150 SE | 43 | 44 | 0.02487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_114-4_1_6_line_52 | NAYY 4x150 SE | 44 | 45 | 0.014558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_114-4_1_6_line_53 | NAYY 4x150 SE | 45 | 49 | 0.10648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_114-4_1_6_line_54 | NAYY 4x150 SE | 45 | 66 | 0.039295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_114-4_1_6_line_55 | NAYY 4x150 SE | 47 | 48 | 0.036308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_114-4_1_6_line_56 | NAYY 4x150 SE | 48 | 49 | 0.034712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_114-4_1_6_line_57 | NAYY 4x150 SE | 48 | 50 | 0.024447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_114-4_1_6_line_58 | NAYY 4x150 SE | 49 | 51 | 0.071827 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_114-4_1_6_line_59 | NAYY 4x150 SE | 50 | 52 | 0.053749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_114-4_1_6_line_60 | NAYY 4x150 SE | 51 | 101 | 0.018738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_114-4_1_6_line_61 | NAYY 4x150 SE | 53 | 54 | 0.0098201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_114-4_1_6_line_62 | NAYY 4x150 SE | 54 | 55 | 0.029642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_114-4_1_6_line_63 | NAYY 4x150 SE | 54 | 56 | 0.12775 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_114-4_1_6_line_64 | NAYY 4x150 SE | 55 | 57 | 0.020288 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_114-4_1_6_line_65 | NAYY 4x150 SE | 56 | 58 | 0.011969 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_114-4_1_6_line_66 | NAYY 4x150 SE | 56 | 59 | 0.023874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_114-4_1_6_line_67 | NAYY 4x150 SE | 57 | 79 | 0.030864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_114-4_1_6_line_68 | NAYY 4x150 SE | 58 | 99 | 0.019348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_114-4_1_6_line_69 | NAYY 4x150 SE | 58 | 108 | 0.0040087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_114-4_1_6_line_70 | NAYY 4x150 SE | 59 | 109 | 0.35956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_114-4_1_6_line_71 | NAYY 4x150 SE | 60 | 61 | 0.090068 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_114-4_1_6_line_72 | NAYY 4x150 SE | 61 | 62 | 0.002955 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
73 | LV_114-4_1_6_line_73 | NAYY 4x150 SE | 61 | 63 | 0.034973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_114-4_1_6_line_74 | NAYY 4x150 SE | 62 | 64 | 0.020318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
75 | LV_114-4_1_6_line_75 | NAYY 4x150 SE | 62 | 65 | 0.017027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_114-4_1_6_line_76 | NAYY 4x150 SE | 64 | 99 | 0.011014 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_114-4_1_6_line_77 | NAYY 4x150 SE | 64 | 100 | 0.057054 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_114-4_1_6_line_78 | NAYY 4x150 SE | 67 | 68 | 0.006949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_114-4_1_6_line_79 | NAYY 4x150 SE | 69 | 70 | 0.05384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_114-4_1_6_line_80 | NAYY 4x150 SE | 69 | 71 | 0.0021443 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_114-4_1_6_line_81 | NAYY 4x150 SE | 70 | 72 | 0.031776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_114-4_1_6_line_82 | NAYY 4x150 SE | 72 | 73 | 0.033477 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_114-4_1_6_line_83 | NAYY 4x150 SE | 72 | 74 | 0.02236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_114-4_1_6_line_84 | NAYY 4x150 SE | 72 | 75 | 0.016517 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_114-4_1_6_line_85 | NAYY 4x150 SE | 73 | 105 | 0.012247 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_114-4_1_6_line_86 | NAYY 4x150 SE | 75 | 104 | 0.020445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_114-4_1_6_line_87 | NAYY 4x150 SE | 77 | 78 | 0.05408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_114-4_1_6_line_88 | NAYY 4x150 SE | 77 | 79 | 0.02688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_114-4_1_6_line_89 | NAYY 4x150 SE | 79 | 80 | 0.012696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_114-4_1_6_line_90 | NAYY 4x150 SE | 82 | 83 | 0.035973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_114-4_1_6_line_91 | NAYY 4x150 SE | 83 | 84 | 0.28073 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_114-4_1_6_line_92 | NAYY 4x150 SE | 84 | 88 | 0.19778 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_114-4_1_6_line_93 | NAYY 4x150 SE | 85 | 86 | 0.18204 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_114-4_1_6_line_94 | NAYY 4x150 SE | 86 | 87 | 0.012896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_114-4_1_6_line_95 | NAYY 4x150 SE | 86 | 88 | 0.082581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_114-4_1_6_line_96 | NAYY 4x150 SE | 87 | 89 | 0.072157 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_114-4_1_6_line_97 | NAYY 4x150 SE | 89 | 92 | 0.036175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_114-4_1_6_line_98 | NAYY 4x150 SE | 89 | 90 | 0.082217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_114-4_1_6_line_99 | NAYY 4x150 SE | 90 | 91 | 0.058928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_114-4_1_6_line_100 | NAYY 4x150 SE | 92 | 93 | 0.022884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_114-4_1_6_line_101 | NAYY 4x150 SE | 93 | 94 | 0.0089715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_114-4_1_6_line_102 | NAYY 4x150 SE | 93 | 95 | 0.10324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_114-4_1_6_line_103 | NAYY 4x150 SE | 95 | 96 | 0.049373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_114-4_1_6_line_104 | NAYY 4x150 SE | 96 | 97 | 0.27543 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_114-4_1_6_line_105 | NAYY 4x150 SE | 97 | 98 | 0.029597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_114-4_1_6_line_106 | NAYY 4x150 SE | 100 | 106 | 0.0014334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_114-4_1_6_line_107 | NAYY 4x150 SE | 101 | 102 | 0.010971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_114-4_1_6_line_108 | NAYY 4x150 SE | 102 | 103 | 0.012449 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_114-4_1_6_line_109 | NAYY 4x150 SE | 105 | 106 | 0.037401 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
110 | LV_114-4_1_6_line_110 | NAYY 4x150 SE | 109 | 110 | 0.00551 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_114-4_1_6_trafo_141 | 0.25 MVA 20/0.4 kV | 112 | 28 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40
0 | 2712855.4336 | 1243940.2088 | 2712858.5804 | 1243945.9011 | 2712857.6338 | 1243953.9341 | 2712858.1132 | 1243958.1355 | 2712872.6601 | 1243971.0893 | 2712874.9489 | 1243975.9368 | 2712874.0646 | 1243980.3013 | 2712869.9695 | 1243983.3703 | 2712859.9172 | 1243986.0702 | 2712856.267 | 1243988.8029 | 2712854.3497 | 1243993.4258 | 2712856.603 | 1243998.9509 | 2712871.8334 | 1244016.0989 | 2712890.2413 | 1244052.156 | 2712897.5683 | 1244065.5396 | 2712897.6588 | 1244074.3528
1 | 2712915.466 | 1244082.0028 | 2712900.2689 | 1244079.7247 | 2712897.6848 | 1244076.8843 | 2712897.6588 | 1244074.3528
2 | 2712973.3923 | 1243877.9978 | 2712960.0902 | 1243894.1354 | 2712946.2099 | 1243904.524 | 2712932.8793 | 1243909.8635 | 2712907.8863 | 1243911.9451 | 2712896.3761 | 1243910.6139 | 2712853.1316 | 1243896.9802 | 2712846.4936 | 1243897.8213 | 2712844.9547 | 1243902.4179 | 2712850.4179 | 1243927.5533 | 2712855.0143 | 1243939.4503 | 2712855.4336 | 1243940.2088
3 | 2712855.4336 | 1243940.2088 | 2712678.6431 | 1243881.2624
4 | 2712915.466 | 1244082.0028 | 2712919.9539 | 1244082.6755
5 | 2712973.3923 | 1243877.9978 | 2712969.1104 | 1243873.5928
6 | 2713055.4141 | 1244170.4079 | 2713040.9011 | 1244161.6687 | 2713028.8603 | 1244151.3198 | 2713011.3481 | 1244129.4018 | 2713005.6857 | 1244119.9196 | 2713003.8294 | 1244110.6323 | 2713003.9674 | 1244099.4259 | 2713001.5478 | 1244086.7696 | 2712993.0807 | 1244072.5412 | 2712982.2419 | 1244063.7611 | 2712970.4173 | 1244060.2998 | 2712957.6533 | 1244062.503 | 2712943.9848 | 1244069.7264 | 2712934.2393 | 1244081.3281 | 2712929.4168 | 1244084.0941 | 2712919.9539 | 1244082.6755
7 | 2713055.4141 | 1244170.4079 | 2713066.2764 | 1244181.902 | 2713074.1399 | 1244194.0728 | 2713073.1851 | 1244200.5376 | 2713047.5353 | 1244223.6453 | 2713030.8937 | 1244245.2791 | 2713014.6891 | 1244274.9277 | 2713012.3061 | 1244284.5457 | 2713012.9926 | 1244305.6314 | 2713011.3558 | 1244332.8111 | 2713008.844 | 1244343.2384 | 2713000.6807 | 1244363.0545 | 2712998.5269 | 1244368.5847
8 | 2713055.4141 | 1244170.4079 | 2713073.2826 | 1244158.1718 | 2713090.4541 | 1244144.0432 | 2713110.1562 | 1244129.2179 | 2713143.967 | 1244107.0891 | 2713161.9861 | 1244095.301 | 2713177.6938 | 1244078.676 | 2713186.8465 | 1244063.7051 | 2713187.6474 | 1244055.0134 | 2713183.3309 | 1244048.6926 | 2713151.1457 | 1244033.9445 | 2713115.2735 | 1244007.2056 | 2713105.3701 | 1243996.1523 | 2713104.0157 | 1243983.9388 | 2713114.5611 | 1243961.3425
9 | 2713114.5611 | 1243961.3425 | 2713116.8546 | 1243956.4279 | 2713120.8208 | 1243940.3127 | 2713135.4343 | 1243917.6619 | 2713144.9953 | 1243911.4058 | 2713165.7416 | 1243905.2854 | 2713183.7885 | 1243897.6234 | 2713190.662 | 1243891.9722 | 2713201.2787 | 1243877.9412 | 2713204.2802 | 1243868.8133 | 2713202.6729 | 1243859.9532 | 2713194.9603 | 1243845.0162 | 2713183.1572 | 1243827.3434 | 2713179.3916 | 1243824.2246 | 2713179.2544 | 1243824.1045
10 | 2712998.5269 | 1244368.5847 | 2712989.6649 | 1244391.3565 | 2712958.201 | 1244442.3654 | 2712946.1667 | 1244453.1228 | 2712915.5325 | 1244472.9112 | 2712905.4185 | 1244483.2605 | 2712885.7985 | 1244517.3912
11 | 2712998.5269 | 1244368.5847 | 2713013.9325 | 1244377.2629 | 2713020.0159 | 1244382.0938 | 2713028.3331 | 1244391.471 | 2713033.904 | 1244403.7537 | 2713034.0713 | 1244407.3997
12 | 2712846.3386 | 1244632.8963 | 2712859.0553 | 1244563.788 | 2712877.0313 | 1244529.947 | 2712884.6785 | 1244519.3395 | 2712885.7985 | 1244517.3912
13 | 2713025.7373 | 1244455.0766 | 2713042.962 | 1244448.4069 | 2713046.6414 | 1244442.5501 | 2713046.3452 | 1244437.4736 | 2713035.8139 | 1244424.8961 | 2713034.3259 | 1244412.947 | 2713034.0713 | 1244407.3997
14 | 2713042.3232 | 1244772.8356 | 2713047.4959 | 1244751.2833 | 2713051.6348 | 1244738.3628 | 2713056.755 | 1244725.1163 | 2713065.5452 | 1244707.2916 | 2713073.4985 | 1244695.7005 | 2713080.4654 | 1244687.8713 | 2713088.9171 | 1244680.2707 | 2713099.1848 | 1244673.7501 | 2713111.1101 | 1244667.5057 | 2713121.6711 | 1244663.4482 | 2713134.2848 | 1244660.3418 | 2713146.0475 | 1244658.6647 | 2713160.1641 | 1244658.0001 | 2713162.0684 | 1244658.079
15 | 2712791.8168 | 1244807.5846 | 2712794.6402 | 1244808.161 | 2712797.2688 | 1244808.2444 | 2712799.5813 | 1244807.8658 | 2712802.0285 | 1244807.1562 | 2712808.4827 | 1244804.7992 | 2712812.6015 | 1244803.6322 | 2712817.5568 | 1244802.5922 | 2712823.3583 | 1244801.5684 | 2712835.9231 | 1244799.8171 | 2712847.7087 | 1244798.896 | 2712851.4011 | 1244798.6883 | 2712854.862 | 1244798.3317 | 2712858.5784 | 1244797.6574 | 2712864.1894 | 1244796.3186 | 2712868.0117 | 1244795.6352 | 2712871.0495 | 1244795.2705 | 2712873.8283 | 1244795.012 | 2712877.7133 | 1244795.0082 | 2712924.2427 | 1244796.5393 | 2712928.9123 | 1244797.0064 | 2712932.8212 | 1244797.3366 | 2712936.5935 | 1244797.2973 | 2712939.6587 | 1244797.0777 | 2712942.5064 | 1244796.7761 | 2712960.6235 | 1244793.9966 | 2712965.2439 | 1244793.473 | 2712969.2543 | 1244793.2381 | 2712973.2073 | 1244793.2356 | 2712979.1308 | 1244793.3485 | 2712991.1271 | 1244782.5682 | 2712997.2451 | 1244778.0255 | 2713002.6144 | 1244774.7028 | 2713008.0363 | 1244772.1818 | 2713013.3761 | 1244770.4043 | 2713018.8077 | 1244769.3625 | 2713023.6573 | 1244769.1103 | 2713028.8958 | 1244769.477 | 2713033.3192 | 1244770.173 | 2713038.0718 | 1244771.4423 | 2713042.3232 | 1244772.8356
16 | 2713187.2827 | 1244661.3142 | 2713180.6522 | 1244659.7257 | 2713170.1182 | 1244658.4125 | 2713162.0684 | 1244658.079
17 | 2712791.8168 | 1244807.5846 | 2712789.6436 | 1244806.9984 | 2712788.0541 | 1244806.3232 | 2712786.5088 | 1244804.9149 | 2712785.2674 | 1244803.4234 | 2712783.7347 | 1244800.9589 | 2712781.5597 | 1244793.7117 | 2712780.1362 | 1244786.3009 | 2712779.72 | 1244777.5859 | 2712780.8116 | 1244755.5666 | 2712780.2481 | 1244735.5285 | 2712781.4074 | 1244717.5026 | 2712772.337 | 1244705.2091 | 2712769.2136 | 1244691.7944 | 2712767.8152 | 1244685.4405 | 2712763.8031 | 1244682.9844 | 2712745.8451 | 1244681.364 | 2712743.2483 | 1244680.792 | 2712724.3929 | 1244673.5994
18 | 2712791.8168 | 1244807.5846 | 2712791.9948 | 1244802.9954 | 2712792.2605 | 1244800.1537 | 2712792.7491 | 1244797.1161 | 2712793.4931 | 1244793.3716 | 2712794.9859 | 1244788.0068 | 2712796.4309 | 1244783.1637 | 2712798.3323 | 1244776.9837 | 2712800.2913 | 1244771.3497 | 2712802.0009 | 1244767.3012 | 2712803.9817 | 1244763.3022 | 2712821.5646 | 1244730.2098 | 2712839.0662 | 1244672.418 | 2712846.3386 | 1244632.8963
19 | 2712407.703 | 1244538.9101 | 2712408.8096 | 1244516.4239 | 2712407.5904 | 1244508.5723 | 2712398.6225 | 1244499.9843 | 2712388.4426 | 1244487.9484 | 2712365.768 | 1244467.9472 | 2712357.1829 | 1244459.0997 | 2712345.3351 | 1244446.1204 | 2712334.407 | 1244438.4517 | 2712322.6945 | 1244431.0906 | 2712290.0529 | 1244410.1225 | 2712283.7308 | 1244409.8804 | 2712278.6571 | 1244412.3753 | 2712270.9624 | 1244421.9485 | 2712258.8336 | 1244434.5737 | 2712252.356 | 1244439.355 | 2712242.6187 | 1244440.6496 | 2712239.3462 | 1244440.5793
20 | 2712407.703 | 1244538.9101 | 2712416.8309 | 1244542.6416 | 2712423.3594 | 1244538.508
21 | 2712407.703 | 1244538.9101 | 2712401.9633 | 1244539.057 | 2712391.2029 | 1244543.1326
22 | 2712443.0665 | 1244524.7131 | 2712438.7828 | 1244526.6002 | 2712425.3229 | 1244537.2648 | 2712423.3594 | 1244538.508
23 | 2712348.9384 | 1244579.0405 | 2712359.6562 | 1244553.9232 | 2712366.5117 | 1244549.9387 | 2712376.3526 | 1244548.7574 | 2712391.2029 | 1244543.1326
24 | 2712443.027 | 1244575.409 | 2712442.2812 | 1244570.8912 | 2712448.9526 | 1244537.5684 | 2712448.0199 | 1244527.7651 | 2712443.0665 | 1244524.7131
25 | 2712348.9384 | 1244579.0405 | 2712337.0396 | 1244575.5457 | 2712324.8942 | 1244571.5013 | 2712312.423 | 1244571.4874 | 2712297.8004 | 1244572.9229 | 2712275.5213 | 1244573.9465 | 2712240.9868 | 1244575.5388 | 2712214.4784 | 1244580.7749 | 2712191.7853 | 1244581.7131 | 2712172.8216 | 1244583.2892 | 2712154.0701 | 1244589.2283 | 2712141.8439 | 1244598.2378 | 2712130.1822 | 1244612.1731
26 | 2712553.1838 | 1244387.9239 | 2712541.8502 | 1244393.658 | 2712534.8829 | 1244395.9499 | 2712529.8589 | 1244393.4303 | 2712527.329 | 1244389.3863
27 | 2712532.6354 | 1244352.6834 | 2712546.0256 | 1244375.1889 | 2712553.1838 | 1244387.9239
28 | 2712553.1838 | 1244387.9239 | 2712566.9043 | 1244380.6783 | 2712584.2494 | 1244384.7774 | 2712594.9764 | 1244401.7193
29 | 2712532.6354 | 1244352.6834 | 2712527.9159 | 1244355.6185 | 2712523.8006 | 1244357.7866 | 2712515.3068 | 1244359.6604 | 2712512.287 | 1244359.7599
30 | 2712532.6354 | 1244352.6834 | 2712519.5266 | 1244332.8743 | 2712503.5351 | 1244311.6094 | 2712489.5869 | 1244294.5979 | 2712478.9095 | 1244283.8412
31 | 2712595.2796 | 1244424.6783 | 2712605.4725 | 1244418.2962 | 2712594.9764 | 1244401.7193
32 | 2712579.6856 | 1244434.4421 | 2712600.5111 | 1244470.978 | 2712608.5672 | 1244466.6719
33 | 2712579.6856 | 1244434.4421 | 2712595.2796 | 1244424.6783
34 | 2712608.5672 | 1244466.6719 | 2712630.2784 | 1244505.9046 | 2712633.5422 | 1244507.1787 | 2712646.9802 | 1244499.5101
35 | 2712608.5672 | 1244466.6719 | 2712621.9046 | 1244490.7729
36 | 2712608.5672 | 1244466.6719 | 2712600.5111 | 1244470.978 | 2712607.9431 | 1244484.0074 | 2712632.1643 | 1244526.7907 | 2712633.2082 | 1244528.7343
37 | 2712503.9011 | 1244358.0428 | 2712506.9567 | 1244359.9356 | 2712512.287 | 1244359.7599
38 | 2712437.1644 | 1244247.4412 | 2712446.0352 | 1244255.0292 | 2712456.7597 | 1244263.8729 | 2712473.4993 | 1244278.3909 | 2712478.9095 | 1244283.8412
39 | 2712633.2082 | 1244528.7343 | 2712615.482 | 1244539.1076
40 | 2712520.364 | 1244548.3978 | 2712524.6233 | 1244551.381 | 2712529.636 | 1244558.871 | 2712538.1926 | 1244566.4172 | 2712542.1512 | 1244569.7061 | 2712543.0088 | 1244575.4937 | 2712544.0859 | 1244578.0829 | 2712546.4915 | 1244578.7735 | 2712549.4248 | 1244576.7498 | 2712553.9415 | 1244568.1619 | 2712555.7189 | 1244567.7063 | 2712557.7873 | 1244569.0355 | 2712560.0498 | 1244577.2629 | 2712561.525 | 1244584.3633 | 2712563.6088 | 1244584.881 | 2712565.7628 | 1244581.7082 | 2712567.4452 | 1244577.8926 | 2712568.5435 | 1244579.3591 | 2712570.9951 | 1244585.9887 | 2712573.174 | 1244587.0754 | 2712575.7502 | 1244583.5548 | 2712577.4811 | 1244579.5733 | 2712579.9896 | 1244579.6209 | 2712582.5097 | 1244583.0382 | 2712584.141 | 1244591.8652 | 2712585.5283 | 1244594.0377 | 2712588.1029 | 1244594.587 | 2712590.1752 | 1244591.3348 | 2712591.9201 | 1244582.6386 | 2712593.4376 | 1244567.2105 | 2712595.731 | 1244559.8814 | 2712601.0447 | 1244551.52 | 2712609.0242 | 1244542.8867 | 2712615.482 | 1244539.1076
41 | 2712643.515 | 1244558.3317 | 2712639.4734 | 1244543.0982 | 2712635.9237 | 1244534.2014 | 2712633.2082 | 1244528.7343
42 | 2712443.027 | 1244575.409 | 2712454.9149 | 1244571.5089 | 2712467.6178 | 1244567.2796 | 2712491.0221 | 1244570.6928 | 2712502.2052 | 1244573.6628 | 2712510.1359 | 1244574.3582 | 2712516.2094 | 1244572.95 | 2712519.9102 | 1244569.5174 | 2712521.698 | 1244561.3447 | 2712520.364 | 1244548.3978
43 | 2712643.515 | 1244558.3317 | 2712643.7331 | 1244561.4372
44 | 2712643.515 | 1244558.3317 | 2712655.4959 | 1244557.1026
45 | 2712644.7018 | 1244581.5761 | 2712644.6512 | 1244574.5108 | 2712643.7331 | 1244561.4372
46 | 2712655.4959 | 1244557.1026 | 2712663.5835 | 1244555.9108
47 | 2712655.4959 | 1244557.1026 | 2712652.2595 | 1244544.8424 | 2712646.4644 | 1244529.6089 | 2712662.4591 | 1244521.1397
48 | 2712412.4287 | 1244236.2772 | 2712405.5247 | 1244245.9876
49 | 2712412.4287 | 1244236.2772 | 2712429.7659 | 1244268.1718
50 | 2712419.6244 | 1244229.9195 | 2712412.4287 | 1244236.2772
51 | 2712419.6244 | 1244229.9195 | 2712427.5289 | 1244239.199 | 2712437.1644 | 1244247.4412
52 | 2712411.2556 | 1244218.018 | 2712415.313 | 1244224.489 | 2712419.6244 | 1244229.9195
53 | 2712378.9409 | 1244116.7463 | 2712382.7996 | 1244130.1191 | 2712390.859 | 1244157.9498 | 2712403.2289 | 1244200.0292 | 2712406.405 | 1244208.3294 | 2712410.4453 | 1244216.5014 | 2712410.8833 | 1244217.3215 | 2712411.2556 | 1244218.018
54 | 2712411.2556 | 1244218.018 | 2712408.3457 | 1244219.5975 | 2712403.8865 | 1244219.5685 | 2712399.0897 | 1244217.8096 | 2712387.7755 | 1244212.5466 | 2712378.5207 | 1244208.3012 | 2712374.7742 | 1244208.5587
55 | 2712412.3907 | 1244107.1277 | 2712406.0109 | 1244092.3727 | 2712399.7186 | 1244073.1431
56 | 2712378.9409 | 1244116.7463 | 2712382.8487 | 1244115.5638 | 2712412.3907 | 1244107.1277
57 | 2712412.3907 | 1244107.1277 | 2712423.6737 | 1244128.8156
58 | 2712378.9409 | 1244116.7463 | 2712362.9839 | 1244061.6996 | 2712358.9053 | 1244047.7708
59 | 2712430.4471 | 1244172.2113 | 2712442.1081 | 1244163.1806 | 2712432.9867 | 1244146.7166 | 2712423.6737 | 1244128.8156
60 | 2712353.4432 | 1244029.8488 | 2712355.4725 | 1244036.0478 | 2712358.9053 | 1244047.7708
61 | 2712658.4799 | 1244789.0471 | 2712668.2099 | 1244787.7197
62 | 2712658.4799 | 1244789.0471 | 2712661.9268 | 1244810.1074 | 2712663.227 | 1244818.0497 | 2712663.2706 | 1244818.2999
63 | 2712658.4799 | 1244789.0471 | 2712655.4792 | 1244769.5633 | 2712654.459 | 1244762.794 | 2712653.6315 | 1244757.8187 | 2712646.0729 | 1244712.8943 | 2712642.4895 | 1244684.6923 | 2712641.8976 | 1244662.5409
64 | 2712663.2706 | 1244818.2999 | 2712666.7566 | 1244838.2857
65 | 2712641.8976 | 1244662.5409 | 2712642.4347 | 1244650.5859
66 | 2712641.8976 | 1244662.5409 | 2712635.5593 | 1244662.376 | 2712618.3918 | 1244665.9384
67 | 2712672.6287 | 1244868.5803 | 2712669.32 | 1244852.9826 | 2712666.7566 | 1244838.2857
68 | 2712642.4347 | 1244650.5859 | 2712651.3673 | 1244651.0559 | 2712661.7455 | 1244650.3307
69 | 2712642.4347 | 1244650.5859 | 2712642.632 | 1244646.5821
70 | 2712500.1961 | 1244778.6906 | 2712518.3271 | 1244792.2899 | 2712521.3979 | 1244796.9519 | 2712530.6057 | 1244819.1446 | 2712536.5636 | 1244833.3691 | 2712543.4456 | 1244849.079 | 2712544.6326 | 1244852.6378 | 2712544.0047 | 1244857.0517 | 2712540.9913 | 1244860.9087 | 2712533.9673 | 1244867.4141 | 2712532.4322 | 1244869.8425 | 2712531.7819 | 1244872.6435 | 2712534.3628 | 1244874.0492 | 2712543.5102 | 1244873.1442 | 2712553.9477 | 1244869.1723 | 2712560.3113 | 1244866.4019 | 2712564.2427 | 1244861.9618 | 2712565.868 | 1244855.9767 | 2712566.0366 | 1244841.9241 | 2712567.1978 | 1244831.3264 | 2712571.8098 | 1244816.9134 | 2712576.3142 | 1244799.418 | 2712582.1754 | 1244784.1057 | 2712587.6184 | 1244777.6816 | 2712591.7866 | 1244768.342 | 2712599.2864 | 1244747.145 | 2712610.3395 | 1244725.5039 | 2712613.2671 | 1244712.6379 | 2712609.6425 | 1244678.6416 | 2712610.353 | 1244673.0728 | 2712613.1484 | 1244668.7557 | 2712616.9528 | 1244666.237 | 2712618.3918 | 1244665.9384
71 | 2712694.8685 | 1244655.2855 | 2712700.7359 | 1244666.3059 | 2712712.0017 | 1244678.4297 | 2712716.7825 | 1244681.801 | 2712744.0812 | 1244689.4593 | 2712743.3364 | 1244716.2798
72 | 2712692.9461 | 1244653.036 | 2712694.8685 | 1244655.2855
73 | 2712694.8685 | 1244655.2855 | 2712709.0663 | 1244666.253 | 2712718.3353 | 1244671.2887 | 2712724.3929 | 1244673.5994
74 | 2712692.9461 | 1244653.036 | 2712689.6549 | 1244652.4174 | 2712681.3266 | 1244651.1694 | 2712677.3515 | 1244650.738 | 2712672.7548 | 1244650.4059
75 | 2712692.9461 | 1244653.036 | 2712699.6894 | 1244647.404 | 2712697.1839 | 1244639.5529
76 | 2712672.7548 | 1244650.4059 | 2712663.1286 | 1244650.2341 | 2712661.7455 | 1244650.3307
77 | 2712672.7548 | 1244650.4059 | 2712675.3705 | 1244613.7926 | 2712674.9127 | 1244605.6663 | 2712672.4399 | 1244593.7116
78 | 2712433.0846 | 1244274.2771 | 2712429.7659 | 1244268.1718
79 | 2712730.7492 | 1244521.6812 | 2712737.8296 | 1244513.4424 | 2712743.3282 | 1244500.9368 | 2712748.7959 | 1244482.9038 | 2712751.8348 | 1244472.8823
80 | 2712752.4571 | 1244470.8303 | 2712751.8348 | 1244472.8823
81 | 2712707.3693 | 1244543.2211 | 2712719.9507 | 1244532.2735 | 2712728.1058 | 1244524.7557 | 2712730.7492 | 1244521.6812
82 | 2712707.3693 | 1244543.2211 | 2712698.0615 | 1244547.3699 | 2712685.2895 | 1244550.0516 | 2712675.4069 | 1244552.7193
83 | 2712707.3693 | 1244543.2211 | 2712701.4576 | 1244537.7043 | 2712698.7095 | 1244533.1595 | 2712694.0668 | 1244525.4925
84 | 2712707.3693 | 1244543.2211 | 2712716.8557 | 1244556.7421
85 | 2712663.5835 | 1244555.9108 | 2712675.4069 | 1244552.7193
86 | 2712716.8557 | 1244556.7421 | 2712723.8168 | 1244566.6637 | 2712730.7638 | 1244562.0768
87 | 2712661.4141 | 1244884.4023 | 2712660.0102 | 1244878.7378 | 2712659.3768 | 1244875.4786 | 2712659.5187 | 1244871.9896 | 2712660.2326 | 1244862.262 | 2712660.0586 | 1244861.0799 | 2712659.6988 | 1244860.1279 | 2712658.9305 | 1244859.1903 | 2712657.8911 | 1244858.6034 | 2712656.7404 | 1244858.3036 | 2712655.6606 | 1244858.2497 | 2712654.4389 | 1244858.5045 | 2712653.4709 | 1244858.9309 | 2712652.6717 | 1244859.6274 | 2712646.9491 | 1244866.0461 | 2712645.505 | 1244867.2641 | 2712643.6283 | 1244868.1848 | 2712641.5184 | 1244868.6451 | 2712634.8149 | 1244869.4073
88 | 2712661.4141 | 1244884.4023 | 2712670.9166 | 1244881.9141 | 2712675.4619 | 1244880.566 | 2712672.6287 | 1244868.5803
89 | 2712672.6287 | 1244868.5803 | 2712681.0285 | 1244862.079 | 2712681.8518 | 1244861.7054 | 2712683.0112 | 1244861.5496
90 | 2711982.7755 | 1245099.5248 | 2711985.788 | 1245100.9741 | 2712000.9619 | 1245107.0878 | 2712014.4674 | 1245108.6996 | 2712017.1202 | 1245108.4
91 | 2712196.2332 | 1244892.2374 | 2712017.1202 | 1245108.4
92 | 2712196.2332 | 1244892.2374 | 2712195.1459 | 1244892.5502 | 2712177.4056 | 1244895.8285 | 2712154.6968 | 1244893.6641 | 2712136.7815 | 1244891.0121 | 2712131.0219 | 1244889.035 | 2712131.1996 | 1244879.6419 | 2712139.7404 | 1244872.4419 | 2712183.4957 | 1244834.4162 | 2712209.6383 | 1244813.705 | 2712216.0828 | 1244807.4552 | 2712226.1685 | 1244803.7881
93 | 2712219.1319 | 1244756.9832 | 2712245.5883 | 1244755.2489 | 2712263.0533 | 1244755.7576 | 2712280.2833 | 1244757.4962 | 2712289.2589 | 1244760.0792 | 2712303.9691 | 1244767.5637 | 2712316.6013 | 1244779.001 | 2712322.625 | 1244790.9803 | 2712326.1308 | 1244804.2018 | 2712328.2786 | 1244810.9146 | 2712331.6954 | 1244814.0819 | 2712339.582 | 1244817.4895 | 2712350.9961 | 1244821.8092 | 2712360.8297 | 1244827.3666 | 2712366.1948 | 1244831.8162
94 | 2712219.1319 | 1244756.9832 | 2712206.3238 | 1244758.4857
95 | 2712219.1319 | 1244756.9832 | 2712223.9821 | 1244761.89 | 2712242.0301 | 1244772.7179 | 2712251.8389 | 1244779.9983 | 2712254.5965 | 1244786.0443 | 2712253.4555 | 1244791.2158 | 2712249.1355 | 1244795.4374 | 2712226.1685 | 1244803.7881
96 | 2712140.1873 | 1244741.3444 | 2712157.4881 | 1244754.5266 | 2712169.259 | 1244760.3761 | 2712188.1261 | 1244761.0778 | 2712205.3377 | 1244758.6013 | 2712206.3238 | 1244758.4857
97 | 2712140.1873 | 1244741.3444 | 2712136.8721 | 1244745.9855 | 2712133.4669 | 1244746.1991 | 2712122.4796 | 1244742.077 | 2712111.9728 | 1244740.5216 | 2712107.3723 | 1244741.5009
98 | 2712140.1873 | 1244741.3444 | 2712140.2302 | 1244721.8962 | 2712143.4719 | 1244712.3497 | 2712159.1809 | 1244679.8426 | 2712159.7768 | 1244671.5138 | 2712157.4613 | 1244663.6637 | 2712157.4416 | 1244663.6197
99 | 2712130.1822 | 1244612.1731 | 2712130.2746 | 1244617.279 | 2712147.0313 | 1244643.6615 | 2712152.0516 | 1244651.5739 | 2712157.4416 | 1244663.6197
100 | 2712086.1412 | 1244749.5853 | 2712098.8746 | 1244743.3097 | 2712107.3723 | 1244741.5009
101 | 2712086.1412 | 1244749.5853 | 2712086.4025 | 1244758.553
102 | 2712086.1412 | 1244749.5853 | 2712078.778 | 1244753.6606 | 2712059.9214 | 1244759.1977 | 2712023.5322 | 1244769.8079 | 2712015.2801 | 1244770.1301 | 2712004.7192 | 1244767.4397 | 2711987.1648 | 1244762.9768
103 | 2711940.1488 | 1244771.8801 | 2711963.7655 | 1244762.4181 | 2711976.3685 | 1244760.232 | 2711987.1648 | 1244762.9768
104 | 2711940.1488 | 1244771.8801 | 2711920.0667 | 1244783.088 | 2711901.3719 | 1244797.2802 | 2711892.4319 | 1244801.6151 | 2711887.2886 | 1244801.0176 | 2711882.5993 | 1244797.5819 | 2711881.6983 | 1244793.2614 | 2711886.8542 | 1244779.1806 | 2711891.4769 | 1244772.9294 | 2711900.3334 | 1244763.411 | 2711907.0684 | 1244745.7571 | 2711909.8149 | 1244739.2037 | 2711911.0871 | 1244732.2665 | 2711909.401 | 1244727.0972 | 2711904.128 | 1244723.3502 | 2711896.0039 | 1244721.6957 | 2711879.2251 | 1244721.6681 | 2711858.7296 | 1244724.7396 | 2711830.0628 | 1244723.4537 | 2711798.4481 | 1244719.766 | 2711782.2208 | 1244716.4198
105 | 2711755.8294 | 1244720.9249 | 2711762.4095 | 1244723.4233 | 2711765.8938 | 1244721.0203 | 2711775.0029 | 1244714.9314 | 2711782.2208 | 1244716.4198
106 | 2712672.4399 | 1244593.7116 | 2712672.1496 | 1244592.3079
107 | 2712353.4432 | 1244029.8488 | 2712342.4991 | 1244030.6149
108 | 2712335.1997 | 1244024.6818 | 2712336.5564 | 1244031.03 | 2712342.0667 | 1244030.6452 | 2712342.4991 | 1244030.6149
109 | 2712663.5835 | 1244555.9108 | 2712669.0841 | 1244577.4883 | 2712672.1496 | 1244592.3079
110 | 2712496.3253 | 1244774.7585 | 2712500.1961 | 1244778.6906

## bus_geodata
| x | y | coords
0 | 2712897.6588 | 1244074.3528
1 | 2712855.4336 | 1243940.2088
2 | 2712915.466 | 1244082.0028
3 | 2712973.3923 | 1243877.9978
4 | 2712678.6431 | 1243881.2624
5 | 2712919.9539 | 1244082.6755
6 | 2712969.1104 | 1243873.5928
7 | 2713055.4141 | 1244170.4079
8 | 2713114.5611 | 1243961.3425
9 | 2713179.2544 | 1243824.1045
10 | 2712998.5269 | 1244368.5847
11 | 2712885.7985 | 1244517.3912
12 | 2713034.0713 | 1244407.3997
13 | 2713042.3232 | 1244772.8356
14 | 2713162.0684 | 1244658.079
15 | 2712791.8168 | 1244807.5846
16 | 2713187.2827 | 1244661.3142
17 | 2712239.3462 | 1244440.5793
18 | 2712407.703 | 1244538.9101
19 | 2712423.3594 | 1244538.508
20 | 2712391.2029 | 1244543.1326
21 | 2712443.0665 | 1244524.7132
22 | 2712348.9384 | 1244579.0405
23 | 2712527.329 | 1244389.3863
24 | 2712553.1838 | 1244387.9239
25 | 2712532.6354 | 1244352.6834
26 | 2712594.9764 | 1244401.7193
27 | 2712579.6856 | 1244434.4421
28 | 2712608.5672 | 1244466.6719
29 | 2712595.2796 | 1244424.6783
30 | 2712512.287 | 1244359.7599
31 | 2712478.9095 | 1244283.8412
32 | 2712615.482 | 1244539.1076
33 | 2712633.2082 | 1244528.7343
34 | 2712520.364 | 1244548.3978
35 | 2712643.515 | 1244558.3317
36 | 2712443.027 | 1244575.409
37 | 2712643.7331 | 1244561.4372
38 | 2712655.4959 | 1244557.1026
39 | 2712646.9802 | 1244499.5101
40 | 2712621.9046 | 1244490.7729
41 | 2712405.5247 | 1244245.9876
42 | 2712412.4287 | 1244236.2772
43 | 2712437.1644 | 1244247.4412
44 | 2712419.6244 | 1244229.9195
45 | 2712411.2556 | 1244218.018
46 | 2712503.9011 | 1244358.0428
47 | 2712399.7186 | 1244073.1431
48 | 2712412.3907 | 1244107.1277
49 | 2712378.9409 | 1244116.7463
50 | 2712423.6737 | 1244128.8156
51 | 2712358.9053 | 1244047.7708
52 | 2712430.4471 | 1244172.2113
53 | 2712668.2099 | 1244787.7197
54 | 2712658.4799 | 1244789.0471
55 | 2712663.2706 | 1244818.2999
56 | 2712641.8976 | 1244662.5409
57 | 2712666.7566 | 1244838.2857
58 | 2712642.4347 | 1244650.5859
59 | 2712618.3918 | 1244665.9384
60 | 2712743.3364 | 1244716.2798
61 | 2712694.8685 | 1244655.2855
62 | 2712692.9461 | 1244653.036
63 | 2712724.3929 | 1244673.5994
64 | 2712672.7548 | 1244650.4059
65 | 2712697.1839 | 1244639.5529
66 | 2712374.7742 | 1244208.5587
67 | 2712429.7659 | 1244268.1718
68 | 2712433.0846 | 1244274.2771
69 | 2712751.8348 | 1244472.8823
70 | 2712730.7493 | 1244521.6812
71 | 2712752.4571 | 1244470.8303
72 | 2712707.3693 | 1244543.2211
73 | 2712675.4069 | 1244552.7193
74 | 2712694.0668 | 1244525.4925
75 | 2712716.8557 | 1244556.7421
76 | 2712846.3386 | 1244632.8963
77 | 2712661.4141 | 1244884.4023
78 | 2712634.8149 | 1244869.4073
79 | 2712672.6287 | 1244868.5803
80 | 2712683.0112 | 1244861.5496
81 | 2713025.7373 | 1244455.0766
82 | 2711982.7755 | 1245099.5248
83 | 2712017.1202 | 1245108.4
84 | 2712196.2332 | 1244892.2374
85 | 2712366.1948 | 1244831.8162
86 | 2712219.1319 | 1244756.9832
87 | 2712206.3238 | 1244758.4857
88 | 2712226.1685 | 1244803.7881
89 | 2712140.1873 | 1244741.3444
90 | 2712157.4416 | 1244663.6197
91 | 2712130.1822 | 1244612.1731
92 | 2712107.3723 | 1244741.5009
93 | 2712086.1412 | 1244749.5853
94 | 2712086.4025 | 1244758.553
95 | 2711987.1648 | 1244762.9768
96 | 2711940.1488 | 1244771.8801
97 | 2711782.2208 | 1244716.4198
98 | 2711755.8294 | 1244720.9249
99 | 2712661.7455 | 1244650.3307
100 | 2712672.4399 | 1244593.7116
101 | 2712353.4432 | 1244029.8488
102 | 2712342.4991 | 1244030.6149
103 | 2712335.1997 | 1244024.6818
104 | 2712730.7638 | 1244562.0768
105 | 2712663.5835 | 1244555.9108
106 | 2712672.1496 | 1244592.3079
107 | 2712644.7018 | 1244581.5761
108 | 2712642.632 | 1244646.5821
109 | 2712500.1961 | 1244778.6906
110 | 2712496.3253 | 1244774.7585
111 | 2712662.4591 | 1244521.1397
112 | 2712600.5111 | 1244470.978

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97455 | -0.18046 | 0.0010452 | 0.00026194
1 | 0.97214 | -0.19787 | 0.001114 | 0.00027921
2 | 0.9749 | -0.17796 | 0.0028756 | 0.00072069
3 | 0.97172 | -0.20089 | 0 | 0
4 | 0.97016 | -0.21214 | 0.0072283 | 0.0018116
5 | 0.97499 | -0.1773 | 0.00026007 | 6.518e-05
6 | 0.97171 | -0.20099 | 0.0015319 | 0.00038393
7 | 0.97713 | -0.16198 | 0 | 0
8 | 0.97629 | -0.16809 | 0.0012641 | 0.00031682
9 | 0.97614 | -0.16916 | 0.00053137 | 0.00013317
10 | 0.9789 | -0.14924 | 0 | 0
11 | 0.98129 | -0.13207 | 0.0032069 | 0.00080373
12 | 0.9781 | -0.15493 | 0.0020897 | 0.00052373
13 | 0.98453 | -0.10898 | 0 | 0
14 | 0.98369 | -0.11501 | 0.001001 | 0.00025088
15 | 0.98573 | -0.1004 | 0 | 0
16 | 0.98361 | -0.11558 | 0.0021724 | 0.00054446
17 | 0.98788 | -0.085717 | 0.0014624 | 0.00036652
18 | 0.9884 | -0.081985 | 0 | 0
19 | 0.98871 | -0.079782 | 0.00039627 | 9.9314e-05
20 | 0.98813 | -0.083883 | 0.0015067 | 0.0003776
21 | 0.98914 | -0.076659 | 0.0005419 | 0.00013581
22 | 0.98733 | -0.089666 | 0 | 0
23 | 0.98858 | -0.079415 | 0.0035282 | 0.00088425
24 | 0.98874 | -0.078319 | 0 | 0
25 | 0.98604 | -0.097302 | 0 | 0
26 | 0.99254 | -0.0517 | 0.0012993 | 0.00032565
27 | 0.99621 | -0.026155 | 0 | 0
28 | 1 | 0 | -0.1636 | -0.041031
29 | 0.99485 | -0.035603 | 0.00066946 | 0.00016778
30 | 0.98578 | -0.09913 | 0.0026933 | 0.000675
31 | 0.98128 | -0.13103 | 0.010872 | 0.0027247
32 | 0.99568 | -0.030148 | 0.00042296 | 0.000106
33 | 0.99608 | -0.027325 | 0 | 0
34 | 0.99208 | -0.055733 | 0 | 0
35 | 0.99465 | -0.037319 | 0 | 0
36 | 0.99016 | -0.069362 | 0 | 0
37 | 0.99465 | -0.037341 | 0.00057131 | 0.00014318
38 | 0.99411 | -0.041116 | 0 | 0
39 | 0.99998 | -0.00016865 | 0.00026167 | 6.558e-05
40 | 0.99994 | -0.00039786 | 0.0014458 | 0.00036236
41 | 0.97807 | -0.15401 | 0.001705 | 0.00042731
42 | 0.9781 | -0.1538 | 0 | 0
43 | 0.97915 | -0.14627 | 0.0019941 | 0.00049977
44 | 0.97826 | -0.15261 | 0 | 0
45 | 0.97799 | -0.15453 | 0 | 0
46 | 0.98571 | -0.099627 | 0.0054232 | 0.0013592
47 | 0.97556 | -0.17201 | 0.0042328 | 0.0010608
48 | 0.97578 | -0.1704 | 0 | 0
49 | 0.97619 | -0.16749 | 0 | 0
50 | 0.97565 | -0.17137 | 0.0014444 | 0.00036201
51 | 0.97581 | -0.17021 | 0.00063353 | 0.00015878
52 | 0.97546 | -0.17268 | 0.0023208 | 0.00058164
53 | 0.98607 | -0.097914 | 0.0063577 | 0.0015934
54 | 0.98616 | -0.097273 | 0 | 0
55 | 0.98591 | -0.099118 | 0.0031199 | 0.00078192
56 | 0.98846 | -0.081018 | 0 | 0
57 | 0.98582 | -0.09973 | 0.00076062 | 0.00019063
58 | 0.98876 | -0.078882 | 0 | 0
59 | 0.98828 | -0.082247 | 0.0038917 | 0.00097534
60 | 0.98657 | -0.094364 | 0.019969 | 0.0050046
61 | 0.98917 | -0.075966 | 0 | 0
62 | 0.98925 | -0.075406 | 0 | 0
63 | 0.98857 | -0.08022 | 0.0021435 | 0.00053721
64 | 0.98981 | -0.071427 | 0 | 0
65 | 0.9892 | -0.075738 | 0.0019075 | 0.00047807
66 | 0.97794 | -0.15493 | 0.00097865 | 0.00024527
67 | 0.97756 | -0.15764 | 0.0027773 | 0.00069606
68 | 0.97748 | -0.15818 | 0.0073672 | 0.0018464
69 | 0.99329 | -0.046884 | 0.00012204 | 3.0586e-05
70 | 0.99334 | -0.046563 | 0 | 0
71 | 0.99329 | -0.046894 | 0.00046448 | 0.00011641
72 | 0.99337 | -0.046373 | 0 | 0
73 | 0.99364 | -0.044452 | 0.00069792 | 0.00017492
74 | 0.99335 | -0.046497 | 0.00054944 | 0.0001377
75 | 0.99326 | -0.047128 | 0.00061401 | 0.00015388
76 | 0.98304 | -0.11958 | 0.0010335 | 0.00025901
77 | 0.98568 | -0.10072 | 0 | 0
78 | 0.98559 | -0.10133 | 0.0010951 | 0.00027445
79 | 0.98572 | -0.10042 | 0 | 0
80 | 0.9857 | -0.10056 | 0.0010714 | 0.00026852
81 | 0.97737 | -0.16018 | 0.0077992 | 0.0019547
82 | 0.97948 | -0.14625 | 0.00081279 | 0.0002037
83 | 0.97952 | -0.14595 | 0.0016944 | 0.00042466
84 | 0.98054 | -0.13858 | 0.0004587 | 0.00011496
85 | 0.98175 | -0.12984 | 0.00039904 | 0.00010001
86 | 0.98186 | -0.12907 | 0 | 0
87 | 0.98194 | -0.12849 | 0.00093779 | 0.00023503
88 | 0.9814 | -0.13242 | 0.0008943 | 0.00022413
89 | 0.98248 | -0.12456 | 0 | 0
90 | 0.98351 | -0.11716 | 0.00052016 | 0.00013036
91 | 0.98429 | -0.11155 | 0 | 0
92 | 0.98231 | -0.12584 | 0.00045728 | 0.0001146
93 | 0.98221 | -0.12654 | 0 | 0
94 | 0.9822 | -0.12661 | 0.00079073 | 0.00019818
95 | 0.98189 | -0.12885 | 0.00024349 | 6.1025e-05
96 | 0.98176 | -0.12983 | 0 | 0
97 | 0.981 | -0.13526 | 0.001165 | 0.00029197
98 | 0.98097 | -0.13548 | 0.00071972 | 0.00018038
99 | 0.98937 | -0.074504 | 0.0052329 | 0.0013115
100 | 0.99214 | -0.054984 | 0.00012464 | 3.1237e-05
101 | 0.97573 | -0.1708 | 0 | 0
102 | 0.97568 | -0.17114 | 0.0013392 | 0.00033563
103 | 0.97565 | -0.17135 | 0.0016389 | 0.00041074
104 | 0.99314 | -0.047937 | 0.0039069 | 0.00097915
105 | 0.99375 | -0.043664 | 0 | 0
106 | 0.9922 | -0.054572 | 0.0012298 | 0.00030821
107 | 0.99465 | -0.037368 | 0.0001319 | 3.3057e-05
108 | 0.98873 | -0.079074 | 0.004698 | 0.0011774
109 | 0.98771 | -0.086407 | 0 | 0
110 | 0.9877 | -0.08647 | 0.0011137 | 0.00027913
111 | 0.99404 | -0.04166 | 0.0011419 | 0.00028619
112 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.009913 | 0.0024829 | -0.0098892 | -0.0024758 | 2.3825e-05 | 7.0918e-06 | 0.015135 | 0.015136 | 0.015136 | 0.97455 | -0.18046 | 0.97214 | -0.19787 | 5.6059
1 | -0.010958 | -0.0027448 | 0.010962 | 0.002746 | 3.7972e-06 | 1.1895e-06 | 0.016731 | 0.016731 | 0.016731 | 0.97455 | -0.18046 | 0.9749 | -0.17796 | 6.1967
2 | 0.0015325 | 0.00038181 | -0.0015319 | -0.00038386 | 6.3675e-07 | -2.054e-06 | 0.002345 | 0.0023458 | 0.0023458 | 0.97214 | -0.19787 | 0.97172 | -0.20089 | 0.86882
3 | 0.0072426 | 0.0018148 | -0.0072283 | -0.0018116 | 1.4292e-05 | 3.1912e-06 | 0.011086 | 0.011087 | 0.011087 | 0.97214 | -0.19787 | 0.97016 | -0.21214 | 4.1062
4 | -0.013838 | -0.0034667 | 0.013839 | 0.0034671 | 1.2631e-06 | 4.2922e-07 | 0.02112 | 0.02112 | 0.02112 | 0.9749 | -0.17796 | 0.97499 | -0.1773 | 7.8223
5 | 0.0015319 | 0.00038386 | -0.0015319 | -0.00038393 | 2.1095e-08 | -6.7986e-08 | 0.0023458 | 0.0023458 | 0.0023458 | 0.97172 | -0.20089 | 0.97171 | -0.20099 | 0.86883
6 | -0.014099 | -0.0035323 | 0.014129 | 0.0035386 | 2.9899e-05 | 6.325e-06 | 0.021517 | 0.021515 | 0.021517 | 0.97499 | -0.1773 | 0.97713 | -0.16198 | 3.9846
7 | -0.015926 | -0.0039828 | 0.015954 | 0.003985 | 2.7962e-05 | 2.1472e-06 | 0.02425 | 0.024246 | 0.02425 | 0.97713 | -0.16198 | 0.9789 | -0.14924 | 2.9938
8 | 0.0017971 | 0.00044422 | -0.0017956 | -0.00044765 | 1.4915e-06 | -3.425e-06 | 0.0027345 | 0.0027359 | 0.0027359 | 0.97713 | -0.16198 | 0.97629 | -0.16809 | 1.0133
9 | 0.00053144 | 0.00013083 | -0.00053137 | -0.00013317 | 7.7657e-08 | -2.3441e-06 | 0.00080916 | 0.00081001 | 0.00081001 | 0.97629 | -0.16809 | 0.97614 | -0.16916 | 0.3
10 | -0.025856 | -0.0064671 | 0.025917 | 0.0064834 | 6.1295e-05 | 1.6361e-05 | 0.039299 | 0.039297 | 0.039299 | 0.9789 | -0.14924 | 0.98129 | -0.13207 | 4.8518
11 | 0.0099024 | 0.0024821 | -0.0098946 | -0.0024798 | 7.7937e-06 | 2.3052e-06 | 0.015053 | 0.015053 | 0.015053 | 0.9789 | -0.14924 | 0.9781 | -0.15493 | 5.5752
12 | -0.029124 | -0.0072872 | 0.029175 | 0.0073018 | 5.0258e-05 | 1.4626e-05 | 0.04416 | 0.044158 | 0.04416 | 0.98129 | -0.13207 | 0.98304 | -0.11958 | 5.4518
13 | 0.0078049 | 0.001956 | -0.0077992 | -0.0019547 | 5.6721e-06 | 1.373e-06 | 0.011874 | 0.011874 | 0.011874 | 0.9781 | -0.15493 | 0.97737 | -0.16018 | 4.3978
14 | 0.0031763 | 0.00079377 | -0.0031736 | -0.00079509 | 2.6393e-06 | -1.3171e-06 | 0.0047998 | 0.0048006 | 0.0048006 | 0.98453 | -0.10898 | 0.98369 | -0.11501 | 1.778
15 | -0.0031763 | -0.00079377 | 0.00318 | 0.00079189 | 3.7409e-06 | -1.8752e-06 | 0.0047998 | 0.0047986 | 0.0047998 | 0.98453 | -0.10898 | 0.98573 | -0.1004 | 1.7777
16 | 0.0021726 | 0.0005442 | -0.0021724 | -0.00054446 | 1.7179e-07 | -2.5749e-07 | 0.0032864 | 0.0032865 | 0.0032865 | 0.98369 | -0.11501 | 0.98361 | -0.11558 | 1.2172
17 | -0.033468 | -0.0083765 | 0.033562 | 0.0084057 | 9.3442e-05 | 2.9188e-05 | 0.050518 | 0.050516 | 0.050518 | 0.98573 | -0.1004 | 0.98857 | -0.08022 | 6.2368
18 | 0.030288 | 0.0075846 | -0.030208 | -0.0075608 | 8.0132e-05 | 2.3791e-05 | 0.04572 | 0.045722 | 0.045722 | 0.98573 | -0.1004 | 0.98304 | -0.11958 | 5.6447
19 | -0.0014624 | -0.00036652 | 0.0014632 | 0.00036363 | 7.4955e-07 | -2.8844e-06 | 0.0022028 | 0.0022017 | 0.0022028 | 0.98788 | -0.085717 | 0.9884 | -0.081985 | 0.81586
20 | -0.012129 | -0.0030224 | 0.012133 | 0.0030236 | 3.6572e-06 | 1.1811e-06 | 0.018254 | 0.018254 | 0.018254 | 0.9884 | -0.081985 | 0.98871 | -0.079782 | 6.7609
21 | 0.010666 | 0.0026588 | -0.010663 | -0.002658 | 2.7735e-06 | 8.4571e-07 | 0.016053 | 0.016053 | 0.016053 | 0.9884 | -0.081985 | 0.98813 | -0.083883 | 5.9455
22 | -0.012529 | -0.0031229 | 0.012535 | 0.0031247 | 5.3611e-06 | 1.7517e-06 | 0.018851 | 0.018851 | 0.018851 | 0.98871 | -0.079782 | 0.98914 | -0.076659 | 6.9818
23 | 0.0091568 | 0.0022804 | -0.0091496 | -0.0022784 | 7.2357e-06 | 2.0018e-06 | 0.013784 | 0.013784 | 0.013784 | 0.98813 | -0.083883 | 0.98733 | -0.089666 | 5.1053
24 | -0.013077 | -0.0032605 | 0.01309 | 0.0032648 | 1.3087e-05 | 4.3366e-06 | 0.019666 | 0.019666 | 0.019666 | 0.98914 | -0.076659 | 0.99016 | -0.069362 | 7.2836
25 | 0.0091496 | 0.0022784 | -0.0091223 | -0.0022708 | 2.7321e-05 | 7.5703e-06 | 0.013784 | 0.013785 | 0.013785 | 0.98733 | -0.089666 | 0.98429 | -0.11155 | 5.1057
26 | -0.0035282 | -0.00088425 | 0.0035287 | 0.00088406 | 5.3545e-07 | -1.8423e-07 | 0.0053106 | 0.0053105 | 0.0053106 | 0.98858 | -0.079415 | 0.98874 | -0.078319 | 1.9669
27 | 0.045836 | 0.011534 | -0.045715 | -0.011488 | 0.00012111 | 4.606e-05 | 0.068998 | 0.068999 | 0.068999 | 0.98874 | -0.078319 | 0.98604 | -0.097302 | 25.555
28 | -0.049365 | -0.012418 | 0.049549 | 0.012488 | 0.00018397 | 7.0068e-05 | 0.074309 | 0.074309 | 0.074309 | 0.98874 | -0.078319 | 0.99254 | -0.0517 | 27.5218
29 | 0.0081189 | 0.0020347 | -0.0081169 | -0.0020342 | 2.0541e-06 | 5.104e-07 | 0.012252 | 0.012252 | 0.012252 | 0.98604 | -0.097302 | 0.98578 | -0.09913 | 4.5378
30 | 0.037596 | 0.0094534 | -0.03742 | -0.0093869 | 0.00017585 | 6.6525e-05 | 0.056746 | 0.056747 | 0.056747 | 0.98604 | -0.097302 | 0.98128 | -0.13103 | 21.0174
31 | -0.050848 | -0.012814 | 0.050963 | 0.012858 | 0.00011483 | 4.3756e-05 | 0.076257 | 0.076256 | 0.076257 | 0.99254 | -0.0517 | 0.99485 | -0.035603 | 28.2432
32 | -0.051701 | -0.013052 | 0.051892 | 0.013124 | 0.00019065 | 7.2659e-05 | 0.077258 | 0.077257 | 0.077258 | 0.99621 | -0.026155 | 1 | 0 | 28.614
33 | 0.051701 | 0.013052 | -0.051632 | -0.013026 | 6.8526e-05 | 2.6117e-05 | 0.077258 | 0.077258 | 0.077258 | 0.99621 | -0.026155 | 0.99485 | -0.035603 | 28.614
34 | 0.00026167 | 6.4745e-05 | -0.00026167 | -6.558e-05 | 6.0327e-09 | -8.3487e-07 | 0.00038908 | 0.00038937 | 0.00038937 | 1 | 0 | 0.99998 | -0.00016865 | 0.14421
35 | 0.0014459 | 0.00036203 | -0.0014458 | -0.00036236 | 7.9561e-08 | -3.3075e-07 | 0.0021514 | 0.0021515 | 0.0021515 | 1 | 0 | 0.99994 | -0.00039786 | 0.79686
36 | 0.1092 | 0.027479 | -0.10878 | -0.027323 | 0.00041487 | 0.0001566 | 0.16253 | 0.16253 | 0.16253 | 1 | 0 | 0.99608 | -0.027325 | 20.0656
37 | 0.0054236 | 0.0013592 | -0.0054232 | -0.0013592 | 3.7337e-07 | 2.9796e-08 | 0.0081867 | 0.0081868 | 0.0081868 | 0.98578 | -0.09913 | 0.98571 | -0.099627 | 3.0321
38 | 0.026548 | 0.0066622 | -0.026492 | -0.0066413 | 5.6048e-05 | 2.0858e-05 | 0.040261 | 0.040261 | 0.040261 | 0.98128 | -0.13103 | 0.97915 | -0.14627 | 14.9116
39 | -0.013583 | -0.0033942 | 0.013589 | 0.003396 | 5.2794e-06 | 1.7633e-06 | 0.020296 | 0.020296 | 0.020296 | 0.99568 | -0.030148 | 0.99608 | -0.027325 | 7.5172
40 | 0.01316 | 0.0032882 | -0.013114 | -0.0032729 | 4.6199e-05 | 1.5288e-05 | 0.019664 | 0.019665 | 0.019665 | 0.99568 | -0.030148 | 0.99208 | -0.055733 | 7.2834
41 | 0.095196 | 0.023927 | -0.095064 | -0.023877 | 0.00013228 | 4.9652e-05 | 0.14223 | 0.14224 | 0.14224 | 0.99608 | -0.027325 | 0.99465 | -0.037319 | 17.5599
42 | 0.013114 | 0.0032729 | -0.01309 | -0.0032648 | 2.4501e-05 | 8.115e-06 | 0.019665 | 0.019666 | 0.019666 | 0.99208 | -0.055733 | 0.99016 | -0.069362 | 7.2835
43 | 0.00070321 | 0.00017594 | -0.00070321 | -0.00017598 | 2.1496e-09 | -3.958e-08 | 0.0010519 | 0.0010519 | 0.0010519 | 0.99465 | -0.037319 | 0.99465 | -0.037341 | 0.3896
44 | 0.094361 | 0.023701 | -0.094311 | -0.023683 | 4.979e-05 | 1.8682e-05 | 0.14118 | 0.14118 | 0.14118 | 0.99465 | -0.037319 | 0.99411 | -0.041116 | 17.4301
45 | 0.0001319 | 3.2795e-05 | -0.0001319 | -3.3057e-05 | 4.8985e-10 | -2.6162e-07 | 0.00019723 | 0.00019732 | 0.00019732 | 0.99465 | -0.037341 | 0.99465 | -0.037368 | 0.073082
46 | 0.093169 | 0.023397 | -0.093136 | -0.023385 | 3.2981e-05 | 1.2368e-05 | 0.13947 | 0.13947 | 0.13947 | 0.99411 | -0.041116 | 0.99375 | -0.043664 | 17.2191
47 | 0.001142 | 0.00028562 | -0.0011419 | -0.00028619 | 8.5828e-08 | -5.7731e-07 | 0.0017092 | 0.0017094 | 0.0017094 | 0.99411 | -0.041116 | 0.99404 | -0.04166 | 0.63311
48 | -0.001705 | -0.00042731 | 0.001705 | 0.00042718 | 5.0023e-08 | -1.3029e-07 | 0.0025939 | 0.0025939 | 0.0025939 | 0.97807 | -0.15401 | 0.9781 | -0.1538 | 0.96072
49 | 0.01015 | 0.0025442 | -0.010145 | -0.0025426 | 5.4019e-06 | 1.6223e-06 | 0.015442 | 0.015442 | 0.015442 | 0.9781 | -0.1538 | 0.97756 | -0.15764 | 5.7194
50 | -0.011855 | -0.0029714 | 0.011857 | 0.002972 | 1.9461e-06 | 6.2814e-07 | 0.018036 | 0.018036 | 0.018036 | 0.9781 | -0.1538 | 0.97826 | -0.15261 | 6.6801
51 | 0.024498 | 0.0061415 | -0.024477 | -0.0061336 | 2.1511e-05 | 7.9609e-06 | 0.037231 | 0.037231 | 0.037231 | 0.97915 | -0.14627 | 0.97826 | -0.15261 | 13.7892
52 | 0.012619 | 0.0031616 | -0.012616 | -0.0031605 | 3.347e-06 | 1.1046e-06 | 0.019195 | 0.019195 | 0.019195 | 0.97826 | -0.15261 | 0.97799 | -0.15453 | 7.1092
53 | 0.011637 | 0.0029157 | -0.011616 | -0.002909 | 2.0829e-05 | 6.6777e-06 | 0.017706 | 0.017706 | 0.017706 | 0.97799 | -0.15453 | 0.97619 | -0.16749 | 6.5579
54 | 0.00097871 | 0.0002448 | -0.00097865 | -0.00024527 | 5.4365e-08 | -4.7215e-07 | 0.0014889 | 0.0014891 | 0.0014891 | 0.97799 | -0.15453 | 0.97794 | -0.15493 | 0.55152
55 | -0.0042328 | -0.0010608 | 0.0042338 | 0.0010608 | 9.4438e-07 | -9.0216e-08 | 0.0064563 | 0.0064562 | 0.0064563 | 0.97556 | -0.17201 | 0.97578 | -0.1704 | 2.3912
56 | -0.0079999 | -0.0020038 | 0.0080031 | 0.0020046 | 3.2233e-06 | 8.0596e-07 | 0.012199 | 0.012199 | 0.012199 | 0.97578 | -0.1704 | 0.97619 | -0.16749 | 4.5181
57 | 0.0037661 | 0.00094303 | -0.0037656 | -0.00094314 | 5.0313e-07 | -1.1183e-07 | 0.0057428 | 0.0057429 | 0.0057429 | 0.97578 | -0.1704 | 0.97565 | -0.17137 | 2.127
58 | 0.0036134 | 0.00090441 | -0.003612 | -0.00090479 | 1.3596e-06 | -3.7471e-07 | 0.0055075 | 0.0055078 | 0.0055078 | 0.97619 | -0.16749 | 0.97581 | -0.17021 | 2.0399
59 | 0.0023212 | 0.00058113 | -0.0023208 | -0.00058164 | 4.2033e-07 | -5.0944e-07 | 0.00354 | 0.0035402 | 0.0035402 | 0.97565 | -0.17137 | 0.97546 | -0.17268 | 1.3112
60 | 0.0029785 | 0.00074601 | -0.0029782 | -0.00074615 | 2.4119e-07 | -1.4129e-07 | 0.0045417 | 0.0045418 | 0.0045418 | 0.97581 | -0.17021 | 0.97573 | -0.1708 | 1.6822
61 | -0.0063577 | -0.0015934 | 0.0063583 | 0.0015935 | 5.6403e-07 | 9.1653e-08 | 0.009594 | 0.009594 | 0.009594 | 0.98607 | -0.097914 | 0.98616 | -0.097273 | 3.5533
62 | 0.0060492 | 0.0015141 | -0.0060476 | -0.0015139 | 1.5408e-06 | 2.1452e-07 | 0.0091269 | 0.009127 | 0.009127 | 0.98616 | -0.097273 | 0.98591 | -0.099118 | 3.3804
63 | -0.012407 | -0.0031076 | 0.012435 | 0.0031167 | 2.7937e-05 | 9.1111e-06 | 0.018721 | 0.01872 | 0.018721 | 0.98616 | -0.097273 | 0.98846 | -0.081018 | 6.9336
64 | 0.0029277 | 0.00073199 | -0.0029275 | -0.00073215 | 2.4712e-07 | -1.6364e-07 | 0.0044181 | 0.0044182 | 0.0044182 | 0.98591 | -0.099118 | 0.98582 | -0.09973 | 1.6364
65 | -0.017442 | -0.0043668 | 0.017447 | 0.0043686 | 5.1487e-06 | 1.8268e-06 | 0.026256 | 0.026256 | 0.026256 | 0.98846 | -0.081018 | 0.98876 | -0.078882 | 9.7244
66 | 0.0050069 | 0.0012501 | -0.0050061 | -0.00125 | 8.4597e-07 | 1.941e-08 | 0.0075357 | 0.0075358 | 0.0075358 | 0.98846 | -0.081018 | 0.98828 | -0.082247 | 2.791
67 | 0.0021668 | 0.00054152 | -0.0021666 | -0.00054184 | 2.0596e-07 | -3.1425e-07 | 0.0032701 | 0.0032703 | 0.0032703 | 0.98582 | -0.09973 | 0.98572 | -0.10042 | 1.2112
68 | -0.022146 | -0.0055461 | 0.022159 | 0.005551 | 1.3409e-05 | 4.9091e-06 | 0.033326 | 0.033326 | 0.033326 | 0.98876 | -0.078882 | 0.98937 | -0.074504 | 12.3431
69 | 0.0046981 | 0.0011774 | -0.004698 | -0.0011774 | 1.2505e-07 | -3.3183e-09 | 0.0070704 | 0.0070704 | 0.0070704 | 0.98876 | -0.078882 | 0.98873 | -0.079074 | 2.6187
70 | 0.0011144 | 0.0002747 | -0.0011138 | -0.00027906 | 6.3105e-07 | -4.3619e-06 | 0.0016763 | 0.0016779 | 0.0016779 | 0.98828 | -0.082247 | 0.98771 | -0.086407 | 0.62144
71 | -0.019969 | -0.0050046 | 0.02002 | 0.0050231 | 5.0981e-05 | 1.8455e-05 | 0.030118 | 0.030118 | 0.030118 | 0.98657 | -0.094364 | 0.98917 | -0.075966 | 11.1549
72 | -0.055746 | -0.013973 | 0.05575 | 0.013974 | 4.3224e-06 | 1.5487e-06 | 0.08386 | 0.08386 | 0.08386 | 0.98917 | -0.075966 | 0.98925 | -0.075406 | 10.3531
73 | 0.035726 | 0.0089496 | -0.035705 | -0.0089429 | 2.101e-05 | 6.7347e-06 | 0.053742 | 0.053742 | 0.053742 | 0.98917 | -0.075966 | 0.98857 | -0.08022 | 6.6349
74 | -0.057658 | -0.014452 | 0.05769 | 0.014464 | 3.1789e-05 | 1.1443e-05 | 0.086729 | 0.086729 | 0.086729 | 0.98925 | -0.075406 | 0.98981 | -0.071427 | 10.7073
75 | 0.0019076 | 0.00047789 | -0.0019075 | -0.00047807 | 8.748e-08 | -1.8495e-07 | 0.0028694 | 0.0028694 | 0.0028694 | 0.98925 | -0.075406 | 0.9892 | -0.075738 | 1.0628
76 | 0.027404 | 0.0068668 | -0.027392 | -0.0068625 | 1.1664e-05 | 4.3447e-06 | 0.041196 | 0.041196 | 0.041196 | 0.98981 | -0.071427 | 0.98937 | -0.074504 | 15.258
77 | -0.085093 | -0.02133 | 0.085287 | 0.021403 | 0.0001942 | 7.2488e-05 | 0.12793 | 0.12792 | 0.12793 | 0.98981 | -0.071427 | 0.99214 | -0.054984 | 15.7932
78 | 0.0073677 | 0.0018465 | -0.0073672 | -0.0018464 | 5.4538e-07 | 1.2265e-07 | 0.011215 | 0.011215 | 0.011215 | 0.97756 | -0.15764 | 0.97748 | -0.15818 | 4.1537
79 | -0.00058652 | -0.00014697 | 0.00058655 | 0.00014628 | 2.5929e-08 | -6.8696e-07 | 0.00087864 | 0.00087839 | 0.00087864 | 0.99329 | -0.046884 | 0.99334 | -0.046563 | 0.32542
80 | 0.00046448 | 0.00011638 | -0.00046448 | -0.00011641 | 6.4781e-10 | -2.7506e-08 | 0.00069581 | 0.00069582 | 0.00069582 | 0.99329 | -0.046884 | 0.99329 | -0.046894 | 0.25771
81 | -0.00058655 | -0.00014628 | 0.00058656 | 0.00014588 | 1.5296e-08 | -4.0547e-07 | 0.00087839 | 0.00087825 | 0.00087839 | 0.99334 | -0.046563 | 0.99337 | -0.046373 | 0.32533
82 | -0.0056578 | -0.0014162 | 0.0056593 | 0.0014163 | 1.5002e-06 | 1.435e-07 | 0.0084745 | 0.0084743 | 0.0084745 | 0.99337 | -0.046373 | 0.99364 | -0.044452 | 3.1387
83 | 0.00054945 | 0.00013742 | -0.00054944 | -0.0001377 | 9.4504e-09 | -2.8583e-07 | 0.00082294 | 0.00082304 | 0.00082304 | 0.99337 | -0.046373 | 0.99335 | -0.046497 | 0.30483
84 | 0.0045218 | 0.0011329 | -0.0045213 | -0.0011329 | 4.7285e-07 | -3.1938e-08 | 0.0067733 | 0.0067734 | 0.0067734 | 0.99337 | -0.046373 | 0.99326 | -0.047128 | 2.5087
85 | -0.0063572 | -0.0015913 | 0.0063579 | 0.0015914 | 6.9251e-07 | 1.077e-07 | 0.0095195 | 0.0095194 | 0.0095195 | 0.99364 | -0.044452 | 0.99375 | -0.043664 | 3.5257
86 | 0.0039073 | 0.00097906 | -0.0039069 | -0.00097915 | 4.3712e-07 | -9.646e-08 | 0.0058535 | 0.0058536 | 0.0058536 | 0.99326 | -0.047128 | 0.99314 | -0.047937 | 2.168
87 | 0.0010952 | 0.0002738 | -0.0010951 | -0.00027445 | 9.2228e-08 | -6.5379e-07 | 0.0016531 | 0.0016533 | 0.0016533 | 0.98568 | -0.10072 | 0.98559 | -0.10133 | 0.61233
88 | -0.0010952 | -0.0002738 | 0.0010952 | 0.00027347 | 4.5831e-08 | -3.2501e-07 | 0.0016531 | 0.0016529 | 0.0016531 | 0.98568 | -0.10072 | 0.98572 | -0.10042 | 0.61224
89 | 0.0010714 | 0.00026837 | -0.0010714 | -0.00026852 | 2.0723e-08 | -1.5386e-07 | 0.0016173 | 0.0016174 | 0.0016174 | 0.98572 | -0.10042 | 0.9857 | -0.10056 | 0.59904
90 | -0.00081279 | -0.0002037 | 0.00081282 | 0.00020326 | 3.4221e-08 | -4.3963e-07 | 0.0012348 | 0.0012346 | 0.0012348 | 0.97948 | -0.14625 | 0.97952 | -0.14595 | 0.45733
91 | -0.0025072 | -0.00062792 | 0.0025098 | 0.00062536 | 2.5402e-06 | -2.5603e-06 | 0.0038086 | 0.0038074 | 0.0038086 | 0.97952 | -0.14595 | 0.98054 | -0.13858 | 1.4106
92 | -0.0029685 | -0.00074032 | 0.002971 | 0.00073879 | 2.5025e-06 | -1.5344e-06 | 0.0045035 | 0.0045026 | 0.0045035 | 0.98054 | -0.13858 | 0.9814 | -0.13242 | 1.668
93 | -0.00039904 | -0.00010001 | 0.00039908 | 9.7722e-05 | 4.1496e-08 | -2.2862e-06 | 0.00060481 | 0.00060399 | 0.00060481 | 0.98175 | -0.12984 | 0.98186 | -0.12907 | 0.224
94 | -0.0042661 | -0.0010603 | 0.0042665 | 0.0010602 | 3.3604e-07 | -3.3871e-08 | 0.0064622 | 0.0064621 | 0.0064622 | 0.98186 | -0.12907 | 0.98194 | -0.12849 | 2.3934
95 | 0.003867 | 0.00096256 | -0.0038653 | -0.00096292 | 1.7685e-06 | -3.6375e-07 | 0.0058582 | 0.0058585 | 0.0058585 | 0.98186 | -0.12907 | 0.9814 | -0.13242 | 2.1698
96 | -0.0052042 | -0.0012953 | 0.005207 | 0.0012954 | 2.798e-06 | 1.6289e-07 | 0.0078832 | 0.0078829 | 0.0078832 | 0.98194 | -0.12849 | 0.98248 | -0.12456 | 2.9197
97 | 0.0033794 | 0.00084075 | -0.0033788 | -0.00084098 | 5.9085e-07 | -2.3078e-07 | 0.005116 | 0.0051162 | 0.0051162 | 0.98248 | -0.12456 | 0.98231 | -0.12584 | 1.8949
98 | -0.0085864 | -0.0021362 | 0.0085951 | 0.0021385 | 8.6686e-06 | 2.2918e-06 | 0.012999 | 0.012999 | 0.012999 | 0.98248 | -0.12456 | 0.98351 | -0.11716 | 4.8144
99 | -0.0091153 | -0.0022688 | 0.0091223 | 0.0022708 | 6.9879e-06 | 1.9393e-06 | 0.013786 | 0.013785 | 0.013786 | 0.98351 | -0.11716 | 0.98429 | -0.11155 | 5.1058
100 | 0.0029215 | 0.00072637 | -0.0029213 | -0.00072655 | 2.7942e-07 | -1.8219e-07 | 0.0044235 | 0.0044236 | 0.0044236 | 0.98231 | -0.12584 | 0.98221 | -0.12654 | 1.6384
101 | 0.00079074 | 0.00019806 | -0.00079073 | -0.00019818 | 8.0335e-09 | -1.1046e-07 | 0.0011979 | 0.0011979 | 0.0011979 | 0.98221 | -0.12654 | 0.9822 | -0.12661 | 0.44368
102 | 0.0021305 | 0.00052849 | -0.0021298 | -0.00052954 | 6.7044e-07 | -1.0484e-06 | 0.0032257 | 0.0032262 | 0.0032262 | 0.98221 | -0.12654 | 0.98189 | -0.12885 | 1.1949
103 | 0.0018864 | 0.00046851 | -0.0018861 | -0.00046904 | 2.5152e-07 | -5.2766e-07 | 0.0028572 | 0.0028574 | 0.0028574 | 0.98189 | -0.12885 | 0.98176 | -0.12983 | 1.0583
104 | 0.0018861 | 0.00046904 | -0.0018847 | -0.00047198 | 1.4039e-06 | -2.9402e-06 | 0.0028574 | 0.0028586 | 0.0028586 | 0.98176 | -0.12983 | 0.981 | -0.13526 | 1.0588
105 | 0.00071974 | 0.00018001 | -0.00071972 | -0.00018038 | 2.2009e-08 | -3.6521e-07 | 0.0010916 | 0.0010917 | 0.0010917 | 0.981 | -0.13526 | 0.98097 | -0.13548 | 0.40434
106 | -0.085412 | -0.021434 | 0.085417 | 0.021436 | 4.8932e-06 | 1.8265e-06 | 0.12811 | 0.12811 | 0.12811 | 0.99214 | -0.054984 | 0.9922 | -0.054572 | 15.8162
107 | 0.0029782 | 0.00074615 | -0.0029781 | -0.00074623 | 1.4122e-07 | -8.2706e-08 | 0.0045418 | 0.0045419 | 0.0045419 | 0.97573 | -0.1708 | 0.97568 | -0.17114 | 1.6822
108 | 0.0016389 | 0.0004106 | -0.0016389 | -0.00041074 | 4.8531e-08 | -1.368e-07 | 0.0024995 | 0.0024995 | 0.0024995 | 0.97568 | -0.17114 | 0.97565 | -0.17135 | 0.92575
109 | 0.086778 | 0.021793 | -0.086647 | -0.021744 | 0.00013138 | 4.908e-05 | 0.12996 | 0.12996 | 0.12996 | 0.99375 | -0.043664 | 0.9922 | -0.054572 | 16.0439
110 | 0.0011138 | 0.00027906 | -0.0011137 | -0.00027913 | 9.6799e-09 | -6.6797e-08 | 0.0016779 | 0.0016779 | 0.0016779 | 0.98771 | -0.086407 | 0.9877 | -0.08647 | 0.62145

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.1636 | 0.041031

## res_load
| p_mw | q_mvar
0 | 0.0010452 | 0.00026194
1 | 0.001114 | 0.00027921
2 | 0.0028756 | 0.00072069
3 | 0.0072283 | 0.0018116
4 | 0.00026007 | 6.518e-05
5 | 0.0015319 | 0.00038393
6 | 0.0012641 | 0.00031682
7 | 0.00053137 | 0.00013317
8 | 0.0032069 | 0.00080373
9 | 0.0020897 | 0.00052373
10 | 0.001001 | 0.00025088
11 | 0.0021724 | 0.00054446
12 | 0.0014624 | 0.00036652
13 | 0.00039627 | 9.9314e-05
14 | 0.0015067 | 0.0003776
15 | 0.0005419 | 0.00013581
16 | 0.0035282 | 0.00088425
17 | 0.0012993 | 0.00032565
18 | 0.00066946 | 0.00016778
19 | 0.0026933 | 0.000675
20 | 0.010872 | 0.0027247
21 | 0.00042296 | 0.000106
22 | 0.00057131 | 0.00014318
23 | 0.00026167 | 6.558e-05
24 | 0.0014458 | 0.00036236
25 | 0.001705 | 0.00042731
26 | 0.0019941 | 0.00049977
27 | 0.0054232 | 0.0013592
28 | 0.0042328 | 0.0010608
29 | 0.0014444 | 0.00036201
30 | 0.00063353 | 0.00015878
31 | 0.0023208 | 0.00058164
32 | 0.0063577 | 0.0015934
33 | 0.0031199 | 0.00078192
34 | 0.00076062 | 0.00019063
35 | 0.0038917 | 0.00097534
36 | 0.019969 | 0.0050046
37 | 0.0021435 | 0.00053721
38 | 0.0019075 | 0.00047807
39 | 0.00097865 | 0.00024527
40 | 0.0027773 | 0.00069606
41 | 0.0073672 | 0.0018464
42 | 0.00012204 | 3.0586e-05
43 | 0.00046448 | 0.00011641
44 | 0.00069792 | 0.00017492
45 | 0.00054944 | 0.0001377
46 | 0.00061401 | 0.00015388
47 | 0.0010335 | 0.00025901
48 | 0.0010951 | 0.00027445
49 | 0.0010714 | 0.00026852
50 | 0.0077992 | 0.0019547
51 | 0.00081279 | 0.0002037
52 | 0.0016944 | 0.00042466
53 | 0.0004587 | 0.00011496
54 | 0.00039904 | 0.00010001
55 | 0.00093779 | 0.00023503
56 | 0.0008943 | 0.00022413
57 | 0.00052016 | 0.00013036
58 | 0.00045728 | 0.0001146
59 | 0.00079073 | 0.00019818
60 | 0.00024349 | 6.1025e-05
61 | 0.001165 | 0.00029197
62 | 0.00071972 | 0.00018038
63 | 0.0052329 | 0.0013115
64 | 0.00012464 | 3.1237e-05
65 | 0.0013392 | 0.00033563
66 | 0.0016389 | 0.00041074
67 | 0.0039069 | 0.00097915
68 | 0.0012298 | 0.00030821
69 | 0.0001319 | 3.3057e-05
70 | 0.004698 | 0.0011774
71 | 0.0011137 | 0.00027913
72 | 0.0011419 | 0.00028619

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1