## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1143-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1143-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1143-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1143-1_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1143-1_0_4_node_32 | 0.4 | n |  | TRUE
5 | bus_LV_1143-1_0_4_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_1143-1_0_4_node_47 | 0.4 | n |  | TRUE
7 | bus_LV_1143-1_0_4_node_45 | 0.4 | n |  | TRUE
8 | bus_LV_1143-1_0_4_node_22 | 0.4 | n |  | TRUE
9 | bus_LV_1143-1_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1143-1_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1143-1_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1143-1_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1143-1_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1143-1_0_4_node_18 | 0.4 | n |  | TRUE
15 | bus_LV_1143-1_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_1143-1_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1143-1_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1143-1_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1143-1_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_1143-1_0_4_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1143-1_0_4_node_39 | 0.4 | n |  | TRUE
22 | bus_LV_1143-1_0_4_node_91 | 0.4 | n |  | TRUE
23 | bus_LV_1143-1_0_4_node_43 | 0.4 | n |  | TRUE
24 | bus_LV_1143-1_0_4_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_1143-1_0_4_node_37 | 0.4 | n |  | TRUE
26 | bus_LV_1143-1_0_4_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_1143-1_0_4_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_1143-1_0_4_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1143-1_0_4_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1143-1_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1143-1_0_4_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1143-1_0_4_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_1143-1_0_4_node_26 | 0.4 | n |  | TRUE
34 | bus_LV_1143-1_0_4_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_1143-1_0_4_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1143-1_0_4_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_1143-1_0_4_node_36 | 0.4 | n |  | TRUE
38 | bus_LV_1143-1_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_1143-1_0_4_node_66 | 0.4 | n |  | TRUE
40 | bus_LV_1143-1_0_4_node_82 | 0.4 | n |  | TRUE
41 | bus_LV_1143-1_0_4_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_1143-1_0_4_node_33 | 0.4 | n |  | TRUE
43 | bus_LV_1143-1_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_1143-1_0_4_node_51 | 0.4 | n |  | TRUE
45 | bus_LV_1143-1_0_4_node_68 | 0.4 | n |  | TRUE
46 | bus_LV_1143-1_0_4_node_67 | 0.4 | n |  | TRUE
47 | bus_LV_1143-1_0_4_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_1143-1_0_4_node_38 | 0.4 | n |  | TRUE
49 | bus_LV_1143-1_0_4_node_40 | 0.4 | n |  | TRUE
50 | bus_LV_1143-1_0_4_node_64 | 0.4 | n |  | TRUE
51 | bus_LV_1143-1_0_4_node_74 | 0.4 | n |  | TRUE
52 | bus_LV_1143-1_0_4_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_1143-1_0_4_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_1143-1_0_4_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_1143-1_0_4_node_84 | 0.4 | n |  | TRUE
56 | bus_LV_1143-1_0_4_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_1143-1_0_4_node_65 | 0.4 | n |  | TRUE
58 | bus_LV_1143-1_0_4_node_81 | 0.4 | n |  | TRUE
59 | bus_LV_1143-1_0_4_node_50 | 0.4 | n |  | TRUE
60 | bus_LV_1143-1_0_4_node_52 | 0.4 | n |  | TRUE
61 | bus_LV_1143-1_0_4_node_85 | 0.4 | n |  | TRUE
62 | bus_LV_1143-1_0_4_node_86 | 0.4 | n |  | TRUE
63 | bus_LV_1143-1_0_4_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_1143-1_0_4_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_1143-1_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_1143-1_0_4_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_1143-1_0_4_node_89 | 0.4 | n |  | TRUE
68 | bus_LV_1143-1_0_4_node_90 | 0.4 | n |  | TRUE
69 | bus_LV_1143-1_0_4_node_57 | 0.4 | n |  | TRUE
70 | bus_LV_1143-1_0_4_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_1143-1_0_4_node_59 | 0.4 | n |  | TRUE
72 | bus_LV_1143-1_0_4_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_1143-1_0_4_node_61 | 0.4 | n |  | TRUE
74 | bus_LV_1143-1_0_4_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_1143-1_0_4_node_78 | 0.4 | n |  | TRUE
76 | bus_LV_1143-1_0_4_node_77 | 0.4 | n |  | TRUE
77 | bus_LV_1143-1_0_4_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_1143-1_0_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_1143-1_0_4_node_70 | 0.4 | n |  | TRUE
80 | bus_LV_1143-1_0_4_node_123 | 0.4 | n |  | TRUE
81 | bus_LV_1143-1_0_4_node_121 | 0.4 | n |  | TRUE
82 | bus_LV_1143-1_0_4_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_1143-1_0_4_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_1143-1_0_4_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_1143-1_0_4_node_76 | 0.4 | n |  | TRUE
86 | bus_LV_1143-1_0_4_node_95 | 0.4 | n |  | TRUE
87 | bus_LV_1143-1_0_4_node_102 | 0.4 | n |  | TRUE
88 | bus_LV_1143-1_0_4_node_119 | 0.4 | n |  | TRUE
89 | bus_LV_1143-1_0_4_node_93 | 0.4 | n |  | TRUE
90 | bus_LV_1143-1_0_4_node_103 | 0.4 | n |  | TRUE
91 | bus_LV_1143-1_0_4_node_105 | 0.4 | n |  | TRUE
92 | bus_LV_1143-1_0_4_node_79 | 0.4 | n |  | TRUE
93 | bus_LV_1143-1_0_4_node_80 | 0.4 | n |  | TRUE
94 | bus_LV_1143-1_0_4_node_92 | 0.4 | n |  | TRUE
95 | bus_LV_1143-1_0_4_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1143-1_0_4_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_1143-1_0_4_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_1143-1_0_4_node_110 | 0.4 | n |  | TRUE
99 | bus_LV_1143-1_0_4_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_1143-1_0_4_node_109 | 0.4 | n |  | TRUE
101 | bus_LV_1143-1_0_4_node_94 | 0.4 | n |  | TRUE
102 | bus_LV_1143-1_0_4_node_107 | 0.4 | n |  | TRUE
103 | bus_LV_1143-1_0_4_node_96 | 0.4 | n |  | TRUE
104 | bus_LV_1143-1_0_4_node_108 | 0.4 | n |  | TRUE
105 | bus_LV_1143-1_0_4_node_116 | 0.4 | n |  | TRUE
106 | bus_LV_1143-1_0_4_node_117 | 0.4 | n |  | TRUE
107 | bus_LV_1143-1_0_4_node_118 | 0.4 | n |  | TRUE
108 | bus_LV_1143-1_0_4_node_97 | 0.4 | n |  | TRUE
109 | bus_LV_1143-1_0_4_node_98 | 0.4 | n |  | TRUE
110 | bus_LV_1143-1_0_4_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_1143-1_0_4_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_1143-1_0_4_node_101 | 0.4 | n |  | TRUE
113 | bus_LV_1143-1_0_4_node_104 | 0.4 | n |  | TRUE
114 | bus_LV_1143-1_0_4_node_106 | 0.4 | n |  | TRUE
115 | bus_LV_1143-1_0_4_node_114 | 0.4 | n |  | TRUE
116 | bus_LV_1143-1_0_4_node_112 | 0.4 | n |  | TRUE
117 | bus_LV_1143-1_0_4_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_1143-1_0_4_node_113 | 0.4 | n |  | TRUE
119 | bus_LV_1143-1_0_4_node_115 | 0.4 | n |  | TRUE
120 | bus_LV_1143-1_0_4_node_120 | 0.4 | n |  | TRUE
121 | bus_MV_131_0_node_66 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1143-1_0_4_load_0 | 0 | 0.012333 | 0.0030908 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1143-1_0_4_load_1 | 1 | 0.00037314 | 9.3517e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1143-1_0_4_load_24 | 5 | 0.0023829 | 0.00059721 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1143-1_0_4_load_45 | 7 | 0.0026925 | 0.00067479 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1143-1_0_4_load_22 | 8 | 0.0013043 | 0.00032689 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1143-1_0_4_load_5 | 9 | 0.00073408 | 0.00018398 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1143-1_0_4_load_6 | 10 | 0.00049284 | 0.00012352 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1143-1_0_4_load_7 | 11 | 0.00042727 | 0.00010708 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1143-1_0_4_load_8 | 12 | 0.0002919 | 7.3156e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1143-1_0_4_load_20 | 13 | 0.00019819 | 4.9671e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1143-1_0_4_load_9 | 15 | 0.014762 | 0.0036997 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1143-1_0_4_load_15 | 19 | 0.0004066 | 0.0001019 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1143-1_0_4_load_91 | 22 | 0.0016676 | 0.00041793 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1143-1_0_4_load_43 | 23 | 0.011474 | 0.0028757 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1143-1_0_4_load_16 | 24 | 0.00040022 | 0.0001003 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1143-1_0_4_load_37 | 25 | 0.0014403 | 0.00036098 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1143-1_0_4_load_41 | 26 | 0.0047818 | 0.0011984 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1143-1_0_4_load_17 | 27 | 0.00039772 | 9.9677e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1143-1_0_4_load_19 | 28 | 0.0005205 | 0.00013045 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1143-1_0_4_load_21 | 29 | 0.0011396 | 0.00028562 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1143-1_0_4_load_23 | 30 | 0.00099383 | 0.00024908 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1143-1_0_4_load_25 | 31 | 0.0012603 | 0.00031586 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1143-1_0_4_load_30 | 32 | 0.0013277 | 0.00033275 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1143-1_0_4_load_26 | 33 | 0.00045634 | 0.00011437 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1143-1_0_4_load_27 | 34 | 0.00026995 | 6.7656e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1143-1_0_4_load_28 | 35 | 0.0014657 | 0.00036735 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1143-1_0_4_load_34 | 38 | 0.00048206 | 0.00012081 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1143-1_0_4_load_66 | 39 | 0.0045574 | 0.0011422 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1143-1_0_4_load_82 | 40 | 0.00048794 | 0.00012229 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1143-1_0_4_load_33 | 42 | 0.0025438 | 0.00063752 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1143-1_0_4_load_51 | 44 | 0.0004688 | 0.00011749 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1143-1_0_4_load_68 | 45 | 0.00027282 | 6.8374e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1143-1_0_4_load_67 | 46 | 0.00034863 | 8.7376e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1143-1_0_4_load_49 | 47 | 0.0018887 | 0.00047335 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1143-1_0_4_load_38 | 48 | 0.0064456 | 0.0016154 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1143-1_0_4_load_40 | 49 | 0.0029764 | 0.00074596 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1143-1_0_4_load_74 | 51 | 0.00165 | 0.00041354 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1143-1_0_4_load_62 | 52 | 0.0021393 | 0.00053616 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1143-1_0_4_load_42 | 53 | 0.0047602 | 0.001193 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1143-1_0_4_load_44 | 54 | 0.0056983 | 0.0014281 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1143-1_0_4_load_84 | 55 | 0.0013492 | 0.00033815 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1143-1_0_4_load_48 | 56 | 0.0012862 | 0.00032236 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1143-1_0_4_load_65 | 57 | 0.0017454 | 0.00043745 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1143-1_0_4_load_81 | 58 | 0.003459 | 0.00086691 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1143-1_0_4_load_50 | 59 | 0.0013208 | 0.00033102 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1143-1_0_4_load_52 | 60 | 0.0021802 | 0.00054642 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1143-1_0_4_load_85 | 61 | 0.0026753 | 0.00067049 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1143-1_0_4_load_53 | 63 | 0.0038893 | 0.00097474 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1143-1_0_4_load_54 | 64 | 0.0019511 | 0.00048899 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1143-1_0_4_load_55 | 65 | 0.0048925 | 0.0012262 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1143-1_0_4_load_56 | 66 | 0.003248 | 0.00081402 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1143-1_0_4_load_89 | 67 | 0.0019688 | 0.00049343 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1143-1_0_4_load_90 | 68 | 0.0013359 | 0.0003348 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1143-1_0_4_load_57 | 69 | 0.0023657 | 0.00059289 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1143-1_0_4_load_58 | 70 | 0.0023793 | 0.00059632 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1143-1_0_4_load_59 | 71 | 0.0075366 | 0.0018888 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1143-1_0_4_load_60 | 72 | 0.0031761 | 0.00079599 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1143-1_0_4_load_61 | 73 | 0.0019758 | 0.00049518 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1143-1_0_4_load_63 | 74 | 0.0017333 | 0.0004344 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1143-1_0_4_load_78 | 75 | 0.0021543 | 0.00053992 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1143-1_0_4_load_77 | 76 | 0.0019448 | 0.00048742 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1143-1_0_4_load_72 | 77 | 0.0017563 | 0.00044017 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1143-1_0_4_load_69 | 78 | 0.00027171 | 6.8097e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1143-1_0_4_load_70 | 79 | 0.00037686 | 9.445e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1143-1_0_4_load_123 | 80 | 0.0019516 | 0.00048912 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1143-1_0_4_load_121 | 81 | 0.0021157 | 0.00053025 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1143-1_0_4_load_71 | 82 | 0.0044946 | 0.0011265 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1143-1_0_4_load_76 | 85 | 0.0033019 | 0.00082753 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1143-1_0_4_load_95 | 86 | 0.0021794 | 0.00054621 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1143-1_0_4_load_102 | 87 | 0.0017925 | 0.00044923 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1143-1_0_4_load_119 | 88 | 0.0016974 | 0.0004254 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1143-1_0_4_load_93 | 89 | 0.0020225 | 0.00050688 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1143-1_0_4_load_103 | 90 | 0.0016648 | 0.00041724 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1143-1_0_4_load_79 | 92 | 0.00089119 | 0.00022335 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1143-1_0_4_load_80 | 93 | 0.00089119 | 0.00022335 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1143-1_0_4_load_92 | 94 | 0.0017141 | 0.00042959 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1143-1_0_4_load_83 | 95 | 0.0050958 | 0.0012771 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1143-1_0_4_load_88 | 97 | 0.0017185 | 0.00043069 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1143-1_0_4_load_110 | 98 | 0.0027182 | 0.00068124 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1143-1_0_4_load_122 | 99 | 0.0016343 | 0.0004096 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1143-1_0_4_load_109 | 100 | 0.0020308 | 0.00050897 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1143-1_0_4_load_94 | 101 | 0.003445 | 0.00086339 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1143-1_0_4_load_107 | 102 | 0.0020801 | 0.00052133 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1143-1_0_4_load_96 | 103 | 0.0030756 | 0.00077083 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1143-1_0_4_load_108 | 104 | 0.0019559 | 0.00049019 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1143-1_0_4_load_116 | 105 | 0.0020038 | 0.0005022 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1143-1_0_4_load_117 | 106 | 0.0032138 | 0.00080545 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1143-1_0_4_load_118 | 107 | 0.00087509 | 0.00021932 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1143-1_0_4_load_97 | 108 | 0.0016935 | 0.00042444 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1143-1_0_4_load_98 | 109 | 0.0022137 | 0.00055481 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1143-1_0_4_load_99 | 110 | 0.0019426 | 0.00048685 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1143-1_0_4_load_100 | 111 | 0.0026298 | 0.00065908 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1143-1_0_4_load_101 | 112 | 0.001651 | 0.00041378 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1143-1_0_4_load_104 | 113 | 0.0029806 | 0.00074702 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1143-1_0_4_load_106 | 114 | 0.0028079 | 0.00070373 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1143-1_0_4_load_114 | 115 | 0.00084595 | 0.00021201 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1143-1_0_4_load_112 | 116 | 0.0016161 | 0.00040504 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1143-1_0_4_load_111 | 117 | 0.0021507 | 0.00053901 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1143-1_0_4_load_113 | 118 | 0.0017471 | 0.00043785 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1143-1_0_4_load_115 | 119 | 0.0021073 | 0.00052813 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1143-1_0_4_load_120 | 120 | 0.0019041 | 0.0004772 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 94 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1143-1_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.031223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1143-1_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.074189 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1143-1_0_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.003674 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1143-1_0_4_line_3 | NAYY 4x150 SE | 3 | 4 | 0.031308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1143-1_0_4_line_4 | NAYY 4x150 SE | 3 | 5 | 0.080028 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1143-1_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.010402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1143-1_0_4_line_6 | NAYY 4x150 SE | 4 | 7 | 0.093976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1143-1_0_4_line_7 | NAYY 4x150 SE | 5 | 8 | 0.019956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1143-1_0_4_line_8 | NAYY 4x150 SE | 6 | 39 | 0.013799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1143-1_0_4_line_9 | NAYY 4x150 SE | 6 | 40 | 0.026781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1143-1_0_4_line_10 | NAYY 4x150 SE | 7 | 41 | 0.0053566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1143-1_0_4_line_11 | NAYY 4x150 SE | 8 | 29 | 0.022199 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1143-1_0_4_line_12 | NAYY 4x150 SE | 9 | 10 | 0.0054437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1143-1_0_4_line_13 | NAYY 4x150 SE | 9 | 11 | 0.01693 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1143-1_0_4_line_14 | NAYY 4x150 SE | 11 | 12 | 0.0010467 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1143-1_0_4_line_15 | NAYY 4x150 SE | 12 | 13 | 0.0075318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1143-1_0_4_line_16 | NAYY 4x150 SE | 13 | 14 | 0.011971 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1143-1_0_4_line_17 | NAYY 4x150 SE | 14 | 17 | 0.043125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1143-1_0_4_line_18 | NAYY 4x150 SE | 15 | 16 | 0.037371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1143-1_0_4_line_19 | NAYY 4x150 SE | 16 | 17 | 0.052498 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1143-1_0_4_line_20 | NAYY 4x150 SE | 16 | 18 | 0.013959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1143-1_0_4_line_21 | NAYY 4x150 SE | 17 | 19 | 0.017944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1143-1_0_4_line_22 | NAYY 4x150 SE | 18 | 21 | 0.01526 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1143-1_0_4_line_23 | NAYY 4x150 SE | 18 | 23 | 0.03911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_1143-1_0_4_line_24 | NAYY 4x150 SE | 19 | 24 | 0.00051286 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1143-1_0_4_line_25 | NAYY 4x150 SE | 20 | 21 | 0.01519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1143-1_0_4_line_26 | NAYY 4x150 SE | 20 | 22 | 0.0075384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1143-1_0_4_line_27 | NAYY 4x150 SE | 21 | 25 | 0.04251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1143-1_0_4_line_28 | NAYY 4x150 SE | 23 | 26 | 0.022476 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
29 | LV_1143-1_0_4_line_29 | NAYY 4x150 SE | 24 | 27 | 0.020387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1143-1_0_4_line_30 | NAYY 4x150 SE | 25 | 48 | 0.039239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1143-1_0_4_line_31 | NAYY 4x150 SE | 26 | 53 | 0.020637 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1143-1_0_4_line_32 | NAYY 4x150 SE | 27 | 28 | 0.0021387 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1143-1_0_4_line_33 | NAYY 4x150 SE | 29 | 30 | 0.0005702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1143-1_0_4_line_34 | NAYY 4x150 SE | 30 | 31 | 0.021738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1143-1_0_4_line_35 | NAYY 4x150 SE | 31 | 32 | 0.021844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1143-1_0_4_line_36 | NAYY 4x150 SE | 33 | 34 | 0.017179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1143-1_0_4_line_37 | NAYY 4x150 SE | 33 | 35 | 0.014369 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1143-1_0_4_line_38 | NAYY 4x150 SE | 34 | 36 | 0.05016 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1143-1_0_4_line_39 | NAYY 4x150 SE | 36 | 37 | 0.20897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1143-1_0_4_line_40 | NAYY 4x150 SE | 37 | 38 | 0.022488 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1143-1_0_4_line_41 | NAYY 4x150 SE | 38 | 42 | 0.04314 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1143-1_0_4_line_42 | NAYY 4x150 SE | 39 | 57 | 0.05317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1143-1_0_4_line_43 | NAYY 4x150 SE | 40 | 58 | 0.01973 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1143-1_0_4_line_44 | NAYY 4x150 SE | 41 | 56 | 0.028657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1143-1_0_4_line_45 | NAYY 4x150 SE | 42 | 43 | 0.040624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1143-1_0_4_line_46 | NAYY 4x150 SE | 43 | 44 | 0.11522 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1143-1_0_4_line_47 | NAYY 4x150 SE | 44 | 47 | 0.0027956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1143-1_0_4_line_48 | NAYY 4x150 SE | 45 | 46 | 0.0061597 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1143-1_0_4_line_49 | NAYY 4x150 SE | 46 | 78 | 0.014121 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1143-1_0_4_line_50 | NAYY 4x150 SE | 47 | 59 | 0.0062671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1143-1_0_4_line_51 | NAYY 4x150 SE | 48 | 49 | 0.0047627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1143-1_0_4_line_52 | NAYY 4x150 SE | 49 | 50 | 0.011202 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_1143-1_0_4_line_53 | NAYY 4x150 SE | 50 | 51 | 0.031976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
54 | LV_1143-1_0_4_line_54 | NAYY 4x150 SE | 50 | 52 | 0.022056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1143-1_0_4_line_55 | NAYY 4x150 SE | 51 | 77 | 0.010108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1143-1_0_4_line_56 | NAYY 4x150 SE | 52 | 72 | 0.0038729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
57 | LV_1143-1_0_4_line_57 | NAYY 4x150 SE | 53 | 54 | 0.02614 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_1143-1_0_4_line_58 | NAYY 4x150 SE | 54 | 55 | 0.016984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_1143-1_0_4_line_59 | NAYY 4x150 SE | 55 | 56 | 0.018995 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1143-1_0_4_line_60 | NAYY 4x150 SE | 57 | 71 | 0.010072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1143-1_0_4_line_61 | NAYY 4x150 SE | 58 | 95 | 0.011114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1143-1_0_4_line_62 | NAYY 4x150 SE | 59 | 60 | 0.018912 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1143-1_0_4_line_63 | NAYY 4x150 SE | 60 | 61 | 0.0076502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1143-1_0_4_line_64 | NAYY 4x150 SE | 61 | 62 | 0.010561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1143-1_0_4_line_65 | NAYY 4x150 SE | 62 | 96 | 0.033877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1143-1_0_4_line_66 | NAYY 4x150 SE | 62 | 97 | 0.014172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1143-1_0_4_line_67 | NAYY 4x150 SE | 63 | 64 | 0.012946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1143-1_0_4_line_68 | NAYY 4x150 SE | 63 | 65 | 0.0080982 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1143-1_0_4_line_69 | NAYY 4x150 SE | 64 | 66 | 0.019683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1143-1_0_4_line_70 | NAYY 4x150 SE | 66 | 67 | 0.011788 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1143-1_0_4_line_71 | NAYY 4x150 SE | 67 | 68 | 0.021646 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1143-1_0_4_line_72 | NAYY 4x150 SE | 68 | 94 | 0.0077257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1143-1_0_4_line_73 | NAYY 4x150 SE | 69 | 70 | 0.020757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1143-1_0_4_line_74 | NAYY 4x150 SE | 70 | 71 | 0.034284 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1143-1_0_4_line_75 | NAYY 4x150 SE | 72 | 73 | 0.016215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_1143-1_0_4_line_76 | NAYY 4x150 SE | 73 | 74 | 0.020146 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1143-1_0_4_line_77 | NAYY 4x150 SE | 74 | 75 | 0.001859 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_1143-1_0_4_line_78 | NAYY 4x150 SE | 75 | 76 | 0.016519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
79 | LV_1143-1_0_4_line_79 | NAYY 4x150 SE | 76 | 92 | 0.0041164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
80 | LV_1143-1_0_4_line_80 | NAYY 4x150 SE | 77 | 82 | 0.015458 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1143-1_0_4_line_81 | NAYY 4x150 SE | 78 | 79 | 0.02296 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1143-1_0_4_line_82 | NAYY 4x150 SE | 79 | 80 | 0.028615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1143-1_0_4_line_83 | NAYY 4x150 SE | 80 | 81 | 0.0023532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1143-1_0_4_line_84 | NAYY 4x150 SE | 81 | 120 | 0.036311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1143-1_0_4_line_85 | NAYY 4x150 SE | 82 | 83 | 0.011824 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1143-1_0_4_line_86 | NAYY 4x150 SE | 83 | 84 | 0.017388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1143-1_0_4_line_87 | NAYY 4x150 SE | 83 | 85 | 0.0049635 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1143-1_0_4_line_88 | NAYY 4x150 SE | 84 | 86 | 0.019513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1143-1_0_4_line_89 | NAYY 4x150 SE | 84 | 87 | 0.017595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1143-1_0_4_line_90 | NAYY 4x150 SE | 85 | 88 | 0.030923 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1143-1_0_4_line_91 | NAYY 4x150 SE | 86 | 89 | 0.016337 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1143-1_0_4_line_92 | NAYY 4x150 SE | 87 | 90 | 0.0014623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1143-1_0_4_line_93 | NAYY 4x150 SE | 88 | 91 | 0.015322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1143-1_0_4_line_94 | NAYY 4x150 SE | 89 | 101 | 0.018472 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1143-1_0_4_line_95 | NAYY 4x150 SE | 89 | 102 | 0.025346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1143-1_0_4_line_96 | NAYY 4x150 SE | 91 | 112 | 0.019205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1143-1_0_4_line_97 | NAYY 4x150 SE | 92 | 93 | 0.0069069 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
98 | LV_1143-1_0_4_line_98 | NAYY 4x150 SE | 93 | 94 | 0.011117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_1143-1_0_4_line_99 | NAYY 4x150 SE | 96 | 98 | 0.0024607 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1143-1_0_4_line_100 | NAYY 4x150 SE | 97 | 99 | 0.0089412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1143-1_0_4_line_101 | NAYY 4x150 SE | 98 | 100 | 0.011362 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1143-1_0_4_line_102 | NAYY 4x150 SE | 100 | 113 | 0.015754 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1143-1_0_4_line_103 | NAYY 4x150 SE | 101 | 103 | 0.0082332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1143-1_0_4_line_104 | NAYY 4x150 SE | 102 | 104 | 0.02539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1143-1_0_4_line_105 | NAYY 4x150 SE | 103 | 106 | 0.01903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1143-1_0_4_line_106 | NAYY 4x150 SE | 104 | 105 | 0.00083613 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1143-1_0_4_line_107 | NAYY 4x150 SE | 106 | 107 | 0.004616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1143-1_0_4_line_108 | NAYY 4x150 SE | 107 | 115 | 0.0016931 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1143-1_0_4_line_109 | NAYY 4x150 SE | 108 | 109 | 0.0072683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1143-1_0_4_line_110 | NAYY 4x150 SE | 108 | 110 | 0.017732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1143-1_0_4_line_111 | NAYY 4x150 SE | 109 | 111 | 0.022454 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1143-1_0_4_line_112 | NAYY 4x150 SE | 110 | 112 | 0.0078656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1143-1_0_4_line_113 | NAYY 4x150 SE | 111 | 113 | 0.0040884 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1143-1_0_4_line_114 | NAYY 4x150 SE | 114 | 115 | 0.030221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1143-1_0_4_line_115 | NAYY 4x150 SE | 115 | 116 | 0.033922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1143-1_0_4_line_116 | NAYY 4x150 SE | 116 | 117 | 0.0028246 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1143-1_0_4_line_117 | NAYY 4x150 SE | 117 | 118 | 0.014679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1143-1_0_4_line_118 | NAYY 4x150 SE | 118 | 119 | 0.012578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
119 | LV_1143-1_0_4_line_119 | NAYY 4x150 SE | 119 | 120 | 0.013359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1143-1_0_4_trafo_92 | 0.25 MVA 20/0.4 kV | 121 | 94 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2641398.0523 | 1225580.8847 | 2641426.2321 | 1225594.331
1 | 2641331.0951 | 1225548.9355 | 2641398.0523 | 1225580.8847
2 | 2641327.5468 | 1225547.9436 | 2641331.0951 | 1225548.9355
3 | 2641343.9315 | 1225521.2411 | 2641327.5468 | 1225547.9436
4 | 2641327.5468 | 1225547.9436 | 2641287.5555 | 1225617.2626
5 | 2641334.6481 | 1225516.496 | 2641343.9315 | 1225521.2411
6 | 2641343.9315 | 1225521.2411 | 2641346.7476 | 1225516.3354 | 2641390.7265 | 1225439.744
7 | 2641277.5833 | 1225634.5481 | 2641287.5555 | 1225617.2626
8 | 2641334.6481 | 1225516.496 | 2641334.4899 | 1225509.813 | 2641337.1761 | 1225503.9503 | 2641337.5934 | 1225503.4326
9 | 2641334.6481 | 1225516.496 | 2641313.7199 | 1225514.1271 | 2641308.5202 | 1225511.745
10 | 2641393.3938 | 1225435.0988 | 2641390.7265 | 1225439.744
11 | 2641266.4826 | 1225653.7724 | 2641267.2711 | 1225652.4227 | 2641277.5833 | 1225634.5481
12 | 2641557.335 | 1225380.0163 | 2641555.3222 | 1225385.0742
13 | 2641557.335 | 1225380.0163 | 2641563.5951 | 1225364.2864
14 | 2641563.5951 | 1225364.2864 | 2641563.9821 | 1225363.3139
15 | 2641563.9821 | 1225363.3139 | 2641566.7671 | 1225356.3159
16 | 2641571.1936 | 1225345.1933 | 2641566.7671 | 1225356.3159
17 | 2641571.1936 | 1225345.1933 | 2641557.2595 | 1225335.5458 | 2641535.6679 | 1225320.5972
18 | 2641491.6123 | 1225291.8505 | 2641491.0529 | 1225292.7138 | 2641487.9341 | 1225297.5172 | 2641487.3823 | 1225298.3695 | 2641482.7762 | 1225299.0378 | 2641479.3243 | 1225300.5146 | 2641477.1807 | 1225302.4342 | 2641467.6534 | 1225318.0743
19 | 2641535.6679 | 1225320.5972 | 2641491.6123 | 1225291.8505
20 | 2641479.4398 | 1225285.0171 | 2641482.4905 | 1225286.7283 | 2641491.6123 | 1225291.8505
21 | 2641535.6679 | 1225320.5972 | 2641526.2845 | 1225335.892
22 | 2641486.9993 | 1225271.7506 | 2641479.4398 | 1225285.0171
23 | 2641479.4398 | 1225285.0171 | 2641459.9386 | 1225318.9189
24 | 2641526.2845 | 1225335.892 | 2641526.0163 | 1225336.3291
25 | 2641486.9993 | 1225271.7506 | 2641494.6111 | 1225258.5956
26 | 2641494.6111 | 1225258.5956 | 2641498.3949 | 1225252.0756
27 | 2641486.9993 | 1225271.7506 | 2641478.9018 | 1225267.5806 | 2641470.9727 | 1225267.5253 | 2641463.4384 | 1225268.4846 | 2641447.6069 | 1225276.7891
28 | 2641448.7768 | 1225338.4276 | 2641459.4577 | 1225319.7547 | 2641459.9386 | 1225318.9189
29 | 2641515.3553 | 1225353.7063 | 2641526.0163 | 1225336.3291
30 | 2641447.6069 | 1225276.7891 | 2641412.8583 | 1225295.0168
31 | 2641448.7768 | 1225338.4276 | 2641438.5304 | 1225356.3407
32 | 2641515.3553 | 1225353.7063 | 2641514.2369 | 1225355.5292
33 | 2641266.195 | 1225654.2647 | 2641266.4826 | 1225653.7724
34 | 2641255.2297 | 1225673.0347 | 2641266.195 | 1225654.2647
35 | 2641255.2297 | 1225673.0347 | 2641244.211 | 1225691.8961
36 | 2640780.6458 | 1225449.4369 | 2640792.5556 | 1225461.4702 | 2640792.7202 | 1225461.6569
37 | 2640780.6458 | 1225449.4369 | 2640780.6458 | 1225449.4369 | 2640780.8623 | 1225446.6034 | 2640782.5025 | 1225443.9797 | 2640786.9789 | 1225443.3988 | 2640790.8692 | 1225443.8732
38 | 2640823.798 | 1225500.8081 | 2640822.6486 | 1225498.1764 | 2640818.2236 | 1225491.253 | 2640805.5161 | 1225476.1679 | 2640792.7202 | 1225461.6569
39 | 2641032.5327 | 1225490.9029 | 2640823.798 | 1225500.8081
40 | 2641032.5327 | 1225490.9029 | 2641050.6321 | 1225504.2487
41 | 2641084.4854 | 1225530.8464 | 2641064.827 | 1225517.0524 | 2641051.9536 | 1225505.2232 | 2641050.6321 | 1225504.2487
42 | 2641354.0355 | 1225459.1513 | 2641354.8582 | 1225459.6572 | 2641358.1599 | 1225462.3262 | 2641359.3625 | 1225465.9812 | 2641359.3646 | 1225470.0504 | 2641349.6856 | 1225488.4277 | 2641337.5934 | 1225503.4326
43 | 2641290.5831 | 1225503.5274 | 2641308.5202 | 1225511.745
44 | 2641393.3938 | 1225435.0988 | 2641407.6654 | 1225410.2485
45 | 2641117.3587 | 1225554.4486 | 2641116.0155 | 1225552.4715 | 2641089.9179 | 1225534.6584 | 2641084.4854 | 1225530.8464
46 | 2641208.4703 | 1225483.9231 | 2641117.3587 | 1225554.4486
47 | 2641210.1866 | 1225481.7162 | 2641208.4703 | 1225483.9231
48 | 2641189.4481 | 1225446.4395 | 2641187.1599 | 1225452.1585
49 | 2641194.6936 | 1225433.3293 | 2641189.4481 | 1225446.4395
50 | 2641210.1866 | 1225481.7162 | 2641214.0339 | 1225476.769
51 | 2641412.8583 | 1225295.0168 | 2641408.6407 | 1225297.2292
52 | 2641398.7206 | 1225302.4329 | 2641408.6407 | 1225297.2292
53 | 2641398.7206 | 1225302.4329 | 2641374.5886 | 1225316.9852 | 2641370.9797 | 1225318.1609
54 | 2641398.7206 | 1225302.4329 | 2641395.4281 | 1225312.594 | 2641389.6723 | 1225322.4046
55 | 2641362.1347 | 1225314.4386 | 2641362.5927 | 1225315.2787 | 2641364.7717 | 1225316.9837 | 2641368.0087 | 1225318.0624 | 2641370.9797 | 1225318.1609
56 | 2641387.7125 | 1225325.7451 | 2641389.6723 | 1225322.4046
57 | 2641438.5304 | 1225356.3407 | 2641425.5516 | 1225379.0307
58 | 2641417.1188 | 1225393.7733 | 2641425.5516 | 1225379.0307
59 | 2641417.1188 | 1225393.7733 | 2641415.0483 | 1225397.393 | 2641407.6654 | 1225410.2485
60 | 2641345.4559 | 1225453.8758 | 2641354.0355 | 1225459.1513
61 | 2641280.4792 | 1225498.8985 | 2641290.5831 | 1225503.5274
62 | 2641214.0339 | 1225476.769 | 2641225.6437 | 1225461.8405
63 | 2641230.3401 | 1225455.8015 | 2641225.6437 | 1225461.8405
64 | 2641236.8234 | 1225447.4649 | 2641230.3401 | 1225455.8015
65 | 2641257.6355 | 1225420.6927 | 2641236.8234 | 1225447.4649
66 | 2641236.8234 | 1225447.4649 | 2641234.3217 | 1225445.3018 | 2641224.2309 | 1225441.2751
67 | 2641290.9579 | 1225440.8323 | 2641299.6673 | 1225431.2538
68 | 2641285.5099 | 1225446.8239 | 2641290.9579 | 1225440.8323
69 | 2641312.9092 | 1225416.6905 | 2641299.6673 | 1225431.2538
70 | 2641312.9092 | 1225416.6905 | 2641320.8395 | 1225407.9688
71 | 2641335.4016 | 1225391.9536 | 2641320.8395 | 1225407.9688
72 | 2641340.599 | 1225386.2376 | 2641335.4016 | 1225391.9536
73 | 2641343.5219 | 1225414.5833 | 2641332.4579 | 1225432.146
74 | 2641345.4559 | 1225453.8758 | 2641326.22 | 1225442.0478 | 2641332.4579 | 1225432.146
75 | 2641387.7125 | 1225325.7451 | 2641379.8242 | 1225339.1906 | 2641379.4367 | 1225339.6827
76 | 2641379.4367 | 1225339.6827 | 2641366.9735 | 1225355.5108
77 | 2641366.9735 | 1225355.5108 | 2641365.8234 | 1225356.9713
78 | 2641355.494 | 1225369.8562 | 2641356.8645 | 1225368.3489 | 2641365.8234 | 1225356.9713
79 | 2641352.7247 | 1225372.9018 | 2641355.494 | 1225369.8562
80 | 2641357.5262 | 1225299.7574 | 2641360.7064 | 1225311.819 | 2641362.1347 | 1225314.4386
81 | 2641194.6936 | 1225433.3293 | 2641194.9988 | 1225432.5665 | 2641197.6427 | 1225428.4267 | 2641207.819 | 1225414.528
82 | 2641207.819 | 1225414.528 | 2641224.7239 | 1225391.4398
83 | 2641226.1141 | 1225389.5412 | 2641224.7239 | 1225391.4398
84 | 2641226.1141 | 1225389.5412 | 2641226.5248 | 1225388.9803 | 2641247.9848 | 1225360.5555
85 | 2641350.2535 | 1225290.9671 | 2641352.8593 | 1225292.3305 | 2641355.6643 | 1225295.5852 | 2641357.2645 | 1225298.765 | 2641357.5262 | 1225299.7574
86 | 2641350.2535 | 1225290.9671 | 2641359.1962 | 1225276.0423
87 | 2641350.2535 | 1225290.9671 | 2641347.3905 | 1225295.0217
88 | 2641359.1962 | 1225276.0423 | 2641343.1575 | 1225264.9279
89 | 2641359.1962 | 1225276.0423 | 2641369.731 | 1225261.9502
90 | 2641347.3905 | 1225295.0217 | 2641329.5543 | 1225320.2824
91 | 2641328.5351 | 1225261.0283 | 2641331.945 | 1225259.4542 | 2641338.8414 | 1225261.9369 | 2641343.1575 | 1225264.9279
92 | 2641369.731 | 1225261.9502 | 2641370.6065 | 1225260.7791
93 | 2641320.7168 | 1225332.7987 | 2641329.5543 | 1225320.2824
94 | 2641328.5351 | 1225261.0283 | 2641325.0167 | 1225262.6525 | 2641317.237 | 1225269.4805 | 2641314.3876 | 1225272.6283
95 | 2641328.5351 | 1225261.0283 | 2641312.4144 | 1225241.4701
96 | 2641320.7168 | 1225332.7987 | 2641309.4499 | 1225348.351
97 | 2641352.7247 | 1225372.9018 | 2641348.0782 | 1225378.0121
98 | 2641340.599 | 1225386.2376 | 2641348.0782 | 1225378.0121
99 | 2641257.6355 | 1225420.6927 | 2641259.0608 | 1225418.6868
100 | 2641224.2309 | 1225441.2751 | 2641215.9265 | 1225437.9613
101 | 2641265.6417 | 1225409.4253 | 2641259.0608 | 1225418.6868
102 | 2641274.7668 | 1225396.5833 | 2641265.6417 | 1225409.4253
103 | 2641308.8625 | 1225278.7323 | 2641314.3876 | 1225272.6283
104 | 2641331.0453 | 1225224.2238 | 2641318.0755 | 1225236.0438 | 2641312.4144 | 1225241.4701
105 | 2641308.8625 | 1225278.7323 | 2641296.0918 | 1225292.8409
106 | 2641331.0453 | 1225224.2238 | 2641331.6633 | 1225223.6606
107 | 2641292.9941 | 1225296.2631 | 2641296.0918 | 1225292.8409
108 | 2641292.9941 | 1225296.2631 | 2641291.8578 | 1225297.5184
109 | 2641294.4325 | 1225369.0802 | 2641290.1683 | 1225374.9662
110 | 2641294.4325 | 1225369.0802 | 2641304.8353 | 1225354.7207
111 | 2641290.1683 | 1225374.9662 | 2641288.0192 | 1225377.9328 | 2641277.1349 | 1225393.2506
112 | 2641304.8353 | 1225354.7207 | 2641309.4499 | 1225348.351
113 | 2641274.7668 | 1225396.5833 | 2641277.1349 | 1225393.2506
114 | 2641291.8578 | 1225297.5184 | 2641262.2516 | 1225291.4555
115 | 2641291.8578 | 1225297.5184 | 2641284.1743 | 1225306.0068 | 2641270.9238 | 1225322.3249 | 2641270.2625 | 1225323.6182
116 | 2641268.9765 | 1225326.1331 | 2641270.2625 | 1225323.6182
117 | 2641268.9765 | 1225326.1331 | 2641268.2726 | 1225327.5097 | 2641262.0683 | 1225335.6384 | 2641260.9962 | 1225338.341
118 | 2641256.0339 | 1225349.8941 | 2641256.0339 | 1225349.8941 | 2641258.8356 | 1225343.7876 | 2641260.9962 | 1225338.341
119 | 2641256.0339 | 1225349.8941 | 2641247.9848 | 1225360.5555

## bus_geodata
| x | y | coords
0 | 2641398.0523 | 1225580.8847
1 | 2641426.2321 | 1225594.331
2 | 2641331.0951 | 1225548.9355
3 | 2641327.5468 | 1225547.9436
4 | 2641343.9315 | 1225521.241
5 | 2641287.5555 | 1225617.2626
6 | 2641334.6481 | 1225516.496
7 | 2641390.7265 | 1225439.744
8 | 2641277.5833 | 1225634.5481
9 | 2641557.335 | 1225380.0163
10 | 2641555.3222 | 1225385.0742
11 | 2641563.5951 | 1225364.2864
12 | 2641563.9821 | 1225363.3139
13 | 2641566.7671 | 1225356.3159
14 | 2641571.1936 | 1225345.1933
15 | 2641467.6534 | 1225318.0743
16 | 2641491.6123 | 1225291.8505
17 | 2641535.6679 | 1225320.5972
18 | 2641479.4398 | 1225285.0171
19 | 2641526.2845 | 1225335.892
20 | 2641494.6111 | 1225258.5956
21 | 2641486.9993 | 1225271.7506
22 | 2641498.3949 | 1225252.0756
23 | 2641459.9386 | 1225318.9189
24 | 2641526.0163 | 1225336.3291
25 | 2641447.6069 | 1225276.7891
26 | 2641448.7768 | 1225338.4276
27 | 2641515.3553 | 1225353.7063
28 | 2641514.2369 | 1225355.5292
29 | 2641266.4826 | 1225653.7724
30 | 2641266.195 | 1225654.2647
31 | 2641255.2297 | 1225673.0347
32 | 2641244.211 | 1225691.8961
33 | 2640780.6458 | 1225449.4369
34 | 2640792.7202 | 1225461.6569
35 | 2640790.8692 | 1225443.8732
36 | 2640823.798 | 1225500.8081
37 | 2641032.5327 | 1225490.9029
38 | 2641050.6321 | 1225504.2487
39 | 2641337.5934 | 1225503.4326
40 | 2641308.5202 | 1225511.745
41 | 2641393.3938 | 1225435.0988
42 | 2641084.4854 | 1225530.8464
43 | 2641117.3587 | 1225554.4486
44 | 2641208.4703 | 1225483.9231
45 | 2641187.1599 | 1225452.1585
46 | 2641189.4481 | 1225446.4395
47 | 2641210.1866 | 1225481.7162
48 | 2641412.8583 | 1225295.0168
49 | 2641408.6407 | 1225297.2292
50 | 2641398.7206 | 1225302.4329
51 | 2641370.9797 | 1225318.1609
52 | 2641389.6723 | 1225322.4046
53 | 2641438.5304 | 1225356.3407
54 | 2641425.5516 | 1225379.0307
55 | 2641417.1188 | 1225393.7733
56 | 2641407.6654 | 1225410.2485
57 | 2641354.0355 | 1225459.1513
58 | 2641290.5831 | 1225503.5274
59 | 2641214.0339 | 1225476.769
60 | 2641225.6437 | 1225461.8405
61 | 2641230.3401 | 1225455.8015
62 | 2641236.8234 | 1225447.4649
63 | 2641290.9579 | 1225440.8323
64 | 2641299.6673 | 1225431.2538
65 | 2641285.5099 | 1225446.8239
66 | 2641312.9092 | 1225416.6905
67 | 2641320.8395 | 1225407.9688
68 | 2641335.4016 | 1225391.9536
69 | 2641343.5219 | 1225414.5833
70 | 2641332.4579 | 1225432.146
71 | 2641345.4559 | 1225453.8758
72 | 2641387.7125 | 1225325.7451
73 | 2641379.4367 | 1225339.6827
74 | 2641366.9735 | 1225355.5108
75 | 2641365.8234 | 1225356.9713
76 | 2641355.494 | 1225369.8562
77 | 2641362.1347 | 1225314.4386
78 | 2641194.6936 | 1225433.3293
79 | 2641207.819 | 1225414.528
80 | 2641224.7239 | 1225391.4398
81 | 2641226.1141 | 1225389.5412
82 | 2641357.5262 | 1225299.7574
83 | 2641350.2535 | 1225290.9671
84 | 2641359.1962 | 1225276.0423
85 | 2641347.3905 | 1225295.0217
86 | 2641343.1575 | 1225264.9279
87 | 2641369.731 | 1225261.9502
88 | 2641329.5543 | 1225320.2824
89 | 2641328.5351 | 1225261.0283
90 | 2641370.6065 | 1225260.7791
91 | 2641320.7168 | 1225332.7987
92 | 2641352.7247 | 1225372.9018
93 | 2641348.0782 | 1225378.0121
94 | 2641340.599 | 1225386.2376
95 | 2641280.4792 | 1225498.8985
96 | 2641257.6355 | 1225420.6927
97 | 2641224.2309 | 1225441.2751
98 | 2641259.0608 | 1225418.6868
99 | 2641215.9265 | 1225437.9613
100 | 2641265.6417 | 1225409.4253
101 | 2641314.3876 | 1225272.6284
102 | 2641312.4144 | 1225241.4701
103 | 2641308.8625 | 1225278.7323
104 | 2641331.0453 | 1225224.2238
105 | 2641331.6633 | 1225223.6606
106 | 2641296.0918 | 1225292.8409
107 | 2641292.9941 | 1225296.2631
108 | 2641294.4325 | 1225369.0802
109 | 2641290.1683 | 1225374.9662
110 | 2641304.8353 | 1225354.7207
111 | 2641277.1349 | 1225393.2506
112 | 2641309.4499 | 1225348.351
113 | 2641274.7668 | 1225396.5833
114 | 2641262.2516 | 1225291.4555
115 | 2641291.8578 | 1225297.5184
116 | 2641270.2625 | 1225323.6182
117 | 2641268.9765 | 1225326.1331
118 | 2641260.9962 | 1225338.341
119 | 2641256.0339 | 1225349.8941
120 | 2641247.9848 | 1225360.5555
121 | 2641285.5099 | 1225446.8239

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97261 | -0.19284 | 0.012333 | 0.0030908
1 | 0.97259 | -0.19297 | 0.00037314 | 9.3517e-05
2 | 0.97399 | -0.18291 | 0 | 0
3 | 0.97406 | -0.18241 | 0 | 0
4 | 0.97502 | -0.17546 | 0 | 0
5 | 0.97307 | -0.18951 | 0.0023829 | 0.00059721
6 | 0.9746 | -0.17848 | 0 | 0
7 | 0.97838 | -0.15147 | 0.0026925 | 0.00067479
8 | 0.97289 | -0.19078 | 0.0013043 | 0.00032689
9 | 0.98298 | -0.11883 | 0.00073408 | 0.00018398
10 | 0.98298 | -0.11885 | 0.00049284 | 0.00012352
11 | 0.98301 | -0.11861 | 0.00042727 | 0.00010708
12 | 0.98301 | -0.11859 | 0.0002919 | 7.3156e-05
13 | 0.98303 | -0.11844 | 0.00019819 | 4.9671e-05
14 | 0.98307 | -0.11818 | 0 | 0
15 | 0.9827 | -0.12081 | 0.014762 | 0.0036997
16 | 0.9835 | -0.11512 | 0 | 0
17 | 0.9832 | -0.11722 | 0 | 0
18 | 0.98388 | -0.11243 | 0 | 0
19 | 0.98316 | -0.11754 | 0.0004066 | 0.0001019
20 | 0.98458 | -0.10747 | 0 | 0
21 | 0.98461 | -0.10721 | 0 | 0
22 | 0.98456 | -0.1076 | 0.0016676 | 0.00041793
23 | 0.98234 | -0.12332 | 0.011474 | 0.0028757
24 | 0.98316 | -0.11755 | 0.00040022 | 0.0001003
25 | 0.9867 | -0.092476 | 0.0014403 | 0.00036098
26 | 0.98158 | -0.1287 | 0.0047818 | 0.0011984
27 | 0.98313 | -0.11774 | 0.00039772 | 9.9677e-05
28 | 0.98313 | -0.11775 | 0.0005205 | 0.00013045
29 | 0.97274 | -0.19189 | 0.0011396 | 0.00028562
30 | 0.97274 | -0.19191 | 0.00099383 | 0.00024908
31 | 0.97265 | -0.1925 | 0.0012603 | 0.00031586
32 | 0.97261 | -0.19281 | 0.0013277 | 0.00033275
33 | 0.97169 | -0.19968 | 0.00045634 | 0.00011437
34 | 0.97174 | -0.19933 | 0.00026995 | 6.7656e-05
35 | 0.97166 | -0.1999 | 0.0014657 | 0.00036735
36 | 0.9719 | -0.19816 | 0 | 0
37 | 0.97257 | -0.19329 | 0 | 0
38 | 0.97265 | -0.19276 | 0.00048206 | 0.00012081
39 | 0.97423 | -0.18118 | 0.0045574 | 0.0011422
40 | 0.97425 | -0.18103 | 0.00048794 | 0.00012229
41 | 0.97851 | -0.15051 | 0 | 0
42 | 0.97282 | -0.19153 | 0.0025438 | 0.00063752
43 | 0.97313 | -0.18928 | 0 | 0
44 | 0.97401 | -0.1829 | 0.0004688 | 0.00011749
45 | 0.97598 | -0.16877 | 0.00027282 | 6.8374e-05
46 | 0.97598 | -0.16876 | 0.00034863 | 8.7376e-05
47 | 0.97403 | -0.18273 | 0.0018887 | 0.00047335
48 | 0.98866 | -0.078736 | 0.0064456 | 0.0016154
49 | 0.98891 | -0.076967 | 0.0029764 | 0.00074596
50 | 0.98952 | -0.072697 | 0 | 0
51 | 0.9874 | -0.087527 | 0.00165 | 0.00041354
52 | 0.99169 | -0.057524 | 0.0021393 | 0.00053616
53 | 0.98093 | -0.13331 | 0.0047602 | 0.001193
54 | 0.98017 | -0.13872 | 0.0056983 | 0.0014281
55 | 0.97972 | -0.14191 | 0.0013492 | 0.00033815
56 | 0.97923 | -0.14539 | 0.0012862 | 0.00032236
57 | 0.97313 | -0.18903 | 0.0017454 | 0.00043745
58 | 0.974 | -0.1828 | 0.003459 | 0.00086691
59 | 0.9741 | -0.18223 | 0.0013208 | 0.00033102
60 | 0.97435 | -0.18045 | 0.0021802 | 0.00054642
61 | 0.97447 | -0.17956 | 0.0026753 | 0.00067049
62 | 0.97468 | -0.17803 | 0 | 0
63 | 0.99862 | -0.0096829 | 0.0038893 | 0.00097474
64 | 0.99878 | -0.0085451 | 0.0019511 | 0.00048899
65 | 0.99856 | -0.01008 | 0.0048925 | 0.0012262
66 | 0.99908 | -0.0064316 | 0.003248 | 0.00081402
67 | 0.99932 | -0.0047836 | 0.0019688 | 0.00049343
68 | 0.99981 | -0.0013336 | 0.0013359 | 0.0003348
69 | 0.97264 | -0.19257 | 0.0023657 | 0.00059289
70 | 0.97272 | -0.19205 | 0.0023793 | 0.00059632
71 | 0.97295 | -0.19034 | 0.0075366 | 0.0018888
72 | 0.99207 | -0.054838 | 0.0031761 | 0.00079599
73 | 0.99371 | -0.043443 | 0.0019758 | 0.00049518
74 | 0.99576 | -0.029203 | 0.0017333 | 0.0004344
75 | 0.99596 | -0.027882 | 0.0021543 | 0.00053992
76 | 0.99767 | -0.016039 | 0.0019448 | 0.00048742
77 | 0.98609 | -0.096764 | 0.0017563 | 0.00044017
78 | 0.97599 | -0.16866 | 0.00027171 | 6.8097e-05
79 | 0.97602 | -0.16845 | 0.00037686 | 9.445e-05
80 | 0.97607 | -0.16807 | 0.0019516 | 0.00048912
81 | 0.97609 | -0.16799 | 0.0021157 | 0.00053025
82 | 0.98413 | -0.11066 | 0.0044946 | 0.0011265
83 | 0.9827 | -0.12077 | 0 | 0
84 | 0.98161 | -0.12848 | 0 | 0
85 | 0.98241 | -0.12283 | 0.0033019 | 0.00082753
86 | 0.98049 | -0.13646 | 0.0021794 | 0.00054621
87 | 0.98152 | -0.12911 | 0.0017925 | 0.00044923
88 | 0.98075 | -0.13459 | 0.0016974 | 0.0004254
89 | 0.97961 | -0.14277 | 0.0020225 | 0.00050688
90 | 0.98152 | -0.12914 | 0.0016648 | 0.00041724
91 | 0.97997 | -0.14017 | 0 | 0
92 | 0.9981 | -0.013068 | 0.00089119 | 0.00022335
93 | 0.99883 | -0.008067 | 0.00089119 | 0.00022335
94 | 1 | 0 | -0.24008 | -0.06052
95 | 0.97392 | -0.1834 | 0.0050958 | 0.0012771
96 | 0.97553 | -0.17192 | 0 | 0
97 | 0.97461 | -0.17852 | 0.0017185 | 0.00043069
98 | 0.97559 | -0.17148 | 0.0027182 | 0.00068124
99 | 0.97459 | -0.17868 | 0.0016343 | 0.0004096
100 | 0.97592 | -0.16911 | 0.0020308 | 0.00050897
101 | 0.97882 | -0.14838 | 0.003445 | 0.00086339
102 | 0.97938 | -0.14437 | 0.0020801 | 0.00052133
103 | 0.97851 | -0.15058 | 0.0030756 | 0.00077083
104 | 0.97924 | -0.14541 | 0.0019559 | 0.00049019
105 | 0.97924 | -0.14543 | 0.0020038 | 0.0005022
106 | 0.97789 | -0.15507 | 0.0032138 | 0.00080545
107 | 0.97776 | -0.15601 | 0.00087509 | 0.00021932
108 | 0.97779 | -0.15571 | 0.0016935 | 0.00042444
109 | 0.97748 | -0.15797 | 0.0022137 | 0.00055481
110 | 0.9786 | -0.1499 | 0.0019426 | 0.00048685
111 | 0.97657 | -0.16443 | 0.0026298 | 0.00065908
112 | 0.97899 | -0.14716 | 0.001651 | 0.00041378
113 | 0.97643 | -0.1655 | 0.0029806 | 0.00074702
114 | 0.97759 | -0.15722 | 0.0028079 | 0.00070373
115 | 0.97771 | -0.15634 | 0.00084595 | 0.00021201
116 | 0.97697 | -0.16161 | 0.0016161 | 0.00040504
117 | 0.97692 | -0.162 | 0.0021507 | 0.00053901
118 | 0.97668 | -0.16371 | 0.0017471 | 0.00043785
119 | 0.97651 | -0.16494 | 0.0021073 | 0.00052813
120 | 0.97637 | -0.16595 | 0.0019041 | 0.0004772
121 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.00037314 | 9.3132e-05 | -0.00037314 | -9.3517e-05 | 6.3482e-09 | -3.8504e-07 | 0.00057074 | 0.00057088 | 0.00057088 | 0.97261 | -0.19284 | 0.97259 | -0.19297 | 0.21144
1 | -0.012706 | -0.003184 | 0.012723 | 0.0031898 | 1.7492e-05 | 5.8059e-06 | 0.019439 | 0.019438 | 0.019439 | 0.97261 | -0.19284 | 0.97399 | -0.18291 | 7.1995
2 | -0.012723 | -0.0031898 | 0.012724 | 0.0031901 | 8.6625e-07 | 2.8744e-07 | 0.019438 | 0.019438 | 0.019438 | 0.97399 | -0.18291 | 0.97406 | -0.18241 | 7.1994
3 | -0.021143 | -0.0052994 | 0.021163 | 0.0053068 | 2.0381e-05 | 7.4488e-06 | 0.032299 | 0.032299 | 0.032299 | 0.97406 | -0.18241 | 0.97502 | -0.17546 | 11.9627
4 | 0.008419 | 0.0021093 | -0.0084107 | -0.0021071 | 8.2602e-06 | 2.1819e-06 | 0.012861 | 0.012861 | 0.012861 | 0.97406 | -0.18241 | 0.97307 | -0.18951 | 4.7635
5 | 0.02767 | 0.0069381 | -0.027659 | -0.0069337 | 1.1575e-05 | 4.3224e-06 | 0.04223 | 0.04223 | 0.04223 | 0.97502 | -0.17546 | 0.9746 | -0.17848 | 15.6406
6 | -0.048834 | -0.012245 | 0.048996 | 0.012305 | 0.00016286 | 6.0286e-05 | 0.074529 | 0.074528 | 0.074529 | 0.97502 | -0.17546 | 0.97838 | -0.15147 | 13.8016
7 | 0.0060278 | 0.0015099 | -0.0060268 | -0.0015098 | 1.058e-06 | 1.5907e-07 | 0.0092175 | 0.0092176 | 0.0092176 | 0.97307 | -0.18951 | 0.97289 | -0.19078 | 3.4139
8 | 0.01861 | 0.0046659 | -0.018603 | -0.0046634 | 6.9518e-06 | 2.5019e-06 | 0.028414 | 0.028415 | 0.028415 | 0.9746 | -0.17848 | 0.97423 | -0.18118 | 10.5239
9 | 0.0090485 | 0.0022678 | -0.0090453 | -0.0022669 | 3.1896e-06 | 8.9314e-07 | 0.013815 | 0.013815 | 0.013815 | 0.9746 | -0.17848 | 0.97425 | -0.18103 | 5.1168
10 | -0.051689 | -0.01298 | 0.051696 | 0.012982 | 6.8873e-06 | 2.4471e-06 | 0.078623 | 0.078623 | 0.078623 | 0.97838 | -0.15147 | 0.97851 | -0.15051 | 9.7065
11 | 0.0047224 | 0.0011829 | -0.0047217 | -0.0011829 | 7.2263e-07 | 2.3165e-09 | 0.0072226 | 0.0072227 | 0.0072227 | 0.97289 | -0.19078 | 0.97274 | -0.19189 | 2.6751
12 | 0.00049284 | 0.00012345 | -0.00049284 | -0.00012352 | 1.8906e-09 | -6.8279e-08 | 0.00074603 | 0.00074605 | 0.00074605 | 0.98298 | -0.11883 | 0.98298 | -0.11885 | 0.27632
13 | -0.0012269 | -0.00030743 | 0.001227 | 0.00030722 | 3.6439e-08 | -2.006e-07 | 0.0018573 | 0.0018572 | 0.0018573 | 0.98298 | -0.11883 | 0.98301 | -0.11861 | 0.68787
14 | -0.0016542 | -0.00041431 | 0.0016542 | 0.0004143 | 4.095e-09 | -1.1694e-08 | 0.0025039 | 0.0025039 | 0.0025039 | 0.98301 | -0.11861 | 0.98301 | -0.11859 | 0.92739
15 | -0.0019461 | -0.00048745 | 0.0019462 | 0.00048737 | 4.0783e-08 | -7.9799e-08 | 0.0029458 | 0.0029458 | 0.0029458 | 0.98301 | -0.11859 | 0.98303 | -0.11844 | 1.091
16 | -0.0021443 | -0.00053704 | 0.0021444 | 0.00053692 | 7.8694e-08 | -1.2151e-07 | 0.0032458 | 0.0032457 | 0.0032458 | 0.98303 | -0.11844 | 0.98307 | -0.11818 | 1.2021
17 | -0.0021444 | -0.00053692 | 0.0021447 | 0.00053648 | 2.8347e-07 | -4.3782e-07 | 0.0032457 | 0.0032455 | 0.0032457 | 0.98307 | -0.11818 | 0.9832 | -0.11722 | 1.2021
18 | -0.014762 | -0.0036997 | 0.014774 | 0.0037037 | 1.1652e-05 | 4.0075e-06 | 0.022353 | 0.022353 | 0.022353 | 0.9827 | -0.12081 | 0.9835 | -0.11512 | 8.2789
19 | 0.003871 | 0.0009681 | -0.0038698 | -0.00096834 | 1.1234e-06 | -2.3391e-07 | 0.005856 | 0.0058562 | 0.0058562 | 0.9835 | -0.11512 | 0.9832 | -0.11722 | 2.169
20 | -0.018645 | -0.0046718 | 0.018652 | 0.0046743 | 6.9314e-06 | 2.4887e-06 | 0.028209 | 0.028209 | 0.028209 | 0.9835 | -0.11512 | 0.98388 | -0.11243 | 10.4477
21 | 0.0017251 | 0.00043185 | -0.0017251 | -0.00043205 | 7.6318e-08 | -1.9821e-07 | 0.0026107 | 0.0026108 | 0.0026108 | 0.9832 | -0.11722 | 0.98316 | -0.11754 | 0.96695
22 | -0.10005 | -0.02514 | 0.10012 | 0.025168 | 7.2693e-05 | 2.7377e-05 | 0.15133 | 0.15133 | 0.15133 | 0.98388 | -0.11243 | 0.98461 | -0.10721 | 18.6833
23 | 0.081395 | 0.020466 | -0.081272 | -0.02042 | 0.00012333 | 4.5946e-05 | 0.12313 | 0.12313 | 0.12313 | 0.98388 | -0.11243 | 0.98234 | -0.12332 | 15.2008
24 | 0.0013185 | 0.00033015 | -0.0013185 | -0.00033015 | 1.2741e-09 | -6.0136e-09 | 0.0019954 | 0.0019954 | 0.0019954 | 0.98316 | -0.11754 | 0.98316 | -0.11755 | 0.73903
25 | -0.0016676 | -0.00041785 | 0.0016677 | 0.00041768 | 6.0202e-08 | -1.7003e-07 | 0.0025202 | 0.0025202 | 0.0025202 | 0.98458 | -0.10747 | 0.98461 | -0.10721 | 0.93342
26 | 0.0016676 | 0.00041785 | -0.0016676 | -0.00041793 | 2.9878e-08 | -8.4378e-08 | 0.0025202 | 0.0025203 | 0.0025203 | 0.98458 | -0.10747 | 0.98456 | -0.1076 | 0.93343
27 | -0.10179 | -0.025585 | 0.102 | 0.025664 | 0.0002093 | 7.8875e-05 | 0.15385 | 0.15385 | 0.15385 | 0.98461 | -0.10721 | 0.9867 | -0.092476 | 18.9944
28 | 0.069797 | 0.017544 | -0.069745 | -0.017525 | 5.2277e-05 | 1.9253e-05 | 0.10575 | 0.10575 | 0.10575 | 0.98234 | -0.12332 | 0.98158 | -0.1287 | 13.055
29 | 0.00091824 | 0.00022985 | -0.00091822 | -0.0002301 | 2.4569e-08 | -2.4907e-07 | 0.0013897 | 0.0013898 | 0.0013898 | 0.98316 | -0.11755 | 0.98313 | -0.11774 | 0.51472
30 | -0.10344 | -0.026025 | 0.10364 | 0.0261 | 0.00019869 | 7.4913e-05 | 0.15603 | 0.15603 | 0.15603 | 0.9867 | -0.092476 | 0.98866 | -0.078736 | 19.2625
31 | 0.064963 | 0.016327 | -0.064922 | -0.016311 | 4.1644e-05 | 1.5235e-05 | 0.098497 | 0.098497 | 0.098497 | 0.98158 | -0.1287 | 0.98093 | -0.13331 | 12.1601
32 | 0.0005205 | 0.00013042 | -0.0005205 | -0.00013045 | 8.2828e-10 | -2.6801e-08 | 0.00078779 | 0.0007878 | 0.0007878 | 0.98313 | -0.11774 | 0.98313 | -0.11775 | 0.29178
33 | 0.0035821 | 0.00089724 | -0.0035821 | -0.00089725 | 1.0683e-08 | -2.9697e-09 | 0.0054794 | 0.0054794 | 0.0054794 | 0.97274 | -0.19189 | 0.97274 | -0.19191 | 2.0294
34 | 0.0025882 | 0.00064817 | -0.002588 | -0.00064836 | 2.1263e-07 | -1.8805e-07 | 0.0039591 | 0.0039592 | 0.0039592 | 0.97274 | -0.19191 | 0.97265 | -0.1925 | 1.4664
35 | 0.0013278 | 0.0003325 | -0.0013277 | -0.00033275 | 5.6238e-08 | -2.4948e-07 | 0.0020312 | 0.0020313 | 0.0020313 | 0.97265 | -0.1925 | 0.97261 | -0.19281 | 0.75232
36 | -0.0019221 | -0.00048156 | 0.0019222 | 0.00048138 | 9.2871e-08 | -1.7709e-07 | 0.0029434 | 0.0029433 | 0.0029434 | 0.97169 | -0.19968 | 0.97174 | -0.19933 | 1.0901
37 | 0.0014658 | 0.00036719 | -0.0014657 | -0.00036735 | 4.5175e-08 | -1.6061e-07 | 0.0022446 | 0.0022446 | 0.0022446 | 0.97169 | -0.19968 | 0.97166 | -0.1999 | 0.83135
38 | -0.0021922 | -0.00054903 | 0.0021925 | 0.00054855 | 3.5264e-07 | -4.8586e-07 | 0.0033567 | 0.0033565 | 0.0033567 | 0.97174 | -0.19933 | 0.9719 | -0.19816 | 1.2432
39 | -0.0021925 | -0.00054855 | 0.002194 | 0.00054652 | 1.4686e-06 | -2.0266e-06 | 0.0033565 | 0.0033555 | 0.0033565 | 0.9719 | -0.19816 | 0.97257 | -0.19329 | 1.2431
40 | -0.002194 | -0.00054652 | 0.0021941 | 0.0005463 | 1.5799e-07 | -2.1832e-07 | 0.0033555 | 0.0033554 | 0.0033555 | 0.97257 | -0.19329 | 0.97265 | -0.19276 | 1.2428
41 | -0.0026762 | -0.00066712 | 0.0026766 | 0.00066676 | 4.5093e-07 | -3.6209e-07 | 0.0040929 | 0.0040927 | 0.0040929 | 0.97265 | -0.19276 | 0.97282 | -0.19153 | 1.5159
42 | 0.014046 | 0.0035213 | -0.014031 | -0.003516 | 1.5271e-05 | 5.212e-06 | 0.021454 | 0.021454 | 0.021454 | 0.97423 | -0.18118 | 0.97313 | -0.18903 | 7.9459
43 | 0.0085573 | 0.0021446 | -0.0085552 | -0.0021441 | 2.1031e-06 | 5.6327e-07 | 0.01307 | 0.01307 | 0.01307 | 0.97425 | -0.18103 | 0.974 | -0.1828 | 4.8408
44 | -0.051696 | -0.012982 | 0.051733 | 0.012996 | 3.6846e-05 | 1.3091e-05 | 0.078623 | 0.078622 | 0.078623 | 0.97851 | -0.15051 | 0.97923 | -0.14539 | 9.7065
45 | -0.0052204 | -0.0013043 | 0.005222 | 0.0013044 | 1.6157e-06 | 1.1688e-07 | 0.0079836 | 0.0079835 | 0.0079836 | 0.97282 | -0.19153 | 0.97313 | -0.18928 | 2.9569
46 | -0.005222 | -0.0013044 | 0.0052266 | 0.0013047 | 4.582e-06 | 3.296e-07 | 0.0079835 | 0.0079829 | 0.0079835 | 0.97313 | -0.18928 | 0.97401 | -0.1829 | 2.9568
47 | -0.0056954 | -0.0014222 | 0.0056955 | 0.0014222 | 1.3201e-07 | 1.5979e-08 | 0.0086991 | 0.0086991 | 0.0086991 | 0.97401 | -0.1829 | 0.97403 | -0.18273 | 3.2219
48 | -0.00027282 | -6.8374e-05 | 0.00027282 | 6.8297e-05 | 6.6496e-10 | -7.6719e-08 | 0.00041595 | 0.00041592 | 0.00041595 | 0.97598 | -0.16877 | 0.97598 | -0.16876 | 0.15405
49 | -0.00062145 | -0.00015567 | 0.00062146 | 0.0001555 | 7.9092e-09 | -1.7342e-07 | 0.00094746 | 0.0009474 | 0.00094746 | 0.97598 | -0.16876 | 0.97599 | -0.16866 | 0.35091
50 | -0.0075842 | -0.0018956 | 0.0075848 | 0.0018957 | 5.2481e-07 | 1.2384e-07 | 0.011584 | 0.011584 | 0.011584 | 0.97403 | -0.18273 | 0.9741 | -0.18223 | 4.2905
51 | -0.11008 | -0.027716 | 0.11011 | 0.027726 | 2.7208e-05 | 1.0281e-05 | 0.16573 | 0.16573 | 0.16573 | 0.98866 | -0.078736 | 0.98891 | -0.076967 | 20.4601
52 | -0.11308 | -0.028472 | 0.11315 | 0.028497 | 6.7501e-05 | 2.553e-05 | 0.17021 | 0.17021 | 0.17021 | 0.98891 | -0.076967 | 0.98952 | -0.072697 | 21.013
53 | 0.091732 | 0.023114 | -0.091542 | -0.023042 | 0.00018996 | 7.2242e-05 | 0.13799 | 0.13799 | 0.13799 | 0.98952 | -0.072697 | 0.9874 | -0.087527 | 25.5536
54 | -0.20488 | -0.051611 | 0.20532 | 0.051778 | 0.00043574 | 0.00016674 | 0.30819 | 0.30819 | 0.30819 | 0.98952 | -0.072697 | 0.99169 | -0.057524 | 38.0486
55 | 0.089892 | 0.022628 | -0.089776 | -0.022584 | 0.00011581 | 4.4414e-05 | 0.1355 | 0.1355 | 0.1355 | 0.9874 | -0.087527 | 0.98609 | -0.096764 | 50.1862
56 | -0.20746 | -0.052314 | 0.20754 | 0.052344 | 7.8118e-05 | 2.9895e-05 | 0.3114 | 0.3114 | 0.3114 | 0.99169 | -0.057524 | 0.99207 | -0.054838 | 38.4449
57 | 0.060162 | 0.015118 | -0.060116 | -0.015102 | 4.5298e-05 | 1.6433e-05 | 0.091276 | 0.091276 | 0.091276 | 0.98093 | -0.13331 | 0.98017 | -0.13872 | 11.2687
58 | 0.054418 | 0.013674 | -0.054394 | -0.013665 | 2.4118e-05 | 8.6341e-06 | 0.082626 | 0.082626 | 0.082626 | 0.98017 | -0.13872 | 0.97972 | -0.14191 | 10.2007
59 | 0.053045 | 0.013327 | -0.053019 | -0.013318 | 2.5652e-05 | 9.1488e-06 | 0.080577 | 0.080577 | 0.080577 | 0.97972 | -0.14191 | 0.97923 | -0.14539 | 9.9478
60 | 0.012285 | 0.0030786 | -0.012283 | -0.0030779 | 2.2177e-06 | 7.2787e-07 | 0.018785 | 0.018785 | 0.018785 | 0.97313 | -0.18903 | 0.97295 | -0.19034 | 6.9574
61 | 0.0050962 | 0.0012771 | -0.0050958 | -0.0012771 | 4.2037e-07 | 2.3372e-08 | 0.0077856 | 0.0077857 | 0.0077857 | 0.974 | -0.1828 | 0.97392 | -0.1834 | 2.8836
62 | -0.0089055 | -0.0022267 | 0.0089077 | 0.0022273 | 2.1833e-06 | 6.0426e-07 | 0.013602 | 0.013602 | 0.013602 | 0.9741 | -0.18223 | 0.97435 | -0.18045 | 5.0378
63 | -0.011088 | -0.0027738 | 0.011089 | 0.0027742 | 1.3685e-06 | 4.3106e-07 | 0.016932 | 0.016932 | 0.016932 | 0.97435 | -0.18045 | 0.97447 | -0.17956 | 6.271
64 | -0.013765 | -0.0034447 | 0.013768 | 0.0034457 | 2.9108e-06 | 9.8795e-07 | 0.021017 | 0.021017 | 0.021017 | 0.97447 | -0.17956 | 0.97468 | -0.17803 | 7.784
65 | -0.017121 | -0.0042858 | 0.017135 | 0.0042909 | 1.4439e-05 | 5.1311e-06 | 0.026136 | 0.026135 | 0.026136 | 0.97468 | -0.17803 | 0.97553 | -0.17192 | 9.6798
66 | 0.0033531 | 0.0008401 | -0.0033528 | -0.00084019 | 2.3172e-07 | -8.7492e-08 | 0.0051189 | 0.005119 | 0.005119 | 0.97468 | -0.17803 | 0.97461 | -0.17852 | 1.8959
67 | -0.008782 | -0.0022009 | 0.0087834 | 0.0022013 | 1.3833e-06 | 3.6265e-07 | 0.013086 | 0.013086 | 0.013086 | 0.99862 | -0.0096829 | 0.99878 | -0.0085451 | 4.8466
68 | 0.0048928 | 0.0012262 | -0.0048925 | -0.0012262 | 2.6859e-07 | -2.6376e-09 | 0.0072906 | 0.0072906 | 0.0072906 | 0.99862 | -0.0096829 | 0.99856 | -0.01008 | 2.7002
69 | -0.010734 | -0.0026903 | 0.010738 | 0.0026912 | 3.1414e-06 | 9.5054e-07 | 0.015993 | 0.015992 | 0.015993 | 0.99878 | -0.0085451 | 0.99908 | -0.0064316 | 5.9232
70 | -0.013986 | -0.0035052 | 0.013989 | 0.0035063 | 3.1916e-06 | 1.0731e-06 | 0.02083 | 0.02083 | 0.02083 | 0.99908 | -0.0064316 | 0.99932 | -0.0047836 | 7.7148
71 | -0.015958 | -0.0039997 | 0.015965 | 0.0040024 | 7.6262e-06 | 2.6494e-06 | 0.023762 | 0.023761 | 0.023762 | 0.99932 | -0.0047836 | 0.99981 | -0.0013336 | 8.8006
72 | -0.017301 | -0.0043372 | 0.017304 | 0.0043383 | 3.1964e-06 | 1.1281e-06 | 0.02575 | 0.02575 | 0.02575 | 0.99981 | -0.0013336 | 1 | 0 | 9.5369
73 | -0.0023657 | -0.00059289 | 0.0023658 | 0.0005927 | 1.6965e-07 | -1.9239e-07 | 0.0036191 | 0.0036191 | 0.0036191 | 0.97264 | -0.19257 | 0.97272 | -0.19205 | 1.3404
74 | -0.0047452 | -0.001189 | 0.0047463 | 0.001189 | 1.1272e-06 | 7.8667e-09 | 0.0072589 | 0.0072587 | 0.0072589 | 0.97272 | -0.19205 | 0.97295 | -0.19034 | 2.6885
75 | -0.21071 | -0.05314 | 0.21105 | 0.053269 | 0.00033714 | 0.00012904 | 0.31617 | 0.31617 | 0.31617 | 0.99207 | -0.054838 | 0.99371 | -0.043443 | 39.033
76 | -0.21303 | -0.053764 | 0.21345 | 0.053928 | 0.00042675 | 0.00016335 | 0.31913 | 0.31913 | 0.31913 | 0.99371 | -0.043443 | 0.99576 | -0.029203 | 39.3982
77 | -0.21519 | -0.054362 | 0.21523 | 0.054377 | 4.0021e-05 | 1.532e-05 | 0.32172 | 0.32172 | 0.32172 | 0.99576 | -0.029203 | 0.99596 | -0.027882 | 39.718
78 | -0.21738 | -0.054917 | 0.21774 | 0.055056 | 0.00036277 | 0.00013888 | 0.32493 | 0.32493 | 0.32493 | 0.99596 | -0.027882 | 0.99767 | -0.016039 | 40.1153
79 | -0.21969 | -0.055544 | 0.21978 | 0.055579 | 9.2021e-05 | 3.5232e-05 | 0.32783 | 0.32783 | 0.32783 | 0.99767 | -0.016039 | 0.9981 | -0.013068 | 40.4734
80 | 0.08802 | 0.022144 | -0.08785 | -0.022078 | 0.00017024 | 6.5281e-05 | 0.13285 | 0.13285 | 0.13285 | 0.98609 | -0.096764 | 0.98413 | -0.11066 | 49.2046
81 | -0.00089317 | -0.0002236 | 0.0008932 | 0.00022332 | 2.6561e-08 | -2.7672e-07 | 0.0013617 | 0.0013615 | 0.0013617 | 0.97599 | -0.16866 | 0.97602 | -0.16845 | 0.50432
82 | -0.0012701 | -0.00031777 | 0.0012701 | 0.00031744 | 6.6929e-08 | -3.319e-07 | 0.0019361 | 0.001936 | 0.0019361 | 0.97602 | -0.16845 | 0.97607 | -0.16807 | 0.71707
83 | -0.0032217 | -0.00080656 | 0.0032218 | 0.00080655 | 3.5417e-08 | -1.5791e-08 | 0.0049112 | 0.0049112 | 0.0049112 | 0.97607 | -0.16807 | 0.97609 | -0.16799 | 1.819
84 | -0.0053375 | -0.0013368 | 0.005339 | 0.0013369 | 1.5e-06 | 1.2293e-07 | 0.0081366 | 0.0081364 | 0.0081366 | 0.97609 | -0.16799 | 0.97637 | -0.16595 | 3.0135
85 | 0.083355 | 0.020952 | -0.083238 | -0.020907 | 0.00011724 | 4.4941e-05 | 0.12606 | 0.12606 | 0.12606 | 0.98413 | -0.11066 | 0.9827 | -0.12077 | 46.6876
86 | 0.043016 | 0.010802 | -0.04297 | -0.010784 | 4.6044e-05 | 1.7489e-05 | 0.065143 | 0.065143 | 0.065143 | 0.9827 | -0.12077 | 0.98161 | -0.12848 | 24.1272
87 | 0.040222 | 0.010105 | -0.04021 | -0.010101 | 1.1492e-05 | 4.3571e-06 | 0.060913 | 0.060913 | 0.060913 | 0.9827 | -0.12077 | 0.98241 | -0.12283 | 22.5605
88 | 0.039513 | 0.0099177 | -0.039469 | -0.0099012 | 4.3692e-05 | 1.6558e-05 | 0.059902 | 0.059902 | 0.059902 | 0.98161 | -0.12848 | 0.98049 | -0.13646 | 22.186
89 | 0.0034575 | 0.00086634 | -0.0034572 | -0.00086645 | 3.016e-07 | -1.064e-07 | 0.0052412 | 0.0052413 | 0.0052413 | 0.98161 | -0.12848 | 0.98152 | -0.12911 | 1.9412
90 | 0.036908 | 0.0092735 | -0.036848 | -0.0092507 | 6.0323e-05 | 2.281e-05 | 0.055912 | 0.055912 | 0.055912 | 0.98241 | -0.12283 | 0.98075 | -0.13459 | 20.7082
91 | 0.03729 | 0.009355 | -0.037257 | -0.0093426 | 3.2651e-05 | 1.2352e-05 | 0.056595 | 0.056595 | 0.056595 | 0.98049 | -0.13646 | 0.97961 | -0.14277 | 20.961
92 | 0.0016648 | 0.00041722 | -0.0016648 | -0.00041724 | 5.8122e-09 | -1.6246e-08 | 0.0025239 | 0.0025239 | 0.0025239 | 0.98152 | -0.12911 | 0.98152 | -0.12914 | 0.93477
93 | 0.035151 | 0.0088253 | -0.035123 | -0.0088151 | 2.7199e-05 | 1.0268e-05 | 0.053337 | 0.053337 | 0.053337 | 0.98075 | -0.13459 | 0.97997 | -0.14017 | 19.7545
94 | 0.029193 | 0.0073219 | -0.02917 | -0.0073134 | 2.2667e-05 | 8.4859e-06 | 0.044345 | 0.044346 | 0.044346 | 0.97961 | -0.14277 | 0.97882 | -0.14838 | 16.4243
95 | 0.0060418 | 0.0015138 | -0.0060404 | -0.0015136 | 1.332e-06 | 1.933e-07 | 0.0091772 | 0.0091773 | 0.0091773 | 0.97961 | -0.14277 | 0.97938 | -0.14437 | 3.399
96 | 0.035123 | 0.0088151 | -0.035089 | -0.0088022 | 3.4092e-05 | 1.287e-05 | 0.053337 | 0.053337 | 0.053337 | 0.97997 | -0.14017 | 0.97899 | -0.14716 | 19.7545
97 | -0.22067 | -0.055802 | 0.22083 | 0.055862 | 0.00015566 | 5.9597e-05 | 0.32916 | 0.32916 | 0.32916 | 0.9981 | -0.013068 | 0.99883 | -0.008067 | 40.6374
98 | -0.22172 | -0.056085 | 0.22197 | 0.056182 | 0.00025257 | 9.6706e-05 | 0.33049 | 0.33049 | 0.33049 | 0.99883 | -0.008067 | 1 | 0 | 40.8013
99 | -0.017135 | -0.0042909 | 0.017136 | 0.0042913 | 1.0488e-06 | 3.7267e-07 | 0.026135 | 0.026135 | 0.026135 | 0.97553 | -0.17192 | 0.97559 | -0.17148 | 9.6798
100 | 0.0016344 | 0.0004095 | -0.0016343 | -0.0004096 | 3.4739e-08 | -9.8058e-08 | 0.0024952 | 0.0024953 | 0.0024953 | 0.97461 | -0.17852 | 0.97459 | -0.17868 | 0.92418
101 | -0.019854 | -0.0049725 | 0.019861 | 0.0049749 | 6.5008e-06 | 2.3584e-06 | 0.030281 | 0.030281 | 0.030281 | 0.97559 | -0.17148 | 0.97592 | -0.16911 | 11.2153
102 | -0.021892 | -0.0054838 | 0.021903 | 0.0054879 | 1.0952e-05 | 4.0153e-06 | 0.033378 | 0.033378 | 0.033378 | 0.97592 | -0.16911 | 0.97643 | -0.1655 | 12.3621
103 | 0.025725 | 0.0064501 | -0.025717 | -0.0064471 | 7.8577e-06 | 2.9187e-06 | 0.039108 | 0.039108 | 0.039108 | 0.97882 | -0.14838 | 0.97851 | -0.15058 | 14.4846
104 | 0.0039603 | 0.00099229 | -0.0039597 | -0.00099239 | 5.7358e-07 | -9.8845e-08 | 0.0060169 | 0.006017 | 0.006017 | 0.97938 | -0.14437 | 0.97924 | -0.14541 | 2.2285
105 | 0.022642 | 0.0056763 | -0.022627 | -0.0056711 | 1.4078e-05 | 5.1756e-06 | 0.034431 | 0.034431 | 0.034431 | 0.97851 | -0.15058 | 0.97789 | -0.15507 | 12.7524
106 | 0.0020038 | 0.00050219 | -0.0020038 | -0.0005022 | 4.8374e-09 | -8.6582e-09 | 0.0030449 | 0.0030449 | 0.0030449 | 0.97924 | -0.14541 | 0.97924 | -0.14543 | 1.1278
107 | 0.019414 | 0.0048657 | -0.019411 | -0.0048648 | 2.5136e-06 | 9.0889e-07 | 0.029541 | 0.029541 | 0.029541 | 0.97789 | -0.15507 | 0.97776 | -0.15601 | 10.9412
108 | 0.018536 | 0.0046455 | -0.018535 | -0.0046452 | 8.4074e-07 | 3.0213e-07 | 0.028209 | 0.028209 | 0.028209 | 0.97776 | -0.15601 | 0.97771 | -0.15634 | 10.4479
109 | 0.029764 | 0.0074628 | -0.029755 | -0.0074593 | 9.3057e-06 | 3.488e-06 | 0.045297 | 0.045297 | 0.045297 | 0.97779 | -0.15571 | 0.97748 | -0.15797 | 16.7766
110 | -0.031458 | -0.0078872 | 0.031483 | 0.0078968 | 2.5359e-05 | 9.5309e-06 | 0.047874 | 0.047874 | 0.047874 | 0.97779 | -0.15571 | 0.9786 | -0.1499 | 17.7311
111 | 0.027541 | 0.0069045 | -0.027517 | -0.0068953 | 2.463e-05 | 9.1919e-06 | 0.041927 | 0.041927 | 0.041927 | 0.97748 | -0.15797 | 0.97657 | -0.16443 | 15.5285
112 | -0.033426 | -0.0083836 | 0.033438 | 0.0083884 | 1.268e-05 | 4.778e-06 | 0.050828 | 0.050828 | 0.050828 | 0.9786 | -0.1499 | 0.97899 | -0.14716 | 18.8251
113 | 0.024887 | 0.0062362 | -0.024883 | -0.0062349 | 3.6683e-06 | 1.3598e-06 | 0.03792 | 0.03792 | 0.03792 | 0.97657 | -0.16443 | 0.97643 | -0.1655 | 14.0444
114 | -0.0028079 | -0.00070373 | 0.0028083 | 0.00070348 | 3.4447e-07 | -2.4646e-07 | 0.004274 | 0.0042739 | 0.004274 | 0.97759 | -0.15722 | 0.97771 | -0.15634 | 1.583
115 | 0.014881 | 0.0037297 | -0.01487 | -0.0037259 | 1.0858e-05 | 3.7509e-06 | 0.022648 | 0.022648 | 0.022648 | 0.97771 | -0.15634 | 0.97697 | -0.16161 | 8.3882
116 | 0.013254 | 0.0033209 | -0.013253 | -0.0033206 | 7.1825e-07 | 2.4088e-07 | 0.020187 | 0.020187 | 0.020187 | 0.97697 | -0.16161 | 0.97692 | -0.162 | 7.4766
117 | 0.011103 | 0.0027816 | -0.0111 | -0.0027808 | 2.6196e-06 | 8.2377e-07 | 0.016911 | 0.016911 | 0.016911 | 0.97692 | -0.162 | 0.97668 | -0.16371 | 6.2633
118 | 0.0093529 | 0.0023429 | -0.0093513 | -0.0023425 | 1.5936e-06 | 4.5554e-07 | 0.014249 | 0.014249 | 0.014249 | 0.97668 | -0.16371 | 0.97651 | -0.16494 | 5.2775
119 | 0.0072441 | 0.0018143 | -0.0072431 | -0.0018141 | 1.0156e-06 | 2.2354e-07 | 0.011038 | 0.011038 | 0.011038 | 0.97651 | -0.16494 | 0.97637 | -0.16595 | 4.0882

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.24179 | 0.06095

## res_load
| p_mw | q_mvar
0 | 0.012333 | 0.0030908
1 | 0.00037314 | 9.3517e-05
2 | 0.0023829 | 0.00059721
3 | 0.0026925 | 0.00067479
4 | 0.0013043 | 0.00032689
5 | 0.00073408 | 0.00018398
6 | 0.00049284 | 0.00012352
7 | 0.00042727 | 0.00010708
8 | 0.0002919 | 7.3156e-05
9 | 0.00019819 | 4.9671e-05
10 | 0.014762 | 0.0036997
11 | 0.0004066 | 0.0001019
12 | 0.0016676 | 0.00041793
13 | 0.011474 | 0.0028757
14 | 0.00040022 | 0.0001003
15 | 0.0014403 | 0.00036098
16 | 0.0047818 | 0.0011984
17 | 0.00039772 | 9.9677e-05
18 | 0.0005205 | 0.00013045
19 | 0.0011396 | 0.00028562
20 | 0.00099383 | 0.00024908
21 | 0.0012603 | 0.00031586
22 | 0.0013277 | 0.00033275
23 | 0.00045634 | 0.00011437
24 | 0.00026995 | 6.7656e-05
25 | 0.0014657 | 0.00036735
26 | 0.00048206 | 0.00012081
27 | 0.0045574 | 0.0011422
28 | 0.00048794 | 0.00012229
29 | 0.0025438 | 0.00063752
30 | 0.0004688 | 0.00011749
31 | 0.00027282 | 6.8374e-05
32 | 0.00034863 | 8.7376e-05
33 | 0.0018887 | 0.00047335
34 | 0.0064456 | 0.0016154
35 | 0.0029764 | 0.00074596
36 | 0.00165 | 0.00041354
37 | 0.0021393 | 0.00053616
38 | 0.0047602 | 0.001193
39 | 0.0056983 | 0.0014281
40 | 0.0013492 | 0.00033815
41 | 0.0012862 | 0.00032236
42 | 0.0017454 | 0.00043745
43 | 0.003459 | 0.00086691
44 | 0.0013208 | 0.00033102
45 | 0.0021802 | 0.00054642
46 | 0.0026753 | 0.00067049
47 | 0.0038893 | 0.00097474
48 | 0.0019511 | 0.00048899
49 | 0.0048925 | 0.0012262
50 | 0.003248 | 0.00081402
51 | 0.0019688 | 0.00049343
52 | 0.0013359 | 0.0003348
53 | 0.0023657 | 0.00059289
54 | 0.0023793 | 0.00059632
55 | 0.0075366 | 0.0018888
56 | 0.0031761 | 0.00079599
57 | 0.0019758 | 0.00049518
58 | 0.0017333 | 0.0004344
59 | 0.0021543 | 0.00053992
60 | 0.0019448 | 0.00048742
61 | 0.0017563 | 0.00044017
62 | 0.00027171 | 6.8097e-05
63 | 0.00037686 | 9.445e-05
64 | 0.0019516 | 0.00048912
65 | 0.0021157 | 0.00053025
66 | 0.0044946 | 0.0011265
67 | 0.0033019 | 0.00082753
68 | 0.0021794 | 0.00054621
69 | 0.0017925 | 0.00044923
70 | 0.0016974 | 0.0004254
71 | 0.0020225 | 0.00050688
72 | 0.0016648 | 0.00041724
73 | 0.00089119 | 0.00022335
74 | 0.00089119 | 0.00022335
75 | 0.0017141 | 0.00042959
76 | 0.0050958 | 0.0012771
77 | 0.0017185 | 0.00043069
78 | 0.0027182 | 0.00068124
79 | 0.0016343 | 0.0004096
80 | 0.0020308 | 0.00050897
81 | 0.003445 | 0.00086339
82 | 0.0020801 | 0.00052133
83 | 0.0030756 | 0.00077083
84 | 0.0019559 | 0.00049019
85 | 0.0020038 | 0.0005022
86 | 0.0032138 | 0.00080545
87 | 0.00087509 | 0.00021932
88 | 0.0016935 | 0.00042444
89 | 0.0022137 | 0.00055481
90 | 0.0019426 | 0.00048685
91 | 0.0026298 | 0.00065908
92 | 0.001651 | 0.00041378
93 | 0.0029806 | 0.00074702
94 | 0.0028079 | 0.00070373
95 | 0.00084595 | 0.00021201
96 | 0.0016161 | 0.00040504
97 | 0.0021507 | 0.00053901
98 | 0.0017471 | 0.00043785
99 | 0.0021073 | 0.00052813
100 | 0.0019041 | 0.0004772

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1