## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1143-2_1_3_node_38 | 0.4 | n |  | TRUE
1 | bus_LV_1143-2_1_3_node_37 | 0.4 | n |  | TRUE
2 | bus_LV_1143-2_1_3_node_27 | 0.4 | n |  | TRUE
3 | bus_LV_1143-2_1_3_node_28 | 0.4 | n |  | TRUE
4 | bus_LV_1143-2_1_3_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_1143-2_1_3_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_1143-2_1_3_node_43 | 0.4 | n |  | TRUE
7 | bus_LV_1143-2_1_3_node_44 | 0.4 | n |  | TRUE
8 | bus_LV_1143-2_1_3_node_40 | 0.4 | n |  | TRUE
9 | bus_LV_1143-2_1_3_node_51 | 0.4 | n |  | TRUE
10 | bus_LV_1143-2_1_3_node_48 | 0.4 | n |  | TRUE
11 | bus_LV_1143-2_1_3_node_41 | 0.4 | n |  | TRUE
12 | bus_LV_1143-2_1_3_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_1143-2_1_3_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_1143-2_1_3_node_33 | 0.4 | n |  | TRUE
15 | bus_LV_1143-2_1_3_node_34 | 0.4 | n |  | TRUE
16 | bus_LV_1143-2_1_3_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_1143-2_1_3_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_1143-2_1_3_node_39 | 0.4 | n |  | TRUE
19 | bus_LV_1143-2_1_3_node_46 | 0.4 | n |  | TRUE
20 | bus_LV_1143-2_1_3_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_1143-2_1_3_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_1143-2_1_3_node_47 | 0.4 | n |  | TRUE
23 | bus_LV_1143-2_1_3_node_49 | 0.4 | n |  | TRUE
24 | bus_MV_131_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1143-2_1_3_load_38 | 0 | 0.0003685 | 9.2356e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1143-2_1_3_load_37 | 1 | 0.0016735 | 0.00041942 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1143-2_1_3_load_27 | 2 | 0.00052895 | 0.00013257 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1143-2_1_3_load_28 | 3 | 0.0066061 | 0.0016556 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1143-2_1_3_load_29 | 4 | 0.0022338 | 0.00055985 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1143-2_1_3_load_40 | 8 | 0.013076 | 0.0032771 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1143-2_1_3_load_51 | 9 | 0.0021379 | 0.00053581 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1143-2_1_3_load_48 | 10 | 0.0021992 | 0.00055116 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1143-2_1_3_load_41 | 11 | 0.028819 | 0.0072227 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1143-2_1_3_load_31 | 12 | 0.0025253 | 0.0006329 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1143-2_1_3_load_32 | 13 | 0.01782 | 0.0044662 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1143-2_1_3_load_33 | 14 | 0.009861 | 0.0024714 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1143-2_1_3_load_34 | 15 | 0.0030838 | 0.00077287 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1143-2_1_3_load_36 | 17 | 0.014824 | 0.0037152 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1143-2_1_3_load_39 | 18 | 0.0068407 | 0.0017144 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1143-2_1_3_load_45 | 20 | 0.0051355 | 0.0012871 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1143-2_1_3_load_49 | 23 | 0.001014 | 0.00025412 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1143-2_1_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.023239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1143-2_1_3_line_1 | NAYY 4x150 SE | 1 | 18 | 0.08273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1143-2_1_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0079407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1143-2_1_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.16699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1143-2_1_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.22816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1143-2_1_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.042926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1143-2_1_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.27005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1143-2_1_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.11846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1143-2_1_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.064987 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1143-2_1_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.058514 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1143-2_1_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.053007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1143-2_1_3_line_11 | NAYY 4x150 SE | 10 | 23 | 0.0079932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1143-2_1_3_line_12 | NAYY 4x150 SE | 11 | 21 | 0.086072 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1143-2_1_3_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0044556 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1143-2_1_3_line_14 | NAYY 4x150 SE | 12 | 14 | 0.093192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1143-2_1_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.028494 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1143-2_1_3_line_16 | NAYY 4x150 SE | 14 | 16 | 0.040677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
17 | LV_1143-2_1_3_line_17 | NAYY 4x150 SE | 15 | 17 | 0.029836 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1143-2_1_3_line_18 | NAYY 4x150 SE | 16 | 18 | 0.073487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1143-2_1_3_line_19 | NAYY 4x150 SE | 16 | 19 | 0.07755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
20 | LV_1143-2_1_3_line_20 | NAYY 4x150 SE | 19 | 20 | 0.005529 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1143-2_1_3_line_21 | NAYY 4x150 SE | 20 | 22 | 0.047076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1143-2_1_3_line_22 | NAYY 4x150 SE | 21 | 22 | 0.035256 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1143-2_1_3_trafo_32 | 0.25 MVA 20/0.4 kV | 24 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29
0 | 2641729.8642 | 1225450.664 | 2641749.4644 | 1225463.1494
1 | 2641729.8642 | 1225450.664 | 2641721.2038 | 1225445.1473 | 2641660.4167 | 1225405.7067
2 | 2641922.7136 | 1225219.0884 | 2641920.6596 | 1225221.6226 | 2641916.775 | 1225224.2302 | 2641916.775 | 1225224.2302
3 | 2641916.775 | 1225224.2302 | 2641912.0964 | 1225224.4085 | 2641904.8859 | 1225219.1879 | 2641900.3588 | 1225217.2216 | 2641896.3532 | 1225218.7165 | 2641874.9017 | 1225243.2028 | 2641788.5658 | 1225172.4228
4 | 2641610.6708 | 1225029.9439 | 2641622.3175 | 1225036.129 | 2641788.5658 | 1225172.4228
5 | 2641596.2838 | 1225065.4984 | 2641607.1738 | 1225028.085 | 2641610.6708 | 1225029.9439
6 | 2641423.8496 | 1225123.8768 | 2641436.3017 | 1225106.942 | 2641444.7272 | 1225102.1422 | 2641453.2968 | 1225097.3322 | 2641462.4401 | 1225090.7029 | 2641471.5108 | 1225081.4493 | 2641488.8394 | 1225070.7857 | 2641491.7378 | 1225072.607 | 2641495.8103 | 1225073.4803 | 2641499.3086 | 1225072.9822 | 2641503.069 | 1225071.8521 | 2641510.6754 | 1225067.1245 | 2641514.4507 | 1225063.871 | 2641517.1265 | 1225060.6544 | 2641520.9234 | 1225054.2992 | 2641523.8183 | 1225046.8371 | 2641525.3733 | 1225038.0092 | 2641526.0079 | 1225029.6308 | 2641525.172 | 1225011.4361 | 2641530.6427 | 1225006.4045 | 2641539.3183 | 1225001.651 | 2641550.5141 | 1224999.6946 | 2641565.1524 | 1224999.7967 | 2641576.2301 | 1225000.6412 | 2641583.0146 | 1225003.9795 | 2641590.0804 | 1225011.5334 | 2641595.3861 | 1225020.3647 | 2641599.5694 | 1225023.8293 | 2641607.1738 | 1225028.085 | 2641610.6708 | 1225029.9439
7 | 2641610.6708 | 1225029.9439 | 2641599.8071 | 1225065.7565 | 2641593.3077 | 1225083.4774 | 2641584.8486 | 1225103.9197 | 2641567.6651 | 1225140.0769
8 | 2641596.2838 | 1225065.4984 | 2641590.1145 | 1225065.2552 | 2641586.2314 | 1225067.6629 | 2641568.748 | 1225096.1248 | 2641555.4219 | 1225112.2416
9 | 2641423.8496 | 1225123.8768 | 2641425.3359 | 1225133.6264 | 2641427.7429 | 1225138.5128 | 2641431.1785 | 1225141.5719 | 2641436.4551 | 1225142.6314 | 2641442.364 | 1225141.0494 | 2641446.559 | 1225138.477 | 2641451.4423 | 1225135.0422 | 2641455.9009 | 1225134.8954 | 2641461.6454 | 1225137.3257 | 2641465.8411 | 1225140.9064
10 | 2641567.6651 | 1225140.0769 | 2641566.0061 | 1225143.5678 | 2641541.4004 | 1225186.1063
11 | 2641465.8411 | 1225140.9064 | 2641467.1619 | 1225142.0336 | 2641469.768 | 1225147.7219
12 | 2641498.304 | 1225260.6115 | 2641541.4004 | 1225186.1063
13 | 2641643.0209 | 1225238.1759 | 2641644.472 | 1225233.9632
14 | 2641643.0209 | 1225238.1759 | 2641612.671 | 1225326.2873
15 | 2641644.472 | 1225233.9632 | 2641653.7516 | 1225207.0228
16 | 2641599.4237 | 1225364.7467 | 2641612.671 | 1225326.2873
17 | 2641663.4684 | 1225178.8131 | 2641653.7516 | 1225207.0228
18 | 2641599.4237 | 1225364.7467 | 2641620.7703 | 1225379.9829 | 2641660.4167 | 1225405.7067
19 | 2641535.6679 | 1225320.5972 | 2641557.2595 | 1225335.5458 | 2641571.1936 | 1225345.1933 | 2641599.4237 | 1225364.7467
20 | 2641535.6679 | 1225320.5972 | 2641531.0375 | 1225317.5758
21 | 2641491.6123 | 1225291.8505 | 2641531.0375 | 1225317.5758
22 | 2641491.6123 | 1225291.8505 | 2641492.1258 | 1225291.0536 | 2641495.191 | 1225286.3276 | 2641495.6202 | 1225285.6635 | 2641493.0143 | 1225282.1321 | 2641491.5745 | 1225278.7867 | 2641491.1745 | 1225276.3491 | 2641491.8253 | 1225273.2518 | 2641495.1273 | 1225266.1038 | 2641498.304 | 1225260.6115

## bus_geodata
| x | y | coords
0 | 2641749.4644 | 1225463.1494
1 | 2641729.8642 | 1225450.664
2 | 2641922.7136 | 1225219.0884
3 | 2641916.775 | 1225224.2302
4 | 2641788.5658 | 1225172.4228
5 | 2641610.6708 | 1225029.9439
6 | 2641596.2838 | 1225065.4984
7 | 2641423.8496 | 1225123.8768
8 | 2641567.6651 | 1225140.0769
9 | 2641555.4219 | 1225112.2416
10 | 2641465.8411 | 1225140.9064
11 | 2641541.4004 | 1225186.1063
12 | 2641643.0209 | 1225238.1759
13 | 2641644.472 | 1225233.9632
14 | 2641612.671 | 1225326.2873
15 | 2641653.7516 | 1225207.0228
16 | 2641599.4237 | 1225364.7467
17 | 2641663.4684 | 1225178.8131
18 | 2641660.4166 | 1225405.7067
19 | 2641535.6679 | 1225320.5972
20 | 2641531.0375 | 1225317.5758
21 | 2641498.304 | 1225260.6115
22 | 2641491.6123 | 1225291.8505
23 | 2641469.768 | 1225147.7219
24 | 2641667.2768 | 1225167.7567

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99101 | -0.062601 | 0.0003685 | 9.2356e-05
1 | 0.99102 | -0.062514 | 0.0016735 | 0.00041942
2 | 0.97194 | -0.19821 | 0.00052895 | 0.00013257
3 | 0.97195 | -0.19817 | 0.0066061 | 0.0016556
4 | 0.9737 | -0.18559 | 0.0022338 | 0.00055985
5 | 0.97683 | -0.16309 | 0 | 0
6 | 0.9767 | -0.16406 | 0 | 0
7 | 0.97556 | -0.17223 | 0 | 0
8 | 0.97938 | -0.1448 | 0.013076 | 0.0032771
9 | 0.97649 | -0.16551 | 0.0021379 | 0.00053581
10 | 0.97529 | -0.17421 | 0.0021992 | 0.00055116
11 | 0.98153 | -0.12945 | 0.028819 | 0.0072227
12 | 0.99973 | -0.0018505 | 0.0025253 | 0.0006329
13 | 1 | 0 | -0.10312 | -0.025804
14 | 0.99429 | -0.039591 | 0.009861 | 0.0024714
15 | 0.99927 | -0.0050975 | 0.0030838 | 0.00077287
16 | 0.9922 | -0.054158 | 0 | 0
17 | 0.99864 | -0.0095214 | 0.014824 | 0.0037152
18 | 0.99127 | -0.060792 | 0.0068407 | 0.0017144
19 | 0.98872 | -0.07857 | 0 | 0
20 | 0.98847 | -0.080317 | 0.0051355 | 0.0012871
21 | 0.98508 | -0.10426 | 0 | 0
22 | 0.98653 | -0.093985 | 0 | 0
23 | 0.97528 | -0.17429 | 0.001014 | 0.00025412
24 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0003685 | -9.2356e-05 | 0.00036851 | 9.2058e-05 | 4.4388e-09 | -2.9772e-07 | 0.00055331 | 0.00055321 | 0.00055331 | 0.99101 | -0.062601 | 0.99102 | -0.062514 | 0.20493
1 | -0.002042 | -0.00051148 | 0.0020425 | 0.0005106 | 4.8521e-07 | -8.7959e-07 | 0.003066 | 0.0030656 | 0.003066 | 0.99102 | -0.062514 | 0.99127 | -0.060792 | 1.1356
2 | -0.00052895 | -0.00013257 | 0.00052895 | 0.00013247 | 3.2493e-09 | -9.7164e-08 | 0.0008098 | 0.00080977 | 0.0008098 | 0.97194 | -0.19821 | 0.97195 | -0.19817 | 0.29993
3 | -0.007135 | -0.0017881 | 0.0071475 | 0.0017908 | 1.2433e-05 | 2.7084e-06 | 0.010923 | 0.010923 | 0.010923 | 0.97195 | -0.19817 | 0.9737 | -0.18559 | 4.0457
4 | -0.0093813 | -0.0023507 | 0.0094105 | 0.0023591 | 2.926e-05 | 8.4069e-06 | 0.014336 | 0.014335 | 0.014336 | 0.9737 | -0.18559 | 0.97683 | -0.16309 | 5.3098
5 | 0.0021386 | 0.00053473 | -0.0021383 | -0.00053516 | 2.8422e-07 | -4.2798e-07 | 0.0032573 | 0.0032575 | 0.0032575 | 0.97683 | -0.16309 | 0.9767 | -0.16406 | 1.2065
6 | 0.0032181 | 0.00080298 | -0.003214 | -0.0008048 | 4.0485e-06 | -1.8192e-06 | 0.0049009 | 0.0049021 | 0.0049021 | 0.97683 | -0.16309 | 0.97556 | -0.17223 | 1.8156
7 | -0.014767 | -0.0036968 | 0.014805 | 0.0037097 | 3.7398e-05 | 1.2897e-05 | 0.022494 | 0.022493 | 0.022494 | 0.97683 | -0.16309 | 0.97938 | -0.1448 | 8.331
8 | 0.0021383 | 0.00053516 | -0.0021379 | -0.00053581 | 4.3036e-07 | -6.4762e-07 | 0.0032575 | 0.0032578 | 0.0032578 | 0.9767 | -0.16406 | 0.97649 | -0.16551 | 1.2066
9 | 0.003214 | 0.0008048 | -0.0032132 | -0.00080519 | 8.7746e-07 | -3.9291e-07 | 0.0049021 | 0.0049023 | 0.0049023 | 0.97556 | -0.17223 | 0.97529 | -0.17421 | 1.8157
10 | -0.02788 | -0.0069867 | 0.02794 | 0.0070089 | 5.935e-05 | 2.2158e-05 | 0.042359 | 0.042359 | 0.042359 | 0.97938 | -0.1448 | 0.98153 | -0.12945 | 15.6887
11 | 0.001014 | 0.00025403 | -0.001014 | -0.00025412 | 1.1937e-08 | -9.5154e-08 | 0.001547 | 0.0015471 | 0.0015471 | 0.97529 | -0.17421 | 0.97528 | -0.17429 | 0.57298
12 | -0.056759 | -0.014232 | 0.056957 | 0.014306 | 0.00019884 | 7.4293e-05 | 0.086049 | 0.086048 | 0.086049 | 0.98153 | -0.12945 | 0.98508 | -0.10426 | 15.935
13 | -0.084366 | -0.0213 | 0.084388 | 0.021308 | 2.1939e-05 | 8.3213e-06 | 0.12563 | 0.12563 | 0.12563 | 0.99973 | -0.0018505 | 1 | 0 | 23.2642
14 | 0.081841 | 0.020667 | -0.081409 | -0.020503 | 0.00043183 | 0.00016366 | 0.12187 | 0.12187 | 0.12187 | 0.99973 | -0.0018505 | 0.99429 | -0.039591 | 22.5683
15 | 0.017929 | 0.0044957 | -0.017917 | -0.0044912 | 1.2656e-05 | 4.4943e-06 | 0.02668 | 0.02668 | 0.02668 | 1 | 0 | 0.99927 | -0.0050975 | 9.8816
16 | 0.071548 | 0.018032 | -0.071402 | -0.017977 | 0.0001456 | 5.4949e-05 | 0.10711 | 0.10711 | 0.10711 | 0.99429 | -0.039591 | 0.9922 | -0.054158 | 19.8355
17 | 0.014833 | 0.0037183 | -0.014824 | -0.0037152 | 9.0834e-06 | 3.103e-06 | 0.022088 | 0.022088 | 0.022088 | 0.99927 | -0.0050975 | 0.99864 | -0.0095214 | 8.1809
18 | 0.0088914 | 0.0022272 | -0.0088832 | -0.002225 | 8.1532e-06 | 2.1876e-06 | 0.013334 | 0.013334 | 0.013334 | 0.9922 | -0.054158 | 0.99127 | -0.060792 | 4.9387
19 | 0.062511 | 0.01575 | -0.062298 | -0.01567 | 0.00021278 | 7.9843e-05 | 0.093778 | 0.093778 | 0.093778 | 0.9922 | -0.054158 | 0.98872 | -0.07857 | 17.3664
20 | 0.062298 | 0.01567 | -0.062283 | -0.015664 | 1.5171e-05 | 5.6931e-06 | 0.093778 | 0.093778 | 0.093778 | 0.98872 | -0.07857 | 0.98847 | -0.080317 | 17.3664
21 | 0.057148 | 0.014377 | -0.057039 | -0.014336 | 0.00010875 | 4.0623e-05 | 0.086048 | 0.086048 | 0.086048 | 0.98847 | -0.080317 | 0.98653 | -0.093985 | 15.9348
22 | -0.056957 | -0.014306 | 0.057039 | 0.014336 | 8.1447e-05 | 3.0427e-05 | 0.086048 | 0.086048 | 0.086048 | 0.98508 | -0.10426 | 0.98653 | -0.093985 | 15.9349

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.12094 | 0.03027

## res_load
| p_mw | q_mvar
0 | 0.0003685 | 9.2356e-05
1 | 0.0016735 | 0.00041942
2 | 0.00052895 | 0.00013257
3 | 0.0066061 | 0.0016556
4 | 0.0022338 | 0.00055985
5 | 0.013076 | 0.0032771
6 | 0.0021379 | 0.00053581
7 | 0.0021992 | 0.00055116
8 | 0.028819 | 0.0072227
9 | 0.0025253 | 0.0006329
10 | 0.01782 | 0.0044662
11 | 0.009861 | 0.0024714
12 | 0.0030838 | 0.00077287
13 | 0.014824 | 0.0037152
14 | 0.0068407 | 0.0017144
15 | 0.0051355 | 0.0012871
16 | 0.001014 | 0.00025412

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1