## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1143-7_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1143-7_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1143-7_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1143-7_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1143-7_0_2_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1143-7_0_2_node_8 | 0.4 | n |  | TRUE
6 | bus_LV_1143-7_0_2_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_1143-7_0_2_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_1143-7_0_2_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1143-7_0_2_node_12 | 0.4 | n |  | TRUE
10 | bus_LV_1143-7_0_2_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1143-7_0_2_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_1143-7_0_2_node_15 | 0.4 | n |  | TRUE
13 | bus_LV_1143-7_0_2_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_1143-7_0_2_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1143-7_0_2_node_17 | 0.4 | n |  | TRUE
16 | bus_LV_1143-7_0_2_node_34 | 0.4 | n |  | TRUE
17 | bus_LV_1143-7_0_2_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1143-7_0_2_node_30 | 0.4 | n |  | TRUE
19 | bus_LV_1143-7_0_2_node_29 | 0.4 | n |  | TRUE
20 | bus_LV_1143-7_0_2_node_18 | 0.4 | n |  | TRUE
21 | bus_LV_1143-7_0_2_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1143-7_0_2_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1143-7_0_2_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_1143-7_0_2_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1143-7_0_2_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_1143-7_0_2_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1143-7_0_2_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_1143-7_0_2_node_19 | 0.4 | n |  | TRUE
29 | bus_LV_1143-7_0_2_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_1143-7_0_2_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1143-7_0_2_node_32 | 0.4 | n |  | TRUE
32 | bus_MV_131_0_node_72 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1143-7_0_2_load_0 | 0 | 0.01258 | 0.003153 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1143-7_0_2_load_7 | 4 | 0.0012424 | 0.00031138 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1143-7_0_2_load_8 | 5 | 0.022788 | 0.0057111 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1143-7_0_2_load_16 | 7 | 0.0097596 | 0.002446 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1143-7_0_2_load_12 | 9 | 0.0036382 | 0.00091181 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1143-7_0_2_load_9 | 10 | 0.0016796 | 0.00042095 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1143-7_0_2_load_33 | 11 | 0.0010964 | 0.00027478 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1143-7_0_2_load_10 | 14 | 0.0020324 | 0.00050938 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1143-7_0_2_load_17 | 15 | 0.011402 | 0.0028576 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1143-7_0_2_load_34 | 16 | 0.0015152 | 0.00037975 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1143-7_0_2_load_11 | 17 | 0.0035993 | 0.00090207 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1143-7_0_2_load_30 | 18 | 0.02172 | 0.0054435 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1143-7_0_2_load_29 | 19 | 0.0018542 | 0.00046471 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1143-7_0_2_load_18 | 20 | 0.0038823 | 0.00097299 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1143-7_0_2_load_13 | 21 | 0.0097592 | 0.0024459 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1143-7_0_2_load_14 | 22 | 0.022696 | 0.0056882 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1143-7_0_2_load_23 | 23 | 0.0070307 | 0.0017621 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1143-7_0_2_load_22 | 24 | 0.0034025 | 0.00085274 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1143-7_0_2_load_28 | 27 | 0.0010811 | 0.00027095 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1143-7_0_2_load_19 | 28 | 0.012229 | 0.0030649 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1143-7_0_2_load_21 | 29 | 0.0012732 | 0.0003191 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1143-7_0_2_load_31 | 30 | 0.0019569 | 0.00049045 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1143-7_0_2_load_32 | 31 | 0.0052706 | 0.0013209 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1143-7_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020249 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1143-7_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.021609 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1143-7_0_2_line_2 | NAYY 4x150 SE | 1 | 3 | 0.044281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1143-7_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.03662 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1143-7_0_2_line_4 | NAYY 4x150 SE | 2 | 5 | 0.026949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1143-7_0_2_line_5 | NAYY 4x150 SE | 3 | 6 | 0.036757 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1143-7_0_2_line_6 | NAYY 4x150 SE | 4 | 11 | 0.032689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1143-7_0_2_line_7 | NAYY 4x150 SE | 6 | 7 | 0.017171 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1143-7_0_2_line_8 | NAYY 4x150 SE | 7 | 12 | 0.0088707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1143-7_0_2_line_9 | NAYY 4x150 SE | 8 | 9 | 0.037732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1143-7_0_2_line_10 | NAYY 4x150 SE | 8 | 10 | 0.01418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1143-7_0_2_line_11 | NAYY 4x150 SE | 9 | 13 | 0.045332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1143-7_0_2_line_12 | NAYY 4x150 SE | 10 | 14 | 0.0025409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1143-7_0_2_line_13 | NAYY 4x150 SE | 11 | 16 | 0.010837 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1143-7_0_2_line_14 | NAYY 4x150 SE | 12 | 15 | 0.021319 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1143-7_0_2_line_15 | NAYY 4x150 SE | 12 | 21 | 0.0063545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1143-7_0_2_line_16 | NAYY 4x150 SE | 13 | 20 | 0.031117 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1143-7_0_2_line_17 | NAYY 4x150 SE | 14 | 17 | 0.021781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1143-7_0_2_line_18 | NAYY 4x150 SE | 16 | 31 | 0.003592 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1143-7_0_2_line_19 | NAYY 4x150 SE | 17 | 18 | 0.016844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1143-7_0_2_line_20 | NAYY 4x150 SE | 18 | 19 | 0.023339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1143-7_0_2_line_21 | NAYY 4x150 SE | 19 | 30 | 0.0085719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1143-7_0_2_line_22 | NAYY 4x150 SE | 20 | 28 | 0.00217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1143-7_0_2_line_23 | NAYY 4x150 SE | 21 | 22 | 0.023275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1143-7_0_2_line_24 | NAYY 4x150 SE | 22 | 23 | 0.18606 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1143-7_0_2_line_25 | NAYY 4x150 SE | 23 | 25 | 0.1083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1143-7_0_2_line_26 | NAYY 4x150 SE | 23 | 24 | 0.0087276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1143-7_0_2_line_27 | NAYY 4x150 SE | 25 | 26 | 0.10909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1143-7_0_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.011759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1143-7_0_2_line_29 | NAYY 4x150 SE | 28 | 29 | 0.023212 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1143-7_0_2_line_30 | NAYY 4x150 SE | 30 | 31 | 0.012295 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1143-7_0_2_trafo_8 | 0.25 MVA 20/0.4 kV | 32 | 5 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2642036.306 | 1224384.9402 | 2642056.4275 | 1224387.2058
1 | 2642077.7367 | 1224384.4768 | 2642069.51 | 1224386.6756 | 2642056.4275 | 1224387.2058
2 | 2642041.5093 | 1224421.1545 | 2642032.1203 | 1224419.3872 | 2642032.5424 | 1224416.5106 | 2642033.9189 | 1224409.4827 | 2642036.306 | 1224384.9402
3 | 2642077.7367 | 1224384.4768 | 2642081.3297 | 1224383.5128 | 2642093.1648 | 1224377.1036 | 2642104.4267 | 1224367.0548 | 2642106.8309 | 1224363.4322
4 | 2642077.7367 | 1224384.4768 | 2642079.2601 | 1224387.7674 | 2642081.8292 | 1224393.3 | 2642082.5292 | 1224394.0165 | 2642086.7644 | 1224394.4467 | 2642090.8233 | 1224397.2993 | 2642090.0363 | 1224402.4524 | 2642091.1409 | 1224403.8611
5 | 2642041.5093 | 1224421.1545 | 2642044.5077 | 1224421.7204 | 2642044.076 | 1224423.8075 | 2642037.8435 | 1224453.904 | 2642037.6709 | 1224454.7255
6 | 2642106.8309 | 1224363.4322 | 2642110.5883 | 1224357.7705 | 2642115.1359 | 1224347.263 | 2642117.3091 | 1224332.9827
7 | 2642037.6709 | 1224454.7255 | 2642054.53 | 1224457.9821
8 | 2642063.2397 | 1224459.6646 | 2642054.53 | 1224457.9821
9 | 2642029.3687 | 1224275.3581 | 2642055.2217 | 1224247.8754
10 | 2642029.3687 | 1224275.3581 | 2642039.9702 | 1224284.7747
11 | 2642086.2824 | 1224214.8565 | 2642055.2217 | 1224247.8754
12 | 2642039.9702 | 1224284.7747 | 2642041.8699 | 1224286.4621
13 | 2642117.3091 | 1224332.9827 | 2642118.1257 | 1224327.6166 | 2642116.9423 | 1224322.3384
14 | 2642063.2397 | 1224459.6646 | 2642060.1955 | 1224476.3198 | 2642058.7747 | 1224480.4714
15 | 2642063.2397 | 1224459.6646 | 2642069.4784 | 1224460.8722
16 | 2642086.2824 | 1224214.8565 | 2642113.3929 | 1224226.0104 | 2642115.0954 | 1224226.5987
17 | 2642058.1546 | 1224300.9266 | 2642041.8699 | 1224286.4621
18 | 2642114.5197 | 1224319.6863 | 2642116.9423 | 1224322.3384 | 2642116.9423 | 1224322.3384
19 | 2642071.262 | 1224311.4646 | 2642071.262 | 1224311.4646 | 2642065.1889 | 1224307.1747 | 2642058.1546 | 1224300.9266
20 | 2642071.262 | 1224311.4646 | 2642076.9414 | 1224313.5393 | 2642094.0731 | 1224315.8908
21 | 2642102.5654 | 1224317.0564 | 2642094.0731 | 1224315.8908
22 | 2642117.1464 | 1224227.3074 | 2642115.0954 | 1224226.5987
23 | 2642092.3291 | 1224465.2956 | 2642069.4784 | 1224460.8722
24 | 2642092.3291 | 1224465.2956 | 2642245.9897 | 1224570.2131
25 | 2642222.0496 | 1224662.5333 | 2642208.53 | 1224627.4829 | 2642207.3468 | 1224622.2046 | 2642207.9835 | 1224617.951 | 2642245.9897 | 1224570.2131
26 | 2642251.4257 | 1224563.3852 | 2642245.9897 | 1224570.2131
27 | 2642311.689 | 1224604.4896 | 2642269.9953 | 1224619.8029 | 2642255.2969 | 1224628.0147 | 2642241.7948 | 1224639.6816 | 2642222.0496 | 1224662.5333
28 | 2642311.689 | 1224604.4896 | 2642319.4747 | 1224595.6771
29 | 2642117.1464 | 1224227.3074 | 2642138.2922 | 1224234.6139 | 2642139.0886 | 1224234.8796
30 | 2642114.5197 | 1224319.6863 | 2642114.5197 | 1224319.6863 | 2642109.6486 | 1224318.0287 | 2642102.5654 | 1224317.0564

## bus_geodata
| x | y | coords
0 | 2642056.4275 | 1224387.2058
1 | 2642036.306 | 1224384.9402
2 | 2642077.7367 | 1224384.4769
3 | 2642041.5093 | 1224421.1545
4 | 2642106.8309 | 1224363.4322
5 | 2642091.1409 | 1224403.8611
6 | 2642037.6709 | 1224454.7255
7 | 2642054.53 | 1224457.9821
8 | 2642029.3687 | 1224275.3581
9 | 2642055.2217 | 1224247.8754
10 | 2642039.9702 | 1224284.7747
11 | 2642117.3091 | 1224332.9827
12 | 2642063.2397 | 1224459.6646
13 | 2642086.2824 | 1224214.8565
14 | 2642041.8699 | 1224286.4621
15 | 2642058.7747 | 1224480.4714
16 | 2642116.9423 | 1224322.3384
17 | 2642058.1546 | 1224300.9266
18 | 2642071.262 | 1224311.4646
19 | 2642094.0731 | 1224315.8908
20 | 2642115.0954 | 1224226.5987
21 | 2642069.4784 | 1224460.8722
22 | 2642092.3291 | 1224465.2956
23 | 2642245.9897 | 1224570.2131
24 | 2642251.4257 | 1224563.3852
25 | 2642222.0496 | 1224662.5333
26 | 2642311.689 | 1224604.4896
27 | 2642319.4747 | 1224595.6771
28 | 2642117.1464 | 1224227.3074
29 | 2642139.0886 | 1224234.8796
30 | 2642102.5654 | 1224317.0564
31 | 2642114.5197 | 1224319.6863
32 | 2642077.7367 | 1224384.4769

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99482 | -0.035892 | 0.01258 | 0.003153
1 | 0.99291 | -0.049228 | 0 | 0
2 | 0.99725 | -0.018986 | 0 | 0
3 | 0.98872 | -0.078573 | 0 | 0
4 | 0.99392 | -0.042223 | 0.0012424 | 0.00031138
5 | 1 | 0 | -0.14366 | -0.03608
6 | 0.98524 | -0.10312 | 0 | 0
7 | 0.98362 | -0.11464 | 0.0097596 | 0.002446
8 | 0.98445 | -0.10891 | 0 | 0
9 | 0.9833 | -0.1171 | 0.0036382 | 0.00091181
10 | 0.98489 | -0.10584 | 0.0016796 | 0.00042095
11 | 0.991 | -0.062684 | 0.0010964 | 0.00027478
12 | 0.9829 | -0.11972 | 0 | 0
13 | 0.98216 | -0.12524 | 0 | 0
14 | 0.98497 | -0.10525 | 0.0020324 | 0.00050938
15 | 0.98255 | -0.12223 | 0.011402 | 0.0028576
16 | 0.99005 | -0.069372 | 0.0015152 | 0.00037975
17 | 0.98575 | -0.099708 | 0.0035993 | 0.00090207
18 | 0.98644 | -0.094806 | 0.02172 | 0.0054435
19 | 0.98814 | -0.08284 | 0.0018542 | 0.00046471
20 | 0.98137 | -0.13085 | 0.0038823 | 0.00097299
21 | 0.9825 | -0.12261 | 0.0097592 | 0.0024459
22 | 0.98134 | -0.13086 | 0.022696 | 0.0056882
23 | 0.97822 | -0.1532 | 0.0070307 | 0.0017621
24 | 0.97817 | -0.1535 | 0.0034025 | 0.00085274
25 | 0.97805 | -0.15444 | 0 | 0
26 | 0.97787 | -0.15567 | 0 | 0
27 | 0.97786 | -0.15581 | 0.0010811 | 0.00027095
28 | 0.98133 | -0.13115 | 0.012229 | 0.0030649
29 | 0.98129 | -0.13146 | 0.0012732 | 0.0003191
30 | 0.98878 | -0.078294 | 0.0019569 | 0.00049045
31 | 0.98974 | -0.071537 | 0.0052706 | 0.0013209
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.065988 | 0.016645 | -0.065865 | -0.016598 | 0.00012319 | 4.7118e-05 | 0.098741 | 0.098741 | 0.098741 | 0.99482 | -0.035892 | 0.99291 | -0.049228 | 36.5706
1 | -0.078569 | -0.019798 | 0.078755 | 0.01987 | 0.00018634 | 7.139e-05 | 0.11756 | 0.11756 | 0.11756 | 0.99482 | -0.035892 | 0.99725 | -0.018986 | 43.54
2 | 0.065865 | 0.016598 | -0.065596 | -0.016495 | 0.0002694 | 0.00010304 | 0.098741 | 0.098741 | 0.098741 | 0.99291 | -0.049228 | 0.98872 | -0.078573 | 36.5707
3 | 0.063723 | 0.016064 | -0.063516 | -0.015985 | 0.00020673 | 7.9035e-05 | 0.095115 | 0.095115 | 0.095115 | 0.99725 | -0.018986 | 0.99392 | -0.042223 | 35.2277
4 | -0.14248 | -0.035934 | 0.14286 | 0.03608 | 0.00038029 | 0.00014556 | 0.21267 | 0.21267 | 0.21267 | 0.99725 | -0.018986 | 1 | 0 | 39.3838
5 | 0.065596 | 0.016495 | -0.065372 | -0.01641 | 0.00022363 | 8.554e-05 | 0.098741 | 0.098741 | 0.098741 | 0.98872 | -0.078573 | 0.98524 | -0.10312 | 36.5708
6 | 0.062274 | 0.015674 | -0.062096 | -0.015606 | 0.00017739 | 6.7805e-05 | 0.093255 | 0.093255 | 0.093255 | 0.99392 | -0.042223 | 0.991 | -0.062684 | 34.5389
7 | 0.065372 | 0.01641 | -0.065268 | -0.01637 | 0.00010446 | 3.996e-05 | 0.098741 | 0.098741 | 0.098741 | 0.98524 | -0.10312 | 0.98362 | -0.11464 | 36.5708
8 | 0.055508 | 0.013924 | -0.055469 | -0.013909 | 3.9036e-05 | 1.4901e-05 | 0.083977 | 0.083977 | 0.083977 | 0.98362 | -0.11464 | 0.9829 | -0.11972 | 31.1025
9 | 0.021081 | 0.0052893 | -0.021057 | -0.0052805 | 2.3908e-05 | 8.7162e-06 | 0.031866 | 0.031866 | 0.031866 | 0.98445 | -0.10891 | 0.9833 | -0.1171 | 11.8022
10 | -0.021081 | -0.0052893 | 0.02109 | 0.0052925 | 8.9846e-06 | 3.2753e-06 | 0.031866 | 0.031866 | 0.031866 | 0.98445 | -0.10891 | 0.98489 | -0.10584 | 11.8021
11 | 0.017419 | 0.0043687 | -0.017399 | -0.0043618 | 1.9656e-05 | 6.9857e-06 | 0.02636 | 0.026361 | 0.026361 | 0.9833 | -0.1171 | 0.98216 | -0.12524 | 9.7632
12 | -0.022769 | -0.0057135 | 0.022771 | 0.0057142 | 1.8766e-06 | 6.8944e-07 | 0.034403 | 0.034403 | 0.034403 | 0.98489 | -0.10584 | 0.98497 | -0.10525 | 12.742
13 | 0.061 | 0.015331 | -0.060943 | -0.01531 | 5.6751e-05 | 2.1688e-05 | 0.091609 | 0.091609 | 0.091609 | 0.991 | -0.062684 | 0.99005 | -0.069372 | 33.9292
14 | 0.011406 | 0.0028589 | -0.011402 | -0.0028576 | 3.9667e-06 | 1.2555e-06 | 0.017268 | 0.017268 | 0.017268 | 0.9829 | -0.11972 | 0.98255 | -0.12223 | 6.3955
15 | 0.044063 | 0.01105 | -0.044045 | -0.011043 | 1.7646e-05 | 6.7063e-06 | 0.066709 | 0.066709 | 0.066709 | 0.9829 | -0.11972 | 0.9825 | -0.12261 | 24.7071
16 | 0.017399 | 0.0043618 | -0.017385 | -0.004357 | 1.3492e-05 | 4.7959e-06 | 0.026361 | 0.026361 | 0.026361 | 0.98216 | -0.12524 | 0.98137 | -0.13085 | 9.7632
17 | -0.024804 | -0.0062236 | 0.024823 | 0.0062306 | 1.9086e-05 | 7.0634e-06 | 0.037474 | 0.037474 | 0.037474 | 0.98497 | -0.10525 | 0.98575 | -0.099708 | 13.8792
18 | 0.059428 | 0.01493 | -0.05941 | -0.014923 | 1.7887e-05 | 6.8333e-06 | 0.089331 | 0.089331 | 0.089331 | 0.99005 | -0.069372 | 0.98974 | -0.071537 | 33.0857
19 | -0.028422 | -0.0071327 | 0.028441 | 0.0071399 | 1.935e-05 | 7.2275e-06 | 0.042907 | 0.042907 | 0.042907 | 0.98575 | -0.099708 | 0.98644 | -0.094806 | 15.8915
20 | -0.050161 | -0.012583 | 0.050244 | 0.012615 | 8.339e-05 | 3.1775e-05 | 0.07567 | 0.07567 | 0.07567 | 0.98644 | -0.094806 | 0.98814 | -0.08284 | 28.0261
21 | -0.052099 | -0.01308 | 0.052132 | 0.013092 | 3.293e-05 | 1.2555e-05 | 0.078463 | 0.078463 | 0.078463 | 0.98814 | -0.08284 | 0.98878 | -0.078294 | 29.0602
22 | 0.013503 | 0.003384 | -0.013503 | -0.0033838 | 5.6763e-07 | 1.909e-07 | 0.020474 | 0.020474 | 0.020474 | 0.98137 | -0.13085 | 0.98133 | -0.13115 | 7.583
23 | 0.034286 | 0.0085973 | -0.034247 | -0.0085826 | 3.9164e-05 | 1.4769e-05 | 0.051929 | 0.051929 | 0.051929 | 0.9825 | -0.12261 | 0.98134 | -0.13086 | 19.2328
24 | 0.01155 | 0.0028943 | -0.011515 | -0.002883 | 3.5615e-05 | 1.1355e-05 | 0.017514 | 0.017515 | 0.017515 | 0.98134 | -0.13086 | 0.97822 | -0.1532 | 6.4869
25 | 0.0010815 | 0.00026822 | -0.0010813 | -0.00026951 | 1.8272e-07 | -1.289e-06 | 0.0016441 | 0.0016446 | 0.0016446 | 0.97822 | -0.1532 | 0.97805 | -0.15444 | 0.6091
26 | 0.0034026 | 0.00085269 | -0.0034025 | -0.00085274 | 1.459e-07 | -5.3446e-08 | 0.0051759 | 0.0051759 | 0.0051759 | 0.97822 | -0.1532 | 0.97817 | -0.1535 | 1.917
27 | 0.0010813 | 0.00026951 | -0.0010811 | -0.00027081 | 1.8416e-07 | -1.2979e-06 | 0.0016446 | 0.0016451 | 0.0016451 | 0.97805 | -0.15444 | 0.97787 | -0.15567 | 0.60928
28 | 0.0010811 | 0.00027081 | -0.0010811 | -0.00027095 | 1.9858e-08 | -1.3988e-07 | 0.0016451 | 0.0016451 | 0.0016451 | 0.97787 | -0.15567 | 0.97786 | -0.15581 | 0.6093
29 | 0.0012733 | 0.00031883 | -0.0012732 | -0.0003191 | 5.399e-08 | -2.7248e-07 | 0.0019306 | 0.0019307 | 0.0019307 | 0.98133 | -0.13115 | 0.98129 | -0.13146 | 0.71508
30 | -0.054089 | -0.013583 | 0.054139 | 0.013602 | 5.0844e-05 | 1.9398e-05 | 0.081407 | 0.081407 | 0.081407 | 0.98878 | -0.078294 | 0.98974 | -0.071537 | 30.1509

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16645 | 0.041791

## res_load
| p_mw | q_mvar
0 | 0.01258 | 0.003153
1 | 0.0012424 | 0.00031138
2 | 0.022788 | 0.0057111
3 | 0.0097596 | 0.002446
4 | 0.0036382 | 0.00091181
5 | 0.0016796 | 0.00042095
6 | 0.0010964 | 0.00027478
7 | 0.0020324 | 0.00050938
8 | 0.011402 | 0.0028576
9 | 0.0015152 | 0.00037975
10 | 0.0035993 | 0.00090207
11 | 0.02172 | 0.0054435
12 | 0.0018542 | 0.00046471
13 | 0.0038823 | 0.00097299
14 | 0.0097592 | 0.0024459
15 | 0.022696 | 0.0056882
16 | 0.0070307 | 0.0017621
17 | 0.0034025 | 0.00085274
18 | 0.0010811 | 0.00027095
19 | 0.012229 | 0.0030649
20 | 0.0012732 | 0.0003191
21 | 0.0019569 | 0.00049045
22 | 0.0052706 | 0.0013209

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1