## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1145-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1145-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1145-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1145-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1145-2_0_4_node_43 | 0.4 | n |  | TRUE
5 | bus_LV_1145-2_0_4_node_45 | 0.4 | n |  | TRUE
6 | bus_LV_1145-2_0_4_node_41 | 0.4 | n |  | TRUE
7 | bus_LV_1145-2_0_4_node_23 | 0.4 | n |  | TRUE
8 | bus_LV_1145-2_0_4_node_105 | 0.4 | n |  | TRUE
9 | bus_LV_1145-2_0_4_node_103 | 0.4 | n |  | TRUE
10 | bus_LV_1145-2_0_4_node_112 | 0.4 | n |  | TRUE
11 | bus_LV_1145-2_0_4_node_104 | 0.4 | n |  | TRUE
12 | bus_LV_1145-2_0_4_node_42 | 0.4 | n |  | TRUE
13 | bus_LV_1145-2_0_4_node_44 | 0.4 | n |  | TRUE
14 | bus_LV_1145-2_0_4_node_61 | 0.4 | n |  | TRUE
15 | bus_LV_1145-2_0_4_node_63 | 0.4 | n |  | TRUE
16 | bus_LV_1145-2_0_4_node_48 | 0.4 | n |  | TRUE
17 | bus_LV_1145-2_0_4_node_60 | 0.4 | n |  | TRUE
18 | bus_LV_1145-2_0_4_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_1145-2_0_4_node_52 | 0.4 | n |  | TRUE
20 | bus_LV_1145-2_0_4_node_53 | 0.4 | n |  | TRUE
21 | bus_LV_1145-2_0_4_node_71 | 0.4 | n |  | TRUE
22 | bus_LV_1145-2_0_4_node_90 | 0.4 | n |  | TRUE
23 | bus_LV_1145-2_0_4_node_87 | 0.4 | n |  | TRUE
24 | bus_LV_1145-2_0_4_node_91 | 0.4 | n |  | TRUE
25 | bus_LV_1145-2_0_4_node_54 | 0.4 | n |  | TRUE
26 | bus_LV_1145-2_0_4_node_55 | 0.4 | n |  | TRUE
27 | bus_LV_1145-2_0_4_node_56 | 0.4 | n |  | TRUE
28 | bus_LV_1145-2_0_4_node_57 | 0.4 | n |  | TRUE
29 | bus_LV_1145-2_0_4_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_1145-2_0_4_node_73 | 0.4 | n |  | TRUE
31 | bus_LV_1145-2_0_4_node_223 | 0.4 | n |  | TRUE
32 | bus_LV_1145-2_0_4_node_72 | 0.4 | n |  | TRUE
33 | bus_LV_1145-2_0_4_node_206 | 0.4 | n |  | TRUE
34 | bus_LV_1145-2_0_4_node_62 | 0.4 | n |  | TRUE
35 | bus_LV_1145-2_0_4_node_64 | 0.4 | n |  | TRUE
36 | bus_LV_1145-2_0_4_node_65 | 0.4 | n |  | TRUE
37 | bus_LV_1145-2_0_4_node_66 | 0.4 | n |  | TRUE
38 | bus_LV_1145-2_0_4_node_67 | 0.4 | n |  | TRUE
39 | bus_LV_1145-2_0_4_node_68 | 0.4 | n |  | TRUE
40 | bus_LV_1145-2_0_4_node_69 | 0.4 | n |  | TRUE
41 | bus_LV_1145-2_0_4_node_70 | 0.4 | n |  | TRUE
42 | bus_LV_1145-2_0_4_node_75 | 0.4 | n |  | TRUE
43 | bus_LV_1145-2_0_4_node_127 | 0.4 | n |  | TRUE
44 | bus_LV_1145-2_0_4_node_76 | 0.4 | n |  | TRUE
45 | bus_LV_1145-2_0_4_node_79 | 0.4 | n |  | TRUE
46 | bus_LV_1145-2_0_4_node_74 | 0.4 | n |  | TRUE
47 | bus_LV_1145-2_0_4_node_126 | 0.4 | n |  | TRUE
48 | bus_LV_1145-2_0_4_node_77 | 0.4 | n |  | TRUE
49 | bus_LV_1145-2_0_4_node_78 | 0.4 | n |  | TRUE
50 | bus_LV_1145-2_0_4_node_86 | 0.4 | n |  | TRUE
51 | bus_LV_1145-2_0_4_node_120 | 0.4 | n |  | TRUE
52 | bus_LV_1145-2_0_4_node_228 | 0.4 | n |  | TRUE
53 | bus_LV_1145-2_0_4_node_80 | 0.4 | n |  | TRUE
54 | bus_LV_1145-2_0_4_node_81 | 0.4 | n |  | TRUE
55 | bus_LV_1145-2_0_4_node_97 | 0.4 | n |  | TRUE
56 | bus_LV_1145-2_0_4_node_95 | 0.4 | n |  | TRUE
57 | bus_LV_1145-2_0_4_node_82 | 0.4 | n |  | TRUE
58 | bus_LV_1145-2_0_4_node_83 | 0.4 | n |  | TRUE
59 | bus_LV_1145-2_0_4_node_84 | 0.4 | n |  | TRUE
60 | bus_LV_1145-2_0_4_node_118 | 0.4 | n |  | TRUE
61 | bus_LV_1145-2_0_4_node_85 | 0.4 | n |  | TRUE
62 | bus_LV_1145-2_0_4_node_125 | 0.4 | n |  | TRUE
63 | bus_LV_1145-2_0_4_node_114 | 0.4 | n |  | TRUE
64 | bus_LV_1145-2_0_4_node_88 | 0.4 | n |  | TRUE
65 | bus_LV_1145-2_0_4_node_89 | 0.4 | n |  | TRUE
66 | bus_LV_1145-2_0_4_node_226 | 0.4 | n |  | TRUE
67 | bus_LV_1145-2_0_4_node_135 | 0.4 | n |  | TRUE
68 | bus_LV_1145-2_0_4_node_92 | 0.4 | n |  | TRUE
69 | bus_LV_1145-2_0_4_node_93 | 0.4 | n |  | TRUE
70 | bus_LV_1145-2_0_4_node_94 | 0.4 | n |  | TRUE
71 | bus_LV_1145-2_0_4_node_96 | 0.4 | n |  | TRUE
72 | bus_LV_1145-2_0_4_node_100 | 0.4 | n |  | TRUE
73 | bus_LV_1145-2_0_4_node_102 | 0.4 | n |  | TRUE
74 | bus_LV_1145-2_0_4_node_98 | 0.4 | n |  | TRUE
75 | bus_LV_1145-2_0_4_node_99 | 0.4 | n |  | TRUE
76 | bus_LV_1145-2_0_4_node_101 | 0.4 | n |  | TRUE
77 | bus_LV_1145-2_0_4_node_139 | 0.4 | n |  | TRUE
78 | bus_LV_1145-2_0_4_node_119 | 0.4 | n |  | TRUE
79 | bus_LV_1145-2_0_4_node_188 | 0.4 | n |  | TRUE
80 | bus_LV_1145-2_0_4_node_122 | 0.4 | n |  | TRUE
81 | bus_LV_1145-2_0_4_node_121 | 0.4 | n |  | TRUE
82 | bus_LV_1145-2_0_4_node_117 | 0.4 | n |  | TRUE
83 | bus_LV_1145-2_0_4_node_106 | 0.4 | n |  | TRUE
84 | bus_LV_1145-2_0_4_node_107 | 0.4 | n |  | TRUE
85 | bus_LV_1145-2_0_4_node_128 | 0.4 | n |  | TRUE
86 | bus_LV_1145-2_0_4_node_136 | 0.4 | n |  | TRUE
87 | bus_LV_1145-2_0_4_node_110 | 0.4 | n |  | TRUE
88 | bus_LV_1145-2_0_4_node_129 | 0.4 | n |  | TRUE
89 | bus_LV_1145-2_0_4_node_137 | 0.4 | n |  | TRUE
90 | bus_LV_1145-2_0_4_node_108 | 0.4 | n |  | TRUE
91 | bus_LV_1145-2_0_4_node_109 | 0.4 | n |  | TRUE
92 | bus_LV_1145-2_0_4_node_111 | 0.4 | n |  | TRUE
93 | bus_LV_1145-2_0_4_node_113 | 0.4 | n |  | TRUE
94 | bus_LV_1145-2_0_4_node_115 | 0.4 | n |  | TRUE
95 | bus_LV_1145-2_0_4_node_116 | 0.4 | n |  | TRUE
96 | bus_LV_1145-2_0_4_node_227 | 0.4 | n |  | TRUE
97 | bus_LV_1145-2_0_4_node_123 | 0.4 | n |  | TRUE
98 | bus_LV_1145-2_0_4_node_124 | 0.4 | n |  | TRUE
99 | bus_LV_1145-2_0_4_node_130 | 0.4 | n |  | TRUE
100 | bus_LV_1145-2_0_4_node_131 | 0.4 | n |  | TRUE
101 | bus_LV_1145-2_0_4_node_132 | 0.4 | n |  | TRUE
102 | bus_LV_1145-2_0_4_node_133 | 0.4 | n |  | TRUE
103 | bus_LV_1145-2_0_4_node_134 | 0.4 | n |  | TRUE
104 | bus_LV_1145-2_0_4_node_224 | 0.4 | n |  | TRUE
105 | bus_LV_1145-2_0_4_node_225 | 0.4 | n |  | TRUE
106 | bus_LV_1145-2_0_4_node_138 | 0.4 | n |  | TRUE
107 | bus_LV_1145-2_0_4_node_189 | 0.4 | n |  | TRUE
108 | bus_LV_1145-2_0_4_node_190 | 0.4 | n |  | TRUE
109 | bus_LV_1145-2_0_4_node_191 | 0.4 | n |  | TRUE
110 | bus_LV_1145-2_0_4_node_192 | 0.4 | n |  | TRUE
111 | bus_LV_1145-2_0_4_node_193 | 0.4 | n |  | TRUE
112 | bus_LV_1145-2_0_4_node_213 | 0.4 | n |  | TRUE
113 | bus_LV_1145-2_0_4_node_218 | 0.4 | n |  | TRUE
114 | bus_LV_1145-2_0_4_node_212 | 0.4 | n |  | TRUE
115 | bus_LV_1145-2_0_4_node_222 | 0.4 | n |  | TRUE
116 | bus_LV_1145-2_0_4_node_221 | 0.4 | n |  | TRUE
117 | bus_LV_1145-2_0_4_node_203 | 0.4 | n |  | TRUE
118 | bus_LV_1145-2_0_4_node_204 | 0.4 | n |  | TRUE
119 | bus_LV_1145-2_0_4_node_205 | 0.4 | n |  | TRUE
120 | bus_LV_1145-2_0_4_node_207 | 0.4 | n |  | TRUE
121 | bus_LV_1145-2_0_4_node_215 | 0.4 | n |  | TRUE
122 | bus_LV_1145-2_0_4_node_214 | 0.4 | n |  | TRUE
123 | bus_LV_1145-2_0_4_node_208 | 0.4 | n |  | TRUE
124 | bus_LV_1145-2_0_4_node_209 | 0.4 | n |  | TRUE
125 | bus_LV_1145-2_0_4_node_210 | 0.4 | n |  | TRUE
126 | bus_LV_1145-2_0_4_node_211 | 0.4 | n |  | TRUE
127 | bus_LV_1145-2_0_4_node_216 | 0.4 | n |  | TRUE
128 | bus_LV_1145-2_0_4_node_217 | 0.4 | n |  | TRUE
129 | bus_LV_1145-2_0_4_node_219 | 0.4 | n |  | TRUE
130 | bus_LV_1145-2_0_4_node_220 | 0.4 | n |  | TRUE
131 | bus_MV_129_0_node_37 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1145-2_0_4_load_0 | 0 | 0.0005715 | 0.00014323 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1145-2_0_4_load_1 | 1 | 0.000474 | 0.0001188 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1145-2_0_4_load_3 | 3 | 0.00091139 | 0.00022842 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1145-2_0_4_load_45 | 5 | 0.0005483 | 0.00013742 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1145-2_0_4_load_41 | 6 | 0.00044096 | 0.00011052 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1145-2_0_4_load_105 | 8 | 0.00047289 | 0.00011852 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1145-2_0_4_load_103 | 9 | 0.00024945 | 6.2517e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1145-2_0_4_load_42 | 12 | 0.00082835 | 0.0002076 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1145-2_0_4_load_44 | 13 | 0.0022415 | 0.00056176 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1145-2_0_4_load_63 | 15 | 8.7991e-05 | 2.2053e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1145-2_0_4_load_48 | 16 | 0.0013861 | 0.0003474 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1145-2_0_4_load_60 | 17 | 0.0007324 | 0.00018356 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1145-2_0_4_load_53 | 20 | 0.0002838 | 7.1126e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1145-2_0_4_load_71 | 21 | 0.0001425 | 3.5713e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1145-2_0_4_load_90 | 22 | 8.7084e-05 | 2.1825e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1145-2_0_4_load_87 | 23 | 0.00030491 | 7.6418e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1145-2_0_4_load_91 | 24 | 0.00093172 | 0.00023351 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1145-2_0_4_load_54 | 25 | 0.011044 | 0.0027678 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1145-2_0_4_load_55 | 26 | 0.0023515 | 0.00058935 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1145-2_0_4_load_57 | 28 | 0.0011793 | 0.00029555 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1145-2_0_4_load_58 | 29 | 0.004192 | 0.0010506 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1145-2_0_4_load_73 | 30 | 0.0041058 | 0.001029 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1145-2_0_4_load_223 | 31 | 0.0046942 | 0.0011765 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1145-2_0_4_load_72 | 32 | 0.0073992 | 0.0018544 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1145-2_0_4_load_62 | 34 | 0.00097908 | 0.00024538 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1145-2_0_4_load_64 | 35 | 0.0012164 | 0.00030486 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1145-2_0_4_load_67 | 38 | 0.0013125 | 0.00032895 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1145-2_0_4_load_68 | 39 | 0.0016022 | 0.00040155 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1145-2_0_4_load_69 | 40 | 0.0020246 | 0.00050741 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1145-2_0_4_load_70 | 41 | 0.0014589 | 0.00036564 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1145-2_0_4_load_75 | 42 | 0.0023785 | 0.00059612 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1145-2_0_4_load_127 | 43 | 0.0012133 | 0.00030408 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1145-2_0_4_load_76 | 44 | 0.00065946 | 0.00016528 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1145-2_0_4_load_79 | 45 | 0.0012164 | 0.00030486 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1145-2_0_4_load_74 | 46 | 0.002495 | 0.00062532 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1145-2_0_4_load_126 | 47 | 0.00084853 | 0.00021266 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1145-2_0_4_load_77 | 48 | 8.8542e-05 | 2.2191e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1145-2_0_4_load_78 | 49 | 0.00017364 | 4.3517e-05 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1145-2_0_4_load_86 | 50 | 0.00048043 | 0.00012041 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1145-2_0_4_load_120 | 51 | 8.4861e-05 | 2.1268e-05 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1145-2_0_4_load_228 | 52 | 8.8448e-05 | 2.2167e-05 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1145-2_0_4_load_80 | 53 | 0.0013841 | 0.00034688 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1145-2_0_4_load_81 | 54 | 0.00013507 | 3.3853e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1145-2_0_4_load_97 | 55 | 0.00014617 | 3.6634e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1145-2_0_4_load_95 | 56 | 0.00014622 | 3.6645e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1145-2_0_4_load_82 | 57 | 0.0004873 | 0.00012213 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1145-2_0_4_load_83 | 58 | 0.00052751 | 0.00013221 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1145-2_0_4_load_84 | 59 | 0.0012153 | 0.00030458 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1145-2_0_4_load_85 | 61 | 0.0010247 | 0.00025682 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1145-2_0_4_load_125 | 62 | 0.00073818 | 0.00018501 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1145-2_0_4_load_114 | 63 | 0.00072065 | 0.00018061 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1145-2_0_4_load_88 | 64 | 8.9505e-05 | 2.2432e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1145-2_0_4_load_89 | 65 | 8.6943e-05 | 2.179e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1145-2_0_4_load_226 | 66 | 8.9414e-05 | 2.2409e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1145-2_0_4_load_135 | 67 | 8.6916e-05 | 2.1783e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1145-2_0_4_load_92 | 68 | 0.00051489 | 0.00012904 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1145-2_0_4_load_93 | 69 | 0.00036159 | 9.0624e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1145-2_0_4_load_94 | 70 | 0.00012845 | 3.2192e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1145-2_0_4_load_96 | 71 | 0.00012829 | 3.2152e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1145-2_0_4_load_102 | 73 | 0.00011172 | 2.8e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1145-2_0_4_load_98 | 74 | 0.00063561 | 0.0001593 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1145-2_0_4_load_139 | 77 | 0.0007238 | 0.0001814 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1145-2_0_4_load_119 | 78 | 0.00011172 | 2.8e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1145-2_0_4_load_188 | 79 | 0.00094619 | 0.00023714 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1145-2_0_4_load_122 | 80 | 0.00019751 | 4.95e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1145-2_0_4_load_121 | 81 | 0.00033739 | 8.4558e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1145-2_0_4_load_117 | 82 | 0.00028213 | 7.0708e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1145-2_0_4_load_106 | 83 | 0.00029668 | 7.4355e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1145-2_0_4_load_107 | 84 | 0.00036204 | 9.0735e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1145-2_0_4_load_128 | 85 | 0.0006532 | 0.00016371 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1145-2_0_4_load_136 | 86 | 0.00024077 | 6.0342e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1145-2_0_4_load_110 | 87 | 0.00037712 | 9.4514e-05 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1145-2_0_4_load_129 | 88 | 0.00045612 | 0.00011431 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1145-2_0_4_load_137 | 89 | 0.00045473 | 0.00011397 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1145-2_0_4_load_108 | 90 | 0.00047788 | 0.00011977 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1145-2_0_4_load_109 | 91 | 0.0012215 | 0.00030615 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1145-2_0_4_load_111 | 92 | 0.00076761 | 0.00019238 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1145-2_0_4_load_113 | 93 | 0.0014067 | 0.00035256 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1145-2_0_4_load_115 | 94 | 0.0013937 | 0.0003493 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1145-2_0_4_load_116 | 95 | 0.00068912 | 0.00017271 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1145-2_0_4_load_227 | 96 | 8.4861e-05 | 2.1268e-05 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1145-2_0_4_load_123 | 97 | 0.0011787 | 0.00029541 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1145-2_0_4_load_124 | 98 | 0.0011493 | 0.00028804 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1145-2_0_4_load_130 | 99 | 0.00049395 | 0.0001238 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1145-2_0_4_load_131 | 100 | 0.00051625 | 0.00012938 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1145-2_0_4_load_132 | 101 | 8.6916e-05 | 2.1783e-05 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1145-2_0_4_load_133 | 102 | 8.9414e-05 | 2.2409e-05 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1145-2_0_4_load_134 | 103 | 8.8448e-05 | 2.2167e-05 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1145-2_0_4_load_224 | 104 | 8.4796e-05 | 2.1252e-05 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1145-2_0_4_load_225 | 105 | 8.8542e-05 | 2.2191e-05 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1145-2_0_4_load_138 | 106 | 0.00027331 | 6.8498e-05 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1145-2_0_4_load_189 | 107 | 0.0025427 | 0.00063726 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1145-2_0_4_load_190 | 108 | 0.010052 | 0.0025194 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1145-2_0_4_load_191 | 109 | 0.0026708 | 0.00066937 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1145-2_0_4_load_192 | 110 | 0.0037065 | 0.00092893 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1145-2_0_4_load_193 | 111 | 0.0023775 | 0.00059585 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1145-2_0_4_load_218 | 113 | 0.0039622 | 0.00099303 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1145-2_0_4_load_212 | 114 | 0.0025581 | 0.00064112 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1145-2_0_4_load_222 | 115 | 0.013939 | 0.0034934 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1145-2_0_4_load_221 | 116 | 0.0040261 | 0.001009 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1145-2_0_4_load_203 | 117 | 0.001156 | 0.00028971 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1145-2_0_4_load_204 | 118 | 0.0024995 | 0.00062644 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1145-2_0_4_load_205 | 119 | 0.0016044 | 0.00040211 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1145-2_0_4_load_207 | 120 | 0.0035215 | 0.00088257 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1145-2_0_4_load_215 | 121 | 0.0015897 | 0.00039842 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1145-2_0_4_load_214 | 122 | 0.0014852 | 0.00037221 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1145-2_0_4_load_208 | 123 | 0.0036221 | 0.0009078 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1145-2_0_4_load_209 | 124 | 0.005605 | 0.0014047 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1145-2_0_4_load_210 | 125 | 0.0041859 | 0.0010491 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1145-2_0_4_load_211 | 126 | 0.0023292 | 0.00058375 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1145-2_0_4_load_216 | 127 | 0.0041817 | 0.001048 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1145-2_0_4_load_217 | 128 | 0.0030198 | 0.00075683 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1145-2_0_4_load_219 | 129 | 0.0031153 | 0.00078077 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1145-2_0_4_load_220 | 130 | 0.0028686 | 0.00071893 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1145-2_0_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.029755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1145-2_0_4_line_1 | NAYY 4x150 SE | 0 | 2 | 0.026805 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1145-2_0_4_line_2 | NAYY 4x150 SE | 1 | 3 | 0.027114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1145-2_0_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.45684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1145-2_0_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.091055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1145-2_0_4_line_5 | NAYY 4x150 SE | 4 | 6 | 0.044142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1145-2_0_4_line_6 | NAYY 4x150 SE | 6 | 12 | 0.017818 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1145-2_0_4_line_7 | NAYY 4x150 SE | 7 | 8 | 0.051379 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1145-2_0_4_line_8 | NAYY 4x150 SE | 7 | 9 | 0.017997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1145-2_0_4_line_9 | NAYY 4x150 SE | 8 | 10 | 0.017885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1145-2_0_4_line_10 | NAYY 4x150 SE | 9 | 11 | 0.013025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1145-2_0_4_line_11 | NAYY 4x150 SE | 10 | 87 | 0.030432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1145-2_0_4_line_12 | NAYY 4x150 SE | 11 | 83 | 0.0015421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1145-2_0_4_line_13 | NAYY 4x150 SE | 11 | 84 | 0.016357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1145-2_0_4_line_14 | NAYY 4x150 SE | 12 | 13 | 0.036263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1145-2_0_4_line_15 | NAYY 4x150 SE | 13 | 16 | 0.051979 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1145-2_0_4_line_16 | NAYY 4x150 SE | 14 | 15 | 0.038409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1145-2_0_4_line_17 | NAYY 4x150 SE | 14 | 16 | 0.38542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1145-2_0_4_line_18 | NAYY 4x150 SE | 14 | 17 | 0.028041 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1145-2_0_4_line_19 | NAYY 4x150 SE | 15 | 19 | 0.014108 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1145-2_0_4_line_20 | NAYY 4x150 SE | 17 | 34 | 0.00018767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1145-2_0_4_line_21 | NAYY 4x150 SE | 18 | 19 | 0.017696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1145-2_0_4_line_22 | NAYY 4x150 SE | 18 | 20 | 0.069678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1145-2_0_4_line_23 | NAYY 4x150 SE | 19 | 21 | 0.023492 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1145-2_0_4_line_24 | NAYY 4x150 SE | 20 | 22 | 0.015438 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1145-2_0_4_line_25 | NAYY 4x150 SE | 21 | 23 | 0.033099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1145-2_0_4_line_26 | NAYY 4x150 SE | 22 | 24 | 0.018395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1145-2_0_4_line_27 | NAYY 4x150 SE | 23 | 50 | 0.030155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1145-2_0_4_line_28 | NAYY 4x150 SE | 24 | 68 | 0.048958 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1145-2_0_4_line_29 | NAYY 4x150 SE | 25 | 26 | 0.022441 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1145-2_0_4_line_30 | NAYY 4x150 SE | 25 | 27 | 0.019772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1145-2_0_4_line_31 | NAYY 4x150 SE | 26 | 28 | 0.013067 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1145-2_0_4_line_32 | NAYY 4x150 SE | 27 | 29 | 0.017707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1145-2_0_4_line_33 | NAYY 4x150 SE | 28 | 30 | 0.0087617 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
34 | LV_1145-2_0_4_line_34 | NAYY 4x150 SE | 29 | 31 | 0.028688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
35 | LV_1145-2_0_4_line_35 | NAYY 4x150 SE | 30 | 32 | 0.014847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1145-2_0_4_line_36 | NAYY 4x150 SE | 31 | 33 | 0.021798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_1145-2_0_4_line_37 | NAYY 4x150 SE | 32 | 46 | 0.0012842 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1145-2_0_4_line_38 | NAYY 4x150 SE | 33 | 118 | 0.013237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1145-2_0_4_line_39 | NAYY 4x150 SE | 35 | 36 | 0.025122 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1145-2_0_4_line_40 | NAYY 4x150 SE | 35 | 37 | 0.020275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1145-2_0_4_line_41 | NAYY 4x150 SE | 36 | 38 | 0.024393 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1145-2_0_4_line_42 | NAYY 4x150 SE | 36 | 39 | 0.0039578 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
43 | LV_1145-2_0_4_line_43 | NAYY 4x150 SE | 37 | 40 | 0.016903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1145-2_0_4_line_44 | NAYY 4x150 SE | 37 | 41 | 0.016076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1145-2_0_4_line_45 | NAYY 4x150 SE | 38 | 42 | 0.032906 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_1145-2_0_4_line_46 | NAYY 4x150 SE | 39 | 43 | 0.020841 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1145-2_0_4_line_47 | NAYY 4x150 SE | 40 | 44 | 0.024317 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1145-2_0_4_line_48 | NAYY 4x150 SE | 41 | 45 | 0.018318 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1145-2_0_4_line_49 | NAYY 4x150 SE | 42 | 46 | 0.0178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1145-2_0_4_line_50 | NAYY 4x150 SE | 43 | 47 | 0.045221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1145-2_0_4_line_51 | NAYY 4x150 SE | 44 | 48 | 0.0044779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1145-2_0_4_line_52 | NAYY 4x150 SE | 45 | 49 | 0.024959 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1145-2_0_4_line_53 | NAYY 4x150 SE | 47 | 98 | 0.0092141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1145-2_0_4_line_54 | NAYY 4x150 SE | 48 | 51 | 0.0018359 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1145-2_0_4_line_55 | NAYY 4x150 SE | 49 | 53 | 0.016566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1145-2_0_4_line_56 | NAYY 4x150 SE | 50 | 64 | 0.023257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1145-2_0_4_line_57 | NAYY 4x150 SE | 51 | 52 | 0.0037408 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1145-2_0_4_line_58 | NAYY 4x150 SE | 52 | 96 | 0.0018712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1145-2_0_4_line_59 | NAYY 4x150 SE | 53 | 54 | 0.018332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1145-2_0_4_line_60 | NAYY 4x150 SE | 54 | 55 | 0.010866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1145-2_0_4_line_61 | NAYY 4x150 SE | 55 | 56 | 0.009554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1145-2_0_4_line_62 | NAYY 4x150 SE | 56 | 69 | 0.013695 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1145-2_0_4_line_63 | NAYY 4x150 SE | 57 | 58 | 0.00039081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1145-2_0_4_line_64 | NAYY 4x150 SE | 57 | 59 | 0.043178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1145-2_0_4_line_65 | NAYY 4x150 SE | 58 | 60 | 0.11008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1145-2_0_4_line_66 | NAYY 4x150 SE | 59 | 61 | 0.0042599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1145-2_0_4_line_67 | NAYY 4x150 SE | 60 | 95 | 0.088652 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1145-2_0_4_line_68 | NAYY 4x150 SE | 61 | 62 | 0.023882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1145-2_0_4_line_69 | NAYY 4x150 SE | 62 | 63 | 0.02018 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1145-2_0_4_line_70 | NAYY 4x150 SE | 63 | 93 | 0.0013943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1145-2_0_4_line_71 | NAYY 4x150 SE | 64 | 65 | 0.0037819 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1145-2_0_4_line_72 | NAYY 4x150 SE | 65 | 66 | 0.0007334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1145-2_0_4_line_73 | NAYY 4x150 SE | 66 | 67 | 0.0048731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1145-2_0_4_line_74 | NAYY 4x150 SE | 67 | 102 | 0.00087536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1145-2_0_4_line_75 | NAYY 4x150 SE | 69 | 70 | 0.00084839 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1145-2_0_4_line_76 | NAYY 4x150 SE | 70 | 71 | 0.0079437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1145-2_0_4_line_77 | NAYY 4x150 SE | 71 | 72 | 0.015583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1145-2_0_4_line_78 | NAYY 4x150 SE | 72 | 73 | 0.0061523 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1145-2_0_4_line_79 | NAYY 4x150 SE | 72 | 74 | 0.070851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1145-2_0_4_line_80 | NAYY 4x150 SE | 73 | 78 | 0.0023162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1145-2_0_4_line_81 | NAYY 4x150 SE | 74 | 75 | 0.039648 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1145-2_0_4_line_82 | NAYY 4x150 SE | 75 | 76 | 0.006817 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1145-2_0_4_line_83 | NAYY 4x150 SE | 76 | 77 | 0.034482 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1145-2_0_4_line_84 | NAYY 4x150 SE | 77 | 79 | 0.036866 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1145-2_0_4_line_85 | NAYY 4x150 SE | 78 | 82 | 0.034276 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1145-2_0_4_line_86 | NAYY 4x150 SE | 79 | 107 | 0.020902 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1145-2_0_4_line_87 | NAYY 4x150 SE | 80 | 81 | 0.025508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1145-2_0_4_line_88 | NAYY 4x150 SE | 81 | 97 | 0.027373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1145-2_0_4_line_89 | NAYY 4x150 SE | 82 | 94 | 0.029645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1145-2_0_4_line_90 | NAYY 4x150 SE | 83 | 85 | 0.013992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1145-2_0_4_line_91 | NAYY 4x150 SE | 84 | 86 | 0.021894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1145-2_0_4_line_92 | NAYY 4x150 SE | 85 | 88 | 0.0038177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1145-2_0_4_line_93 | NAYY 4x150 SE | 86 | 89 | 0.0013399 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1145-2_0_4_line_94 | NAYY 4x150 SE | 87 | 90 | 0.013064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1145-2_0_4_line_95 | NAYY 4x150 SE | 88 | 99 | 0.012107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1145-2_0_4_line_96 | NAYY 4x150 SE | 89 | 106 | 0.026205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1145-2_0_4_line_97 | NAYY 4x150 SE | 90 | 91 | 0.0012711 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1145-2_0_4_line_98 | NAYY 4x150 SE | 91 | 92 | 0.018665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1145-2_0_4_line_99 | NAYY 4x150 SE | 92 | 93 | 0.014621 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1145-2_0_4_line_100 | NAYY 4x150 SE | 94 | 95 | 0.028804 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1145-2_0_4_line_101 | NAYY 4x150 SE | 96 | 105 | 0.0037055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1145-2_0_4_line_102 | NAYY 4x150 SE | 97 | 98 | 0.01719 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1145-2_0_4_line_103 | NAYY 4x150 SE | 100 | 101 | 0.0029341 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1145-2_0_4_line_104 | NAYY 4x150 SE | 100 | 102 | 0.0017957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1145-2_0_4_line_105 | NAYY 4x150 SE | 101 | 103 | 0.005573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1145-2_0_4_line_106 | NAYY 4x150 SE | 103 | 104 | 0.0036712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1145-2_0_4_line_107 | NAYY 4x150 SE | 104 | 105 | 0.0019055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1145-2_0_4_line_108 | NAYY 4x150 SE | 108 | 109 | 0.014876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1145-2_0_4_line_109 | NAYY 4x150 SE | 108 | 110 | 0.0045003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1145-2_0_4_line_110 | NAYY 4x150 SE | 109 | 111 | 0.016589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1145-2_0_4_line_111 | NAYY 4x150 SE | 111 | 112 | 0.016334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1145-2_0_4_line_112 | NAYY 4x150 SE | 112 | 113 | 0.013166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1145-2_0_4_line_113 | NAYY 4x150 SE | 112 | 114 | 0.024207 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1145-2_0_4_line_114 | NAYY 4x150 SE | 113 | 127 | 0.0020548 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1145-2_0_4_line_115 | NAYY 4x150 SE | 114 | 125 | 0.0069962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1145-2_0_4_line_116 | NAYY 4x150 SE | 115 | 116 | 0.016015 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1145-2_0_4_line_117 | NAYY 4x150 SE | 116 | 130 | 0.0018694 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
118 | LV_1145-2_0_4_line_118 | NAYY 4x150 SE | 117 | 118 | 0.034896 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
119 | LV_1145-2_0_4_line_119 | NAYY 4x150 SE | 117 | 119 | 0.00081056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
120 | LV_1145-2_0_4_line_120 | NAYY 4x150 SE | 119 | 120 | 0.019479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
121 | LV_1145-2_0_4_line_121 | NAYY 4x150 SE | 120 | 121 | 0.0082471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
122 | LV_1145-2_0_4_line_122 | NAYY 4x150 SE | 121 | 122 | 0.0033196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
123 | LV_1145-2_0_4_line_123 | NAYY 4x150 SE | 122 | 126 | 0.021774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
124 | LV_1145-2_0_4_line_124 | NAYY 4x150 SE | 123 | 124 | 0.0036365 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1145-2_0_4_line_125 | NAYY 4x150 SE | 123 | 125 | 0.02485 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
126 | LV_1145-2_0_4_line_126 | NAYY 4x150 SE | 124 | 126 | 0.0047283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1145-2_0_4_line_127 | NAYY 4x150 SE | 127 | 128 | 0.013076 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1145-2_0_4_line_128 | NAYY 4x150 SE | 128 | 129 | 0.008793 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1145-2_0_4_line_129 | NAYY 4x150 SE | 129 | 130 | 0.0045271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1145-2_0_4_trafo_126 | 0.25 MVA 20/0.4 kV | 131 | 47 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2633947.363 | 1219651.0824 | 2633931.9365 | 1219656.7774 | 2633918.6937 | 1219658.1223
1 | 2633971.1366 | 1219639.1791 | 2633961.7128 | 1219645.7849 | 2633947.363 | 1219651.0824
2 | 2633918.6937 | 1219658.1223 | 2633909.1297 | 1219659.0935 | 2633903.5855 | 1219667.9895 | 2633902.3343 | 1219674.8961
3 | 2634189.3035 | 1219237.8007 | 2633971.1366 | 1219639.1791
4 | 2634189.3035 | 1219237.8007 | 2634209.325 | 1219272.8916 | 2634214.3561 | 1219278.168 | 2634219.2253 | 1219281.2422 | 2634225.5351 | 1219281.8788 | 2634238.3687 | 1219278.9173 | 2634246.3215 | 1219277.54 | 2634256.3024 | 1219278.4422
5 | 2634189.3035 | 1219237.8007 | 2634207.355 | 1219222.1283 | 2634213.9452 | 1219212.2491 | 2634216.6163 | 1219204.3265
6 | 2634216.6163 | 1219204.3265 | 2634216.6163 | 1219204.3265 | 2634216.4777 | 1219192.7633 | 2634216.0588 | 1219186.5229
7 | 2634020.2305 | 1218380.8982 | 2634069.8877 | 1218394.0881
8 | 2634020.2305 | 1218380.8982 | 2634015.6624 | 1218398.3054
9 | 2634087.1736 | 1218398.6796 | 2634069.8877 | 1218394.0881
10 | 2634012.3561 | 1218410.9042 | 2634015.6624 | 1218398.3054
11 | 2634087.1736 | 1218398.6796 | 2634084.7854 | 1218407.5489 | 2634083.4685 | 1218424.1733 | 2634085.0757 | 1218428.4517 | 2634085.0757 | 1218428.4517
12 | 2634012.3561 | 1218410.9042 | 2634013.8479 | 1218411.2947
13 | 2634012.3561 | 1218410.9042 | 2633996.5339 | 1218406.7571
14 | 2634216.0588 | 1219186.5229 | 2634215.7437 | 1219181.8305 | 2634218.0185 | 1219172.8827 | 2634224.7794 | 1219165.0058 | 2634234.7991 | 1219158.4999
15 | 2634234.7991 | 1219158.4999 | 2634264.4098 | 1219139.2737 | 2634276.511 | 1219127.8031
16 | 2634372.676 | 1218754.5707 | 2634369.6708 | 1218749.2947 | 2634368.6687 | 1218742.774 | 2634370.3494 | 1218734.2676 | 2634374.0848 | 1218724.7724 | 2634377.1381 | 1218718.6235
17 | 2634372.676 | 1218754.5707 | 2634276.511 | 1219127.8031
18 | 2634372.676 | 1218754.5707 | 2634376.3458 | 1218756.4374 | 2634381.1998 | 1218758.2664 | 2634389.5473 | 1218758.3145 | 2634399.7559 | 1218756.3859
19 | 2634381.4741 | 1218705.437 | 2634381.4538 | 1218708.95 | 2634378.2079 | 1218716.4691 | 2634377.1381 | 1218718.6235
20 | 2634399.9403 | 1218756.3511 | 2634399.7559 | 1218756.3859
21 | 2634381.4741 | 1218705.437 | 2634373.7711 | 1218705.4704 | 2634363.7904 | 1218704.3456
22 | 2634363.7904 | 1218704.3456 | 2634361.7937 | 1218697.897 | 2634357.3482 | 1218692.3459 | 2634348.2225 | 1218686.4121 | 2634331.1598 | 1218680.2658 | 2634305.231 | 1218673.5117
23 | 2634381.4741 | 1218705.437 | 2634387.2365 | 1218703.7025 | 2634392.9421 | 1218698.6769 | 2634399.7433 | 1218691.5227
24 | 2634290.0853 | 1218670.5368 | 2634303.9257 | 1218673.1717 | 2634305.231 | 1218673.5117
25 | 2634399.7433 | 1218691.5227 | 2634414.0386 | 1218676.4855 | 2634423.6457 | 1218668.7225
26 | 2634290.0853 | 1218670.5368 | 2634272.0153 | 1218667.0967
27 | 2634448.2479 | 1218651.3523 | 2634432.4673 | 1218661.5943 | 2634423.6457 | 1218668.7225
28 | 2634225.4832 | 1218663.2194 | 2634229.4962 | 1218660.6146 | 2634237.4472 | 1218658.3811 | 2634245.5874 | 1218658.8726 | 2634252.6908 | 1218661.5149 | 2634263.4597 | 1218665.4679 | 2634272.0153 | 1218667.0967
29 | 2634669.4256 | 1218541.3649 | 2634689.5472 | 1218540.1456 | 2634691.8294 | 1218540.1831
30 | 2634711.5993 | 1218540.5074 | 2634691.8294 | 1218540.1831
31 | 2634669.4256 | 1218541.3649 | 2634666.111 | 1218541.5658 | 2634656.4145 | 1218542.555
32 | 2634711.5993 | 1218540.5074 | 2634710.4685 | 1218522.8363
33 | 2634656.4145 | 1218542.555 | 2634647.698 | 1218543.4442
34 | 2634710.4685 | 1218522.8363 | 2634708.6366 | 1218494.2069
35 | 2634647.698 | 1218543.4442 | 2634632.928 | 1218544.951
36 | 2634707.2446 | 1218472.4533 | 2634708.6366 | 1218494.2069
37 | 2634631.6504 | 1218545.0813 | 2634632.928 | 1218544.951
38 | 2634707.2446 | 1218472.4533 | 2634694.0192 | 1218473.006
39 | 2634557.0375 | 1218553.6067 | 2634556.9968 | 1218560.6328 | 2634555.5551 | 1218567.1283 | 2634551.6304 | 1218572.5643 | 2634547.5616 | 1218574.9905
40 | 2634529.0456 | 1218582.9508 | 2634533.2875 | 1218580.396 | 2634544.8907 | 1218576.5832 | 2634547.5616 | 1218574.9905
41 | 2634557.0375 | 1218553.6067 | 2634581.2642 | 1218550.7631
42 | 2634557.0375 | 1218553.6067 | 2634553.0797 | 1218553.5934
43 | 2634529.0456 | 1218582.9508 | 2634525.9308 | 1218584.8227 | 2634516.4081 | 1218594.0629
44 | 2634529.0456 | 1218582.9508 | 2634513.329 | 1218579.5717
45 | 2634613.9462 | 1218546.9269 | 2634581.2642 | 1218550.7631
46 | 2634553.0797 | 1218553.5934 | 2634538.6568 | 1218553.5447 | 2634532.3438 | 1218552.3911
47 | 2634516.4081 | 1218594.0629 | 2634498.9561 | 1218610.9971
48 | 2634513.329 | 1218579.5717 | 2634509.6491 | 1218578.7805 | 2634497.4562 | 1218575.6637 | 2634495.673 | 1218574.8285
49 | 2634631.6504 | 1218545.0813 | 2634616.5165 | 1218546.6252 | 2634613.9462 | 1218546.9269
50 | 2634488.9531 | 1218540.1205 | 2634515.0946 | 1218549.2391 | 2634532.3438 | 1218552.3911
51 | 2634495.7424 | 1218614.1154 | 2634498.9561 | 1218610.9971
52 | 2634473.0707 | 1218564.2413 | 2634495.673 | 1218574.8285
53 | 2634480.253 | 1218537.0858 | 2634488.9531 | 1218540.1205
54 | 2634494.4248 | 1218615.3939 | 2634495.7424 | 1218614.1154
55 | 2634473.0707 | 1218564.2413 | 2634458.0688 | 1218557.2142
56 | 2634467.7561 | 1218638.6911 | 2634448.2479 | 1218651.3523
57 | 2634494.4248 | 1218615.3939 | 2634491.7402 | 1218617.999
58 | 2634490.3972 | 1218619.3021 | 2634491.7402 | 1218617.999
59 | 2634458.0688 | 1218557.2142 | 2634458.0688 | 1218557.2142 | 2634450.1381 | 1218555.9121 | 2634442.4011 | 1218556.5233 | 2634440.0054 | 1218557.3501
60 | 2634429.7336 | 1218560.8951 | 2634440.0054 | 1218557.3501
61 | 2634420.7023 | 1218564.012 | 2634429.7336 | 1218560.8951
62 | 2634420.7023 | 1218564.012 | 2634407.7567 | 1218568.4798
63 | 2634218.8393 | 1218471.3246 | 2634218.4655 | 1218471.2108
64 | 2634218.4655 | 1218471.2108 | 2634177.1582 | 1218458.6375
65 | 2634197.307 | 1218579.2823 | 2634218.8393 | 1218471.3246
66 | 2634173.0829 | 1218457.397 | 2634177.1582 | 1218458.6375
67 | 2634197.307 | 1218579.2823 | 2634285.9295 | 1218581.564
68 | 2634173.0829 | 1218457.397 | 2634150.2362 | 1218450.4427
69 | 2634150.2362 | 1218450.4427 | 2634130.9303 | 1218444.5663
70 | 2634129.5965 | 1218444.1603 | 2634130.9303 | 1218444.5663
71 | 2634467.7561 | 1218638.6911 | 2634469.0395 | 1218637.8582 | 2634470.7879 | 1218636.4388
72 | 2634470.7879 | 1218636.4388 | 2634471.3572 | 1218635.9766
73 | 2634475.1405 | 1218632.9051 | 2634471.3572 | 1218635.9766
74 | 2634475.1405 | 1218632.9051 | 2634475.8201 | 1218632.3534
75 | 2634407.7567 | 1218568.4798 | 2634406.9547 | 1218568.7566
76 | 2634399.4457 | 1218571.3481 | 2634406.9547 | 1218568.7566
77 | 2634384.4863 | 1218575.2558 | 2634388.7603 | 1218575.0358 | 2634399.4457 | 1218571.3481
78 | 2634384.4863 | 1218575.2558 | 2634379.4641 | 1218578.8094
79 | 2634384.4863 | 1218575.2558 | 2634386.1407 | 1218569.9956 | 2634385.9757 | 1218563.0906 | 2634377.9556 | 1218541.7429 | 2634368.2939 | 1218523.421 | 2634362.2233 | 1218516.6932 | 2634357.5046 | 1218513.2342
80 | 2634377.5255 | 1218580.0608 | 2634377.9405 | 1218579.8874 | 2634379.4641 | 1218578.8094
81 | 2634335.2329 | 1218484.2855 | 2634334.2233 | 1218489.5939 | 2634335.6642 | 1218495.0498 | 2634341.3482 | 1218501.7086 | 2634353.5097 | 1218510.3059 | 2634357.5046 | 1218513.2342
82 | 2634335.2329 | 1218484.2855 | 2634341.6551 | 1218486.6238
83 | 2634341.6551 | 1218486.6238 | 2634340.5356 | 1218476.7671 | 2634329.5566 | 1218454.7957
84 | 2634329.5566 | 1218454.7957 | 2634324.7796 | 1218445.2358 | 2634322.772 | 1218439.343 | 2634322.3097 | 1218424.7206 | 2634324.5157 | 1218419.8749
85 | 2634377.5255 | 1218580.0608 | 2634368.3551 | 1218583.8901 | 2634351.8516 | 1218586.0297 | 2634344.1554 | 1218586.0578
86 | 2634341.2767 | 1218407.3863 | 2634324.5157 | 1218419.8749 | 2634324.5157 | 1218419.8749
87 | 2634438.2302 | 1218522.259 | 2634414.299 | 1218513.4286
88 | 2634464.0218 | 1218531.424 | 2634446.5808 | 1218525.3403 | 2634438.2302 | 1218522.259
89 | 2634314.6234 | 1218583.9914 | 2634334.1457 | 1218586.0944 | 2634344.1554 | 1218586.0578
90 | 2634013.8479 | 1218411.2947 | 2634027.3837 | 1218414.8382
91 | 2633996.5339 | 1218406.7571 | 2633975.3557 | 1218401.2062
92 | 2634031.077 | 1218415.8051 | 2634027.3837 | 1218414.8382
93 | 2633974.0596 | 1218400.8665 | 2633975.3557 | 1218401.2062
94 | 2634085.0757 | 1218428.4517 | 2634088.7227 | 1218431.7189 | 2634096.5367 | 1218434.0973
95 | 2634042.7895 | 1218418.8713 | 2634031.077 | 1218415.8051
96 | 2633974.0596 | 1218400.8665 | 2633948.7109 | 1218394.2224
97 | 2634096.5367 | 1218434.0973 | 2634097.7527 | 1218434.4675
98 | 2634115.6087 | 1218439.9026 | 2634097.7527 | 1218434.4675
99 | 2634115.6087 | 1218439.9026 | 2634129.5965 | 1218444.1603
100 | 2634314.6234 | 1218583.9914 | 2634302.2001 | 1218582.6531 | 2634287.3466 | 1218581.6004 | 2634285.9295 | 1218581.564
101 | 2634490.3972 | 1218619.3021 | 2634487.7379 | 1218621.8825
102 | 2634464.0218 | 1218531.424 | 2634480.253 | 1218537.0858
103 | 2634479.4922 | 1218629.3723 | 2634477.2142 | 1218631.2216
104 | 2634475.8201 | 1218632.3534 | 2634477.2142 | 1218631.2216
105 | 2634483.7356 | 1218625.766 | 2634482.7185 | 1218626.7529 | 2634479.4922 | 1218629.3723
106 | 2634483.7356 | 1218625.766 | 2634486.3704 | 1218623.2095
107 | 2634486.3704 | 1218623.2095 | 2634487.7379 | 1218621.8825
108 | 2634494.1012 | 1218468.824 | 2634503.2626 | 1218471.9365 | 2634508.4125 | 1218472.6573
109 | 2634494.1012 | 1218468.824 | 2634489.84 | 1218467.3763
110 | 2634508.4125 | 1218472.6573 | 2634522.319 | 1218474.6039 | 2634524.865 | 1218474.6891
111 | 2634541.1899 | 1218475.2357 | 2634524.865 | 1218474.6891
112 | 2634541.1899 | 1218475.2357 | 2634540.659 | 1218462.0804 | 2634540.659 | 1218462.0804
113 | 2634541.1899 | 1218475.2357 | 2634565.3838 | 1218476.0417
114 | 2634540.9408 | 1218460.0451 | 2634540.659 | 1218462.0804
115 | 2634565.3838 | 1218476.0417 | 2634572.3761 | 1218476.2746
116 | 2634550.0786 | 1218417.3199 | 2634549.252 | 1218433.3136
117 | 2634549.1555 | 1218435.1805 | 2634549.252 | 1218433.3136
118 | 2634659.1537 | 1218474.4631 | 2634694.0192 | 1218473.006
119 | 2634659.1537 | 1218474.4631 | 2634658.3439 | 1218474.4969
120 | 2634658.3439 | 1218474.4969 | 2634638.8817 | 1218475.3103
121 | 2634630.6418 | 1218475.6547 | 2634638.8817 | 1218475.3103
122 | 2634627.3252 | 1218475.7933 | 2634630.6418 | 1218475.6547
123 | 2634627.3252 | 1218475.7933 | 2634605.5699 | 1218476.7025
124 | 2634597.2124 | 1218477.0517 | 2634600.8457 | 1218476.8999
125 | 2634597.2124 | 1218477.0517 | 2634596.5431 | 1218477.0797 | 2634572.3761 | 1218476.2746
126 | 2634600.8457 | 1218476.8999 | 2634605.5699 | 1218476.7025
127 | 2634540.9408 | 1218460.0451 | 2634541.7204 | 1218454.4154 | 2634544.966 | 1218447.7736
128 | 2634544.966 | 1218447.7736 | 2634546.6665 | 1218444.2937 | 2634547.9627 | 1218439.5477
129 | 2634549.1555 | 1218435.1805 | 2634549.1555 | 1218435.1805 | 2634547.9627 | 1218439.5477

## bus_geodata
| x | y | coords
0 | 2633947.363 | 1219651.0824
1 | 2633918.6937 | 1219658.1223
2 | 2633971.1366 | 1219639.1791
3 | 2633902.3343 | 1219674.8961
4 | 2634189.3035 | 1219237.8007
5 | 2634256.3024 | 1219278.4422
6 | 2634216.6163 | 1219204.3265
7 | 2634020.2305 | 1218380.8982
8 | 2634069.8877 | 1218394.0881
9 | 2634015.6624 | 1218398.3054
10 | 2634087.1736 | 1218398.6796
11 | 2634012.3561 | 1218410.9042
12 | 2634216.0588 | 1219186.5229
13 | 2634234.7992 | 1219158.4999
14 | 2634372.676 | 1218754.5707
15 | 2634377.1381 | 1218718.6235
16 | 2634276.511 | 1219127.8031
17 | 2634399.7559 | 1218756.3859
18 | 2634363.7904 | 1218704.3456
19 | 2634381.4741 | 1218705.437
20 | 2634305.231 | 1218673.5117
21 | 2634399.7433 | 1218691.5227
22 | 2634290.0853 | 1218670.5368
23 | 2634423.6457 | 1218668.7225
24 | 2634272.0153 | 1218667.0967
25 | 2634691.8294 | 1218540.1831
26 | 2634669.4256 | 1218541.3649
27 | 2634711.5993 | 1218540.5074
28 | 2634656.4145 | 1218542.555
29 | 2634710.4685 | 1218522.8363
30 | 2634647.698 | 1218543.4442
31 | 2634708.6366 | 1218494.2069
32 | 2634632.928 | 1218544.951
33 | 2634707.2446 | 1218472.4533
34 | 2634399.9403 | 1218756.3511
35 | 2634547.5616 | 1218574.9905
36 | 2634557.0375 | 1218553.6067
37 | 2634529.0456 | 1218582.9508
38 | 2634581.2642 | 1218550.7631
39 | 2634553.0797 | 1218553.5934
40 | 2634516.4081 | 1218594.0629
41 | 2634513.329 | 1218579.5717
42 | 2634613.9462 | 1218546.9269
43 | 2634532.3438 | 1218552.3911
44 | 2634498.9561 | 1218610.9971
45 | 2634495.673 | 1218574.8285
46 | 2634631.6504 | 1218545.0813
47 | 2634488.9531 | 1218540.1205
48 | 2634495.7424 | 1218614.1154
49 | 2634473.0707 | 1218564.2413
50 | 2634448.2479 | 1218651.3523
51 | 2634494.4248 | 1218615.3939
52 | 2634491.7402 | 1218617.999
53 | 2634458.0688 | 1218557.2142
54 | 2634440.0054 | 1218557.3501
55 | 2634429.7336 | 1218560.8951
56 | 2634420.7023 | 1218564.012
57 | 2634218.4655 | 1218471.2108
58 | 2634218.8393 | 1218471.3246
59 | 2634177.1582 | 1218458.6375
60 | 2634197.307 | 1218579.2823
61 | 2634173.0829 | 1218457.397
62 | 2634150.2362 | 1218450.4427
63 | 2634130.9303 | 1218444.5663
64 | 2634467.7561 | 1218638.6911
65 | 2634470.7879 | 1218636.4388
66 | 2634471.3572 | 1218635.9765
67 | 2634475.1405 | 1218632.9051
68 | 2634225.4832 | 1218663.2194
69 | 2634407.7567 | 1218568.4798
70 | 2634406.9547 | 1218568.7566
71 | 2634399.4457 | 1218571.3481
72 | 2634384.4863 | 1218575.2558
73 | 2634379.4641 | 1218578.8094
74 | 2634357.5046 | 1218513.2342
75 | 2634335.2329 | 1218484.2855
76 | 2634341.6551 | 1218486.6238
77 | 2634329.5566 | 1218454.7957
78 | 2634377.5255 | 1218580.0608
79 | 2634324.5157 | 1218419.8749
80 | 2634414.299 | 1218513.4286
81 | 2634438.2302 | 1218522.259
82 | 2634344.1554 | 1218586.0578
83 | 2634013.8479 | 1218411.2947
84 | 2633996.5339 | 1218406.7571
85 | 2634027.3837 | 1218414.8382
86 | 2633975.3557 | 1218401.2062
87 | 2634085.0757 | 1218428.4517
88 | 2634031.077 | 1218415.8051
89 | 2633974.0596 | 1218400.8665
90 | 2634096.5367 | 1218434.0973
91 | 2634097.7527 | 1218434.4675
92 | 2634115.6087 | 1218439.9026
93 | 2634129.5965 | 1218444.1603
94 | 2634314.6234 | 1218583.9914
95 | 2634285.9295 | 1218581.564
96 | 2634490.3973 | 1218619.3021
97 | 2634464.0218 | 1218531.424
98 | 2634480.253 | 1218537.0858
99 | 2634042.7895 | 1218418.8713
100 | 2634477.2142 | 1218631.2216
101 | 2634479.4922 | 1218629.3723
102 | 2634475.8201 | 1218632.3534
103 | 2634483.7356 | 1218625.766
104 | 2634486.3704 | 1218623.2095
105 | 2634487.7379 | 1218621.8825
106 | 2633948.7109 | 1218394.2224
107 | 2634341.2767 | 1218407.3863
108 | 2634494.1012 | 1218468.824
109 | 2634508.4125 | 1218472.6573
110 | 2634489.84 | 1218467.3763
111 | 2634524.865 | 1218474.6891
112 | 2634541.1899 | 1218475.2357
113 | 2634540.659 | 1218462.0804
114 | 2634565.3838 | 1218476.0417
115 | 2634550.0786 | 1218417.3199
116 | 2634549.252 | 1218433.3136
117 | 2634659.1537 | 1218474.4631
118 | 2634694.0192 | 1218473.006
119 | 2634658.3439 | 1218474.4969
120 | 2634638.8817 | 1218475.3103
121 | 2634630.6418 | 1218475.6547
122 | 2634627.3252 | 1218475.7933
123 | 2634597.2124 | 1218477.0517
124 | 2634600.8457 | 1218476.8999
125 | 2634572.3761 | 1218476.2746
126 | 2634605.5699 | 1218476.7025
127 | 2634540.9408 | 1218460.0451
128 | 2634544.966 | 1218447.7736
129 | 2634547.9627 | 1218439.5477
130 | 2634549.1555 | 1218435.1805
131 | 2634557.0375 | 1218553.6067

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98082 | -0.13571 | 0.0005715 | 0.00014323
1 | 0.98076 | -0.13614 | 0.000474 | 0.0001188
2 | 0.98089 | -0.13516 | 0 | 0
3 | 0.98072 | -0.13639 | 0.00091139 | 0.00022842
4 | 0.98219 | -0.12576 | 0 | 0
5 | 0.98212 | -0.12628 | 0.0005483 | 0.00013742
6 | 0.98235 | -0.12459 | 0.00044096 | 0.00011052
7 | 0.97817 | -0.15382 | 0 | 0
8 | 0.97843 | -0.15194 | 0.00047289 | 0.00011852
9 | 0.97808 | -0.15447 | 0.00024945 | 6.2517e-05
10 | 0.97853 | -0.1512 | 0 | 0
11 | 0.97801 | -0.15491 | 0 | 0
12 | 0.98243 | -0.12403 | 0.00082835 | 0.0002076
13 | 0.98263 | -0.12259 | 0.0022415 | 0.00056176
14 | 0.98722 | -0.089622 | 0 | 0
15 | 0.98773 | -0.085994 | 8.7991e-05 | 2.2053e-05
16 | 0.98308 | -0.11932 | 0.0013861 | 0.0003474
17 | 0.98715 | -0.090114 | 0.0007324 | 0.00018356
18 | 0.98787 | -0.084981 | 0 | 0
19 | 0.98791 | -0.084649 | 0 | 0
20 | 0.98768 | -0.086284 | 0.0002838 | 7.1126e-05
21 | 0.98829 | -0.081971 | 0.0001425 | 3.5713e-05
22 | 0.98765 | -0.086528 | 8.7084e-05 | 2.1825e-05
23 | 0.98882 | -0.078151 | 0.00030491 | 7.6418e-05
24 | 0.98761 | -0.086801 | 0.00093172 | 0.00023351
25 | 0.98654 | -0.093608 | 0.011044 | 0.0027678
26 | 0.98768 | -0.085634 | 0.0023515 | 0.00058935
27 | 0.98564 | -0.099901 | 0 | 0
28 | 0.98835 | -0.080894 | 0.0011793 | 0.00029555
29 | 0.98484 | -0.10555 | 0.004192 | 0.0010506
30 | 0.98881 | -0.077684 | 0.0041058 | 0.001029
31 | 0.9836 | -0.1143 | 0.0046942 | 0.0011765
32 | 0.98962 | -0.072045 | 0.0073992 | 0.0018544
33 | 0.98271 | -0.12061 | 0 | 0
34 | 0.98715 | -0.090116 | 0.00097908 | 0.00024538
35 | 0.99264 | -0.051095 | 0.0012164 | 0.00030486
36 | 0.99421 | -0.040072 | 0 | 0
37 | 0.99141 | -0.059765 | 0 | 0
38 | 0.99272 | -0.050377 | 0.0013125 | 0.00032895
39 | 0.99453 | -0.037825 | 0.0016022 | 0.00040155
40 | 0.99101 | -0.062588 | 0.0020246 | 0.00050741
41 | 0.99081 | -0.063968 | 0.0014589 | 0.00036564
42 | 0.99074 | -0.06418 | 0.0023785 | 0.00059612
43 | 0.99625 | -0.025906 | 0.0012133 | 0.00030408
44 | 0.99051 | -0.06615 | 0.00065946 | 0.00016528
45 | 0.99017 | -0.06849 | 0.0012164 | 0.00030486
46 | 0.98969 | -0.071525 | 0.002495 | 0.00062532
47 | 1 | 0 | -0.1782 | -0.04486
48 | 0.99042 | -0.066777 | 8.8542e-05 | 2.2191e-05
49 | 0.98934 | -0.074352 | 0.00017364 | 4.3517e-05
50 | 0.98932 | -0.07458 | 0.00048043 | 0.00012041
51 | 0.99038 | -0.067032 | 8.4861e-05 | 2.1268e-05
52 | 0.99031 | -0.067549 | 8.8448e-05 | 2.2167e-05
53 | 0.98879 | -0.078218 | 0.0013841 | 0.00034688
54 | 0.98822 | -0.082242 | 0.00013507 | 3.3853e-05
55 | 0.98788 | -0.084614 | 0.00014617 | 3.6634e-05
56 | 0.98759 | -0.086687 | 0.00014622 | 3.6645e-05
57 | 0.98054 | -0.13684 | 0.0004873 | 0.00012213
58 | 0.98054 | -0.13679 | 0.00052751 | 0.00013221
59 | 0.97979 | -0.14219 | 0.0012153 | 0.00030458
60 | 0.98261 | -0.12201 | 0 | 0
61 | 0.97972 | -0.14267 | 0.0010247 | 0.00025682
62 | 0.97939 | -0.14507 | 0.00073818 | 0.00018501
63 | 0.97912 | -0.14695 | 0.00072065 | 0.00018061
64 | 0.98973 | -0.071714 | 8.9505e-05 | 2.2432e-05
65 | 0.98979 | -0.071245 | 8.6943e-05 | 2.179e-05
66 | 0.9898 | -0.071153 | 8.9414e-05 | 2.2409e-05
67 | 0.98989 | -0.070539 | 8.6916e-05 | 2.1783e-05
68 | 0.98758 | -0.08706 | 0.00051489 | 0.00012904
69 | 0.98717 | -0.089639 | 0.00036159 | 9.0624e-05
70 | 0.98715 | -0.089819 | 0.00012845 | 3.2192e-05
71 | 0.98691 | -0.091492 | 0.00012829 | 3.2152e-05
72 | 0.98645 | -0.094758 | 0 | 0
73 | 0.98631 | -0.09574 | 0.00011172 | 2.8e-05
74 | 0.98595 | -0.098295 | 0.00063561 | 0.0001593
75 | 0.98571 | -0.10001 | 0 | 0
76 | 0.98567 | -0.10031 | 0 | 0
77 | 0.98546 | -0.10181 | 0.0007238 | 0.0001814
78 | 0.98626 | -0.096107 | 0.00011172 | 2.8e-05
79 | 0.98527 | -0.10313 | 0.00094619 | 0.00023714
80 | 0.99989 | -0.00075682 | 0.00019751 | 4.95e-05
81 | 0.9999 | -0.00070621 | 0.00033739 | 8.4558e-05
82 | 0.9855 | -0.10151 | 0.00028213 | 7.0708e-05
83 | 0.97801 | -0.15494 | 0.00029668 | 7.4355e-05
84 | 0.97798 | -0.15514 | 0.00036204 | 9.0735e-05
85 | 0.97798 | -0.15518 | 0.0006532 | 0.00016371
86 | 0.97795 | -0.15536 | 0.00024077 | 6.0342e-05
87 | 0.97871 | -0.14994 | 0.00037712 | 9.4514e-05
88 | 0.97797 | -0.15522 | 0.00045612 | 0.00011431
89 | 0.97795 | -0.15537 | 0.00045473 | 0.00011397
90 | 0.97879 | -0.14935 | 0.00047788 | 0.00011977
91 | 0.9788 | -0.14929 | 0.0012215 | 0.00030615
92 | 0.97896 | -0.14811 | 0.00076761 | 0.00019238
93 | 0.97911 | -0.14707 | 0.0014067 | 0.00035256
94 | 0.98485 | -0.1061 | 0.0013937 | 0.0003493
95 | 0.98428 | -0.11015 | 0.00068912 | 0.00017271
96 | 0.99027 | -0.067806 | 8.4861e-05 | 2.1268e-05
97 | 0.99992 | -0.00055901 | 0.0011787 | 0.00029541
98 | 0.99996 | -0.00026395 | 0.0011493 | 0.00028804
99 | 0.97796 | -0.15528 | 0.00049395 | 0.0001238
100 | 0.98994 | -0.070199 | 0.00051625 | 0.00012938
101 | 0.98999 | -0.069809 | 8.6916e-05 | 2.1783e-05
102 | 0.98991 | -0.070428 | 8.9414e-05 | 2.2409e-05
103 | 0.9901 | -0.069064 | 8.8448e-05 | 2.2167e-05
104 | 0.99017 | -0.068569 | 8.4796e-05 | 2.1252e-05
105 | 0.9902 | -0.068311 | 8.8542e-05 | 2.2191e-05
106 | 0.97794 | -0.15545 | 0.00027331 | 6.8498e-05
107 | 0.9852 | -0.10368 | 0.0025427 | 0.00063726
108 | 0.97173 | -0.19885 | 0.010052 | 0.0025194
109 | 0.97203 | -0.19669 | 0.0026708 | 0.00066937
110 | 0.97171 | -0.19903 | 0.0037065 | 0.00092893
111 | 0.97243 | -0.19381 | 0.0023775 | 0.00059585
112 | 0.97288 | -0.19057 | 0 | 0
113 | 0.97221 | -0.19545 | 0.0039622 | 0.00099303
114 | 0.9748 | -0.17683 | 0.0025581 | 0.00064112
115 | 0.97077 | -0.2058 | 0.013939 | 0.0034934
116 | 0.9711 | -0.20343 | 0.0040261 | 0.001009
117 | 0.98077 | -0.13428 | 0.001156 | 0.00028971
118 | 0.98216 | -0.12445 | 0.0024995 | 0.00062644
119 | 0.98074 | -0.13451 | 0.0016044 | 0.00040211
120 | 0.97999 | -0.13982 | 0.0035215 | 0.00088257
121 | 0.97969 | -0.14198 | 0.0015897 | 0.00039842
122 | 0.97957 | -0.14282 | 0.0014852 | 0.00037221
123 | 0.97759 | -0.1569 | 0.0036221 | 0.0009078
124 | 0.97793 | -0.15446 | 0.005605 | 0.0014047
125 | 0.97538 | -0.17268 | 0.0041859 | 0.0010491
126 | 0.97842 | -0.15101 | 0.0023292 | 0.00058375
127 | 0.97211 | -0.19613 | 0.0041817 | 0.001048
128 | 0.97159 | -0.19985 | 0.0030198 | 0.00075683
129 | 0.97129 | -0.20208 | 0.0031153 | 0.00078077
130 | 0.97115 | -0.20308 | 0.0028686 | 0.00071893
131 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0013855 | 0.00034654 | -0.0013854 | -0.00034688 | 8.2021e-08 | -3.4396e-07 | 0.0021017 | 0.0021019 | 0.0021019 | 0.98082 | -0.13571 | 0.98076 | -0.13614 | 0.77847
1 | -0.001957 | -0.00048977 | 0.0019572 | 0.00048949 | 1.4741e-07 | -2.8163e-07 | 0.0029688 | 0.0029686 | 0.0029688 | 0.98082 | -0.13571 | 0.98089 | -0.13516 | 1.0995
2 | 0.00091142 | 0.00022809 | -0.00091139 | -0.00022842 | 3.235e-08 | -3.2971e-07 | 0.0013827 | 0.0013828 | 0.0013828 | 0.98076 | -0.13614 | 0.98072 | -0.13639 | 0.51216
3 | -0.0019572 | -0.00048949 | 0.0019597 | 0.00048468 | 2.5105e-06 | -4.8086e-06 | 0.0029686 | 0.0029666 | 0.0029686 | 0.98089 | -0.13516 | 0.98219 | -0.12576 | 1.0995
4 | 0.00054834 | 0.00013628 | -0.0005483 | -0.00013742 | 3.9192e-08 | -1.1373e-06 | 0.00083032 | 0.00083073 | 0.00083073 | 0.98219 | -0.12576 | 0.98212 | -0.12628 | 0.30768
5 | -0.002508 | -0.00062096 | 0.0025084 | 0.00062055 | 3.9708e-07 | -4.0604e-07 | 0.0037969 | 0.0037967 | 0.0037969 | 0.98219 | -0.12576 | 0.98235 | -0.12459 | 1.4063
6 | -0.0029494 | -0.00073107 | 0.0029496 | 0.00073093 | 2.2163e-07 | -1.4036e-07 | 0.0044647 | 0.0044646 | 0.0044647 | 0.98235 | -0.12459 | 0.98243 | -0.12403 | 1.6536
7 | -0.0034809 | -0.00087087 | 0.0034818 | 0.00087057 | 8.9874e-07 | -2.9945e-07 | 0.0052947 | 0.0052945 | 0.0052947 | 0.97817 | -0.15382 | 0.97843 | -0.15194 | 1.961
8 | 0.0034809 | 0.00087087 | -0.0034806 | -0.00087098 | 3.1482e-07 | -1.048e-07 | 0.0052947 | 0.0052948 | 0.0052948 | 0.97817 | -0.15382 | 0.97808 | -0.15447 | 1.961
9 | -0.0039547 | -0.00098909 | 0.0039551 | 0.00098902 | 4.036e-07 | -6.9422e-08 | 0.0060136 | 0.0060136 | 0.0060136 | 0.97843 | -0.15194 | 0.97853 | -0.1512 | 2.2273
10 | 0.0032311 | 0.00080846 | -0.0032309 | -0.00080855 | 1.9637e-07 | -8.7936e-08 | 0.0049153 | 0.0049153 | 0.0049153 | 0.97808 | -0.15447 | 0.97801 | -0.15491 | 1.8205
11 | -0.0039551 | -0.00098902 | 0.0039558 | 0.0009889 | 6.867e-07 | -1.1824e-07 | 0.0060136 | 0.0060134 | 0.0060136 | 0.97853 | -0.1512 | 0.97871 | -0.14994 | 2.2272
12 | 0.0019 | 0.0004758 | -0.0019 | -0.00047582 | 8.0405e-09 | -1.6258e-08 | 0.0028907 | 0.0028907 | 0.0028907 | 0.97801 | -0.15491 | 0.97801 | -0.15494 | 1.0706
13 | 0.0013309 | 0.00033274 | -0.0013309 | -0.00033293 | 4.1841e-08 | -1.8916e-07 | 0.0020247 | 0.0020247 | 0.0020247 | 0.97801 | -0.15491 | 0.97798 | -0.15514 | 0.7499
14 | -0.0037779 | -0.00093853 | 0.0037787 | 0.00093836 | 7.4012e-07 | -1.746e-07 | 0.0057192 | 0.0057191 | 0.0057192 | 0.98243 | -0.12403 | 0.98263 | -0.12259 | 2.1182
15 | -0.0060201 | -0.0015001 | 0.0060228 | 0.0015005 | 2.6937e-06 | 3.7732e-07 | 0.0091134 | 0.0091131 | 0.0091134 | 0.98263 | -0.12259 | 0.98308 | -0.11932 | 3.3753
16 | -0.0091508 | -0.0022832 | 0.0091553 | 0.0022845 | 4.5571e-06 | 1.2614e-06 | 0.013789 | 0.013789 | 0.013789 | 0.98722 | -0.089622 | 0.98773 | -0.085994 | 5.1071
17 | 0.0074392 | 0.0018546 | -0.007409 | -0.0018479 | 3.0225e-05 | 6.7174e-06 | 0.011209 | 0.011211 | 0.011211 | 0.98722 | -0.089622 | 0.98308 | -0.11932 | 4.1523
18 | 0.0017116 | 0.00042862 | -0.0017115 | -0.00042893 | 1.1645e-07 | -3.1372e-07 | 0.0025797 | 0.0025799 | 0.0025799 | 0.98722 | -0.089622 | 0.98715 | -0.090114 | 0.9555
19 | -0.0092433 | -0.0023065 | 0.009245 | 0.002307 | 1.7062e-06 | 4.7563e-07 | 0.013922 | 0.013922 | 0.013922 | 0.98773 | -0.085994 | 0.98791 | -0.084649 | 5.1561
20 | 0.00097908 | 0.00024538 | -0.00097908 | -0.00024538 | 2.5489e-10 | -2.3011e-09 | 0.0014758 | 0.0014758 | 0.0014758 | 0.98715 | -0.090114 | 0.98715 | -0.090116 | 0.54661
21 | -0.0018179 | -0.00045373 | 0.001818 | 0.00045353 | 8.2759e-08 | -1.9474e-07 | 0.0027377 | 0.0027376 | 0.0027377 | 0.98787 | -0.084981 | 0.98791 | -0.084649 | 1.014
22 | 0.0018179 | 0.00045373 | -0.0018176 | -0.0004545 | 3.2591e-07 | -7.6656e-07 | 0.0027377 | 0.002738 | 0.002738 | 0.98787 | -0.084981 | 0.98768 | -0.086284 | 1.0141
23 | -0.011063 | -0.0027606 | 0.011067 | 0.0027618 | 4.0683e-06 | 1.2638e-06 | 0.016659 | 0.016659 | 0.016659 | 0.98791 | -0.084649 | 0.98829 | -0.081971 | 6.17
24 | 0.0015338 | 0.00038337 | -0.0015338 | -0.00038355 | 5.1425e-08 | -1.7779e-07 | 0.0023104 | 0.0023105 | 0.0023105 | 0.98768 | -0.086284 | 0.98765 | -0.086528 | 0.85575
25 | -0.01121 | -0.0027975 | 0.011216 | 0.0027994 | 5.8805e-06 | 1.8374e-06 | 0.016874 | 0.016873 | 0.016874 | 0.98829 | -0.081971 | 0.98882 | -0.078151 | 6.2495
26 | 0.0014467 | 0.00036172 | -0.0014466 | -0.00036194 | 5.4516e-08 | -2.1442e-07 | 0.0021793 | 0.0021794 | 0.0021794 | 0.98765 | -0.086528 | 0.98761 | -0.086801 | 0.80718
27 | -0.01152 | -0.0028758 | 0.011526 | 0.0028776 | 5.6526e-06 | 1.7871e-06 | 0.017332 | 0.017332 | 0.017332 | 0.98882 | -0.078151 | 0.98932 | -0.07458 | 6.4194
28 | 0.00051491 | 0.00012843 | -0.00051489 | -0.00012904 | 1.8382e-08 | -6.1938e-07 | 0.00077559 | 0.00077581 | 0.00077581 | 0.98761 | -0.086801 | 0.98758 | -0.08706 | 0.28734
29 | -0.10508 | -0.026471 | 0.1052 | 0.026515 | 0.00011733 | 4.4267e-05 | 0.15855 | 0.15855 | 0.15855 | 0.98654 | -0.093608 | 0.98768 | -0.085634 | 19.5736
30 | 0.094039 | 0.023703 | -0.093956 | -0.023672 | 8.2798e-05 | 3.1089e-05 | 0.14189 | 0.14189 | 0.14189 | 0.98654 | -0.093608 | 0.98564 | -0.099901 | 17.5171
31 | -0.10755 | -0.027105 | 0.10762 | 0.027132 | 7.141e-05 | 2.6963e-05 | 0.16209 | 0.16209 | 0.16209 | 0.98768 | -0.085634 | 0.98835 | -0.080894 | 20.0109
32 | 0.093956 | 0.023672 | -0.093882 | -0.023644 | 7.415e-05 | 2.7843e-05 | 0.14189 | 0.14189 | 0.14189 | 0.98564 | -0.099901 | 0.98484 | -0.10555 | 17.5171
33 | -0.1088 | -0.027427 | 0.10885 | 0.027446 | 4.8935e-05 | 1.8484e-05 | 0.16386 | 0.16386 | 0.16386 | 0.98835 | -0.080894 | 0.98881 | -0.077684 | 20.2301
34 | 0.08969 | 0.022594 | -0.08958 | -0.022553 | 0.00010965 | 4.1078e-05 | 0.13556 | 0.13556 | 0.13556 | 0.98484 | -0.10555 | 0.9836 | -0.1143 | 16.7352
35 | -0.11296 | -0.028475 | 0.11305 | 0.028509 | 8.9291e-05 | 3.3771e-05 | 0.17004 | 0.17004 | 0.17004 | 0.98881 | -0.077684 | 0.98962 | -0.072045 | 20.9929
36 | 0.084886 | 0.021376 | -0.084811 | -0.021348 | 7.4813e-05 | 2.7945e-05 | 0.12845 | 0.12845 | 0.12845 | 0.9836 | -0.1143 | 0.98271 | -0.12061 | 15.8586
37 | -0.12045 | -0.030363 | 0.12045 | 0.030366 | 8.7671e-06 | 3.3224e-06 | 0.18117 | 0.18117 | 0.18117 | 0.98962 | -0.072045 | 0.98969 | -0.071525 | 22.3664
38 | 0.084811 | 0.021348 | -0.084766 | -0.021331 | 4.543e-05 | 1.697e-05 | 0.12845 | 0.12845 | 0.12845 | 0.98271 | -0.12061 | 0.98216 | -0.12445 | 15.8586
39 | -0.043488 | -0.010913 | 0.043555 | 0.010938 | 6.663e-05 | 2.5302e-05 | 0.065196 | 0.065195 | 0.065196 | 0.99264 | -0.051095 | 0.99421 | -0.040072 | 24.1465
40 | 0.042272 | 0.010608 | -0.042221 | -0.010589 | 5.0809e-05 | 1.928e-05 | 0.063372 | 0.063372 | 0.063372 | 0.99264 | -0.051095 | 0.99141 | -0.059765 | 23.4712
41 | 0.12719 | 0.032127 | -0.12701 | -0.032057 | 0.00018405 | 6.9839e-05 | 0.19046 | 0.19046 | 0.19046 | 0.99421 | -0.040072 | 0.99272 | -0.050377 | 23.5133
42 | -0.17075 | -0.043065 | 0.1708 | 0.043085 | 5.3805e-05 | 2.054e-05 | 0.25565 | 0.25565 | 0.25565 | 0.99421 | -0.040072 | 0.99453 | -0.037825 | 31.5621
43 | 0.016373 | 0.0040946 | -0.016366 | -0.0040924 | 6.3677e-06 | 2.2312e-06 | 0.024571 | 0.024571 | 0.024571 | 0.99141 | -0.059765 | 0.99101 | -0.062588 | 9.1003
44 | 0.025848 | 0.0064939 | -0.025833 | -0.0064883 | 1.5103e-05 | 5.6015e-06 | 0.038802 | 0.038802 | 0.038802 | 0.99141 | -0.059765 | 0.99081 | -0.063968 | 14.371
45 | 0.1257 | 0.031728 | -0.12545 | -0.031636 | 0.00024318 | 9.2256e-05 | 0.18849 | 0.18849 | 0.18849 | 0.99272 | -0.050377 | 0.99074 | -0.06418 | 23.2705
46 | -0.1724 | -0.043487 | 0.17269 | 0.043597 | 0.00028866 | 0.00011021 | 0.25805 | 0.25805 | 0.25805 | 0.99453 | -0.037825 | 0.99625 | -0.025906 | 31.858
47 | 0.014342 | 0.003585 | -0.014335 | -0.0035826 | 7.0343e-06 | 2.3924e-06 | 0.021531 | 0.021531 | 0.021531 | 0.99101 | -0.062588 | 0.99051 | -0.06615 | 7.9744
48 | 0.024374 | 0.0061227 | -0.024359 | -0.006117 | 1.5321e-05 | 5.6568e-06 | 0.036611 | 0.036611 | 0.036611 | 0.99081 | -0.063968 | 0.99017 | -0.06849 | 13.5595
49 | 0.12308 | 0.03104 | -0.12295 | -0.030992 | 0.00012661 | 4.8008e-05 | 0.18492 | 0.18492 | 0.18492 | 0.99074 | -0.06418 | 0.98969 | -0.071525 | 22.8295
50 | -0.17391 | -0.043901 | 0.17454 | 0.044144 | 0.00063517 | 0.00024252 | 0.25986 | 0.25986 | 0.25986 | 0.99625 | -0.025906 | 1 | 0 | 32.0817
51 | 0.013675 | 0.0034173 | -0.013674 | -0.0034169 | 1.1789e-06 | 3.9578e-07 | 0.02054 | 0.02054 | 0.02054 | 0.99051 | -0.06615 | 0.99042 | -0.066777 | 7.6075
52 | 0.023142 | 0.0058122 | -0.023124 | -0.0058052 | 1.8842e-05 | 6.9263e-06 | 0.034783 | 0.034783 | 0.034783 | 0.99017 | -0.06849 | 0.98934 | -0.074352 | 12.8825
53 | 0.0028631 | 0.00071654 | -0.002863 | -0.00071662 | 1.0434e-07 | -8.0748e-08 | 0.0042599 | 0.00426 | 0.00426 | 1 | 0 | 0.99996 | -0.00026395 | 1.5778
54 | 0.013585 | 0.0033947 | -0.013585 | -0.0033946 | 4.771e-07 | 1.5987e-07 | 0.020407 | 0.020407 | 0.020407 | 0.99042 | -0.066777 | 0.99038 | -0.067032 | 7.5582
55 | 0.02295 | 0.0057617 | -0.022938 | -0.0057572 | 1.2319e-05 | 4.5256e-06 | 0.034522 | 0.034522 | 0.034522 | 0.98934 | -0.074352 | 0.98879 | -0.078218 | 12.7858
56 | -0.012007 | -0.002998 | 0.012011 | 0.0029995 | 4.7306e-06 | 1.5207e-06 | 0.018055 | 0.018055 | 0.018055 | 0.98932 | -0.07458 | 0.98973 | -0.071714 | 6.6869
57 | 0.0135 | 0.0033733 | -0.013499 | -0.003373 | 9.6e-07 | 3.211e-07 | 0.02028 | 0.02028 | 0.02028 | 0.99038 | -0.067032 | 0.99031 | -0.067549 | 7.511
58 | 0.013411 | 0.0033508 | -0.01341 | -0.0033506 | 4.7394e-07 | 1.5821e-07 | 0.020147 | 0.020147 | 0.020147 | 0.99031 | -0.067549 | 0.99027 | -0.067806 | 7.4618
59 | 0.021554 | 0.0054103 | -0.021542 | -0.0054059 | 1.2037e-05 | 4.3948e-06 | 0.032439 | 0.032439 | 0.032439 | 0.98879 | -0.078218 | 0.98822 | -0.082242 | 12.0144
60 | 0.021406 | 0.0053721 | -0.021399 | -0.0053695 | 7.0459e-06 | 2.5708e-06 | 0.032235 | 0.032236 | 0.032236 | 0.98822 | -0.082242 | 0.98788 | -0.084614 | 11.9391
61 | 0.021253 | 0.0053329 | -0.021247 | -0.0053306 | 6.1107e-06 | 2.228e-06 | 0.032015 | 0.032015 | 0.032015 | 0.98788 | -0.084614 | 0.98759 | -0.086687 | 11.8576
62 | 0.021101 | 0.005294 | -0.021092 | -0.0052908 | 8.639e-06 | 3.1475e-06 | 0.031795 | 0.031795 | 0.031795 | 0.98759 | -0.086687 | 0.98717 | -0.089639 | 11.776
63 | -0.01241 | -0.0031084 | 0.01241 | 0.0031084 | 8.6492e-08 | 2.8337e-08 | 0.018833 | 0.018833 | 0.018833 | 0.98054 | -0.13684 | 0.98054 | -0.13679 | 6.975
64 | 0.011923 | 0.0029863 | -0.011914 | -0.0029834 | 8.8203e-06 | 2.8482e-06 | 0.018093 | 0.018093 | 0.018093 | 0.98054 | -0.13684 | 0.97979 | -0.14219 | 6.7012
65 | -0.012938 | -0.0032406 | 0.012964 | 0.0032494 | 2.6478e-05 | 8.7922e-06 | 0.019633 | 0.019633 | 0.019633 | 0.98054 | -0.13679 | 0.98261 | -0.12201 | 7.2715
66 | 0.010699 | 0.0026788 | -0.010698 | -0.0026786 | 7.0173e-07 | 2.1625e-07 | 0.016248 | 0.016248 | 0.016248 | 0.97979 | -0.14219 | 0.97972 | -0.14267 | 6.0177
67 | -0.012964 | -0.0032494 | 0.012986 | 0.0032565 | 2.1322e-05 | 7.0758e-06 | 0.019633 | 0.019632 | 0.019633 | 0.98261 | -0.12201 | 0.98428 | -0.11015 | 7.2714
68 | 0.0096735 | 0.0024218 | -0.0096703 | -0.0024209 | 3.2164e-06 | 9.3646e-07 | 0.014691 | 0.014691 | 0.014691 | 0.97972 | -0.14267 | 0.97939 | -0.14507 | 5.4413
69 | 0.0089321 | 0.0022359 | -0.0089298 | -0.0022352 | 2.3188e-06 | 6.3798e-07 | 0.01357 | 0.01357 | 0.01357 | 0.97939 | -0.14507 | 0.97912 | -0.14695 | 5.0259
70 | 0.0082091 | 0.0020546 | -0.008209 | -0.0020546 | 1.3539e-07 | 3.4539e-08 | 0.012475 | 0.012475 | 0.012475 | 0.97912 | -0.14695 | 0.97911 | -0.14707 | 4.6203
71 | -0.012101 | -0.0030219 | 0.012102 | 0.0030222 | 7.8078e-07 | 2.5169e-07 | 0.018189 | 0.018189 | 0.018189 | 0.98973 | -0.071714 | 0.98979 | -0.071245 | 6.7367
72 | -0.012188 | -0.003044 | 0.012189 | 0.003044 | 1.5359e-07 | 4.9648e-08 | 0.01832 | 0.01832 | 0.01832 | 0.98979 | -0.071245 | 0.9898 | -0.071153 | 6.7851
73 | -0.012278 | -0.0030664 | 0.012279 | 0.0030668 | 1.0356e-06 | 3.3566e-07 | 0.018454 | 0.018454 | 0.018454 | 0.9898 | -0.071153 | 0.98989 | -0.070539 | 6.8349
74 | -0.012366 | -0.0030886 | 0.012366 | 0.0030886 | 1.8867e-07 | 6.1311e-08 | 0.018585 | 0.018585 | 0.018585 | 0.98989 | -0.070539 | 0.98991 | -0.070428 | 6.8833
75 | 0.020731 | 0.0052002 | -0.02073 | -0.0052 | 5.1699e-07 | 1.88e-07 | 0.03125 | 0.03125 | 0.03125 | 0.98717 | -0.089639 | 0.98715 | -0.089819 | 11.5741
76 | 0.020602 | 0.0051678 | -0.020597 | -0.0051661 | 4.7809e-06 | 1.7373e-06 | 0.031056 | 0.031057 | 0.031057 | 0.98715 | -0.089819 | 0.98691 | -0.091492 | 11.5024
77 | 0.020469 | 0.0051339 | -0.020459 | -0.0051306 | 9.2625e-06 | 3.3635e-06 | 0.030863 | 0.030863 | 0.030863 | 0.98691 | -0.091492 | 0.98645 | -0.094758 | 11.4308
78 | 0.015606 | 0.0039161 | -0.015604 | -0.0039154 | 2.1278e-06 | 7.3985e-07 | 0.023543 | 0.023543 | 0.023543 | 0.98645 | -0.094758 | 0.98631 | -0.09574 | 8.7195
79 | 0.0048536 | 0.0012144 | -0.0048512 | -0.0012144 | 2.3695e-06 | 7.2953e-09 | 0.0073207 | 0.007321 | 0.007321 | 0.98645 | -0.094758 | 0.98595 | -0.098295 | 2.7115
80 | 0.015492 | 0.0038874 | -0.015491 | -0.0038871 | 7.8963e-07 | 2.7415e-07 | 0.023374 | 0.023374 | 0.023374 | 0.98631 | -0.09574 | 0.98626 | -0.096107 | 8.657
81 | 0.0042156 | 0.0010551 | -0.0042146 | -0.0010553 | 1.0013e-06 | -1.204e-07 | 0.0063617 | 0.0063619 | 0.0063619 | 0.98595 | -0.098295 | 0.98571 | -0.10001 | 2.3563
82 | 0.0042146 | 0.0010553 | -0.0042144 | -0.0010553 | 1.7217e-07 | -2.0674e-08 | 0.0063619 | 0.0063619 | 0.0063619 | 0.98571 | -0.10001 | 0.98567 | -0.10031 | 2.3563
83 | 0.0042144 | 0.0010553 | -0.0042135 | -0.0010554 | 8.7089e-07 | -1.0445e-07 | 0.0063619 | 0.0063621 | 0.0063621 | 0.98567 | -0.10031 | 0.98546 | -0.10181 | 2.3563
84 | 0.0034897 | 0.00087398 | -0.0034891 | -0.00087421 | 6.3872e-07 | -2.2395e-07 | 0.0052692 | 0.0052693 | 0.0052693 | 0.98546 | -0.10181 | 0.98527 | -0.10313 | 1.9516
85 | 0.015379 | 0.0038591 | -0.015368 | -0.0038551 | 1.1517e-05 | 3.9927e-06 | 0.023205 | 0.023206 | 0.023206 | 0.98626 | -0.096107 | 0.9855 | -0.10151 | 8.5947
86 | 0.0025429 | 0.00063707 | -0.0025427 | -0.00063726 | 1.9236e-07 | -1.922e-07 | 0.0038403 | 0.0038404 | 0.0038404 | 0.98527 | -0.10313 | 0.9852 | -0.10368 | 1.4224
87 | -0.00019751 | -4.95e-05 | 0.00019751 | 4.9166e-05 | 1.3746e-09 | -3.3405e-07 | 0.00029393 | 0.00029381 | 0.00029393 | 0.99989 | -0.00075682 | 0.9999 | -0.00070621 | 0.10886
88 | -0.0005349 | -0.00013372 | 0.00053491 | 0.00013337 | 1.0818e-08 | -3.5488e-07 | 0.0007959 | 0.00079578 | 0.0007959 | 0.9999 | -0.00070621 | 0.99992 | -0.00055901 | 0.29478
89 | 0.015086 | 0.0037844 | -0.015076 | -0.0037811 | 9.5991e-06 | 3.3145e-06 | 0.02278 | 0.02278 | 0.02278 | 0.9855 | -0.10151 | 0.98485 | -0.1061 | 8.4369
90 | 0.0016033 | 0.00040146 | -0.0016033 | -0.00040162 | 5.1951e-08 | -1.5559e-07 | 0.0024393 | 0.0024393 | 0.0024393 | 0.97801 | -0.15494 | 0.97798 | -0.15518 | 0.90346
91 | 0.00096884 | 0.0002422 | -0.00096881 | -0.00024246 | 2.968e-08 | -2.633e-07 | 0.0014739 | 0.001474 | 0.001474 | 0.97798 | -0.15514 | 0.97795 | -0.15536 | 0.54592
92 | 0.00095008 | 0.00023791 | -0.00095007 | -0.00023796 | 4.9776e-09 | -4.5989e-08 | 0.0014455 | 0.0014455 | 0.0014455 | 0.97798 | -0.15518 | 0.97797 | -0.15522 | 0.53537
93 | 0.00072805 | 0.00018212 | -0.00072805 | -0.00018214 | 1.0258e-09 | -1.6417e-08 | 0.0011076 | 0.0011077 | 0.0011077 | 0.97795 | -0.15536 | 0.97795 | -0.15537 | 0.41024
94 | -0.0043329 | -0.0010834 | 0.0043332 | 0.0010834 | 3.5368e-07 | -2.8155e-08 | 0.0065868 | 0.0065867 | 0.0065868 | 0.97871 | -0.14994 | 0.97879 | -0.14935 | 2.4395
95 | 0.00049395 | 0.00012364 | -0.00049395 | -0.0001238 | 4.2671e-09 | -1.5028e-07 | 0.00075151 | 0.00075156 | 0.00075156 | 0.97797 | -0.15522 | 0.97796 | -0.15528 | 0.27836
96 | 0.00027331 | 6.817e-05 | -0.00027331 | -6.8498e-05 | 2.8271e-09 | -3.2771e-07 | 0.00041575 | 0.00041586 | 0.00041586 | 0.97795 | -0.15537 | 0.97794 | -0.15545 | 0.15402
97 | -0.0048111 | -0.0012032 | 0.0048112 | 0.0012032 | 4.242e-08 | 3.397e-10 | 0.0073132 | 0.0073132 | 0.0073132 | 0.97879 | -0.14935 | 0.9788 | -0.14929 | 2.7086
98 | -0.0060327 | -0.0015093 | 0.0060337 | 0.0015094 | 9.7942e-07 | 1.4207e-07 | 0.0091703 | 0.0091702 | 0.0091703 | 0.9788 | -0.14929 | 0.97896 | -0.14811 | 3.3964
99 | -0.0068013 | -0.0017018 | 0.0068023 | 0.001702 | 9.7489e-07 | 1.9109e-07 | 0.010337 | 0.010337 | 0.010337 | 0.97896 | -0.14811 | 0.97911 | -0.14707 | 3.8285
100 | 0.013683 | 0.0034318 | -0.013675 | -0.0034292 | 7.6821e-06 | 2.5883e-06 | 0.020674 | 0.020674 | 0.020674 | 0.98485 | -0.1061 | 0.98428 | -0.11015 | 7.6571
101 | 0.013325 | 0.0033294 | -0.013324 | -0.0033291 | 9.2668e-07 | 3.0875e-07 | 0.020019 | 0.020019 | 0.020019 | 0.99027 | -0.067806 | 0.9902 | -0.068311 | 7.4146
102 | -0.0017136 | -0.00042878 | 0.0017137 | 0.00042858 | 6.9739e-08 | -1.9868e-07 | 0.0025498 | 0.0025497 | 0.0025498 | 0.99992 | -0.00055901 | 0.99996 | -0.00026395 | 0.94438
103 | -0.012972 | -0.0032405 | 0.012973 | 0.0032408 | 6.9586e-07 | 2.2991e-07 | 0.019495 | 0.019495 | 0.019495 | 0.98994 | -0.070199 | 0.98999 | -0.069809 | 7.2205
104 | 0.012456 | 0.0031112 | -0.012456 | -0.003111 | 3.9265e-07 | 1.2793e-07 | 0.018719 | 0.018719 | 0.018719 | 0.98994 | -0.070199 | 0.98991 | -0.070428 | 6.9331
105 | -0.01306 | -0.0032626 | 0.013061 | 0.003263 | 1.3395e-06 | 4.4352e-07 | 0.019626 | 0.019626 | 0.019626 | 0.98999 | -0.069809 | 0.9901 | -0.069064 | 7.2689
106 | -0.01315 | -0.0032852 | 0.013151 | 0.0032855 | 8.9437e-07 | 2.9677e-07 | 0.019759 | 0.019759 | 0.019759 | 0.9901 | -0.069064 | 0.99017 | -0.068569 | 7.3181
107 | -0.013235 | -0.0033067 | 0.013236 | 0.0033069 | 4.7022e-07 | 1.5634e-07 | 0.019886 | 0.019886 | 0.019886 | 0.99017 | -0.068569 | 0.9902 | -0.068311 | 7.3653
108 | -0.013759 | -0.0034483 | 0.013763 | 0.0034497 | 4.1205e-06 | 1.4005e-06 | 0.021069 | 0.021069 | 0.021069 | 0.97173 | -0.19885 | 0.97203 | -0.19669 | 7.8033
109 | 0.0037065 | 0.00092891 | -0.0037065 | -0.00092893 | 9.0467e-08 | -2.0954e-08 | 0.0056758 | 0.0056758 | 0.0056758 | 0.97173 | -0.19885 | 0.97171 | -0.19903 | 2.1022
110 | -0.016434 | -0.004119 | 0.01644 | 0.0041214 | 6.5517e-06 | 2.3141e-06 | 0.025158 | 0.025157 | 0.025158 | 0.97203 | -0.19669 | 0.97243 | -0.19381 | 9.3176
111 | -0.018818 | -0.0047172 | 0.018826 | 0.0047202 | 8.4513e-06 | 3.0478e-06 | 0.028795 | 0.028795 | 0.028795 | 0.97243 | -0.19381 | 0.97288 | -0.19057 | 10.665
112 | 0.035169 | 0.008821 | -0.035145 | -0.008812 | 2.3773e-05 | 8.9801e-06 | 0.053793 | 0.053793 | 0.053793 | 0.97288 | -0.19057 | 0.97221 | -0.19545 | 19.9233
113 | -0.053995 | -0.013541 | 0.054098 | 0.013581 | 0.00010303 | 3.9326e-05 | 0.082588 | 0.082588 | 0.082588 | 0.97288 | -0.19057 | 0.9748 | -0.17683 | 30.5882
114 | 0.031183 | 0.007819 | -0.03118 | -0.0078179 | 2.9208e-06 | 1.0979e-06 | 0.047729 | 0.047729 | 0.047729 | 0.97221 | -0.19545 | 0.97211 | -0.19613 | 17.6772
115 | -0.056656 | -0.014222 | 0.056689 | 0.014234 | 3.266e-05 | 1.2474e-05 | 0.086493 | 0.086493 | 0.086493 | 0.9748 | -0.17683 | 0.97538 | -0.17268 | 32.0344
116 | -0.013939 | -0.0034934 | 0.013943 | 0.003495 | 4.5619e-06 | 1.5565e-06 | 0.021366 | 0.021366 | 0.021366 | 0.97077 | -0.2058 | 0.9711 | -0.20343 | 7.9132
117 | -0.017969 | -0.004504 | 0.01797 | 0.0045043 | 8.844e-07 | 3.1702e-07 | 0.027535 | 0.027535 | 0.027535 | 0.9711 | -0.20343 | 0.97115 | -0.20308 | 10.1981
118 | -0.082153 | -0.020663 | 0.082266 | 0.020705 | 0.00011281 | 4.2065e-05 | 0.12467 | 0.12467 | 0.12467 | 0.98077 | -0.13428 | 0.98216 | -0.12445 | 15.3911
119 | 0.080997 | 0.020373 | -0.080995 | -0.020372 | 2.5472e-06 | 9.4899e-07 | 0.12291 | 0.12291 | 0.12291 | 0.98077 | -0.13428 | 0.98074 | -0.13451 | 15.1746
120 | 0.07939 | 0.01997 | -0.079331 | -0.019948 | 5.8812e-05 | 2.1883e-05 | 0.12048 | 0.12048 | 0.12048 | 0.98074 | -0.13451 | 0.97999 | -0.13982 | 14.8741
121 | 0.07581 | 0.019066 | -0.075787 | -0.019057 | 2.2739e-05 | 8.434e-06 | 0.11513 | 0.11513 | 0.11513 | 0.97999 | -0.13982 | 0.97969 | -0.14198 | 14.214
122 | 0.074198 | 0.018659 | -0.074189 | -0.018656 | 8.7728e-06 | 3.2488e-06 | 0.11272 | 0.11272 | 0.11272 | 0.97969 | -0.14198 | 0.97957 | -0.14282 | 13.9159
123 | 0.072704 | 0.018283 | -0.072621 | -0.018252 | 8.2895e-05 | 3.1335e-05 | 0.11046 | 0.11046 | 0.11046 | 0.97957 | -0.14282 | 0.97842 | -0.15101 | 20.4561
124 | -0.064631 | -0.016242 | 0.064653 | 0.016251 | 2.1968e-05 | 8.4035e-06 | 0.098392 | 0.098392 | 0.098392 | 0.97759 | -0.1569 | 0.97793 | -0.15446 | 36.4415
125 | 0.061009 | 0.015334 | -0.060875 | -0.015283 | 0.00013377 | 5.1138e-05 | 0.092879 | 0.092879 | 0.092879 | 0.97759 | -0.1569 | 0.97538 | -0.17268 | 34.3996
126 | -0.070258 | -0.017655 | 0.070292 | 0.017668 | 3.373e-05 | 1.2914e-05 | 0.10692 | 0.10692 | 0.10692 | 0.97793 | -0.15446 | 0.97842 | -0.15101 | 39.6003
127 | 0.026998 | 0.0067698 | -0.026984 | -0.0067646 | 1.3936e-05 | 5.1979e-06 | 0.041328 | 0.041328 | 0.041328 | 0.97211 | -0.19613 | 0.97159 | -0.19985 | 15.3065
128 | 0.023965 | 0.0060078 | -0.023957 | -0.0060051 | 7.3913e-06 | 2.7339e-06 | 0.036703 | 0.036703 | 0.036703 | 0.97159 | -0.19985 | 0.97129 | -0.20208 | 13.5936
129 | 0.020842 | 0.0052243 | -0.020839 | -0.0052232 | 2.8801e-06 | 1.0517e-06 | 0.03193 | 0.03193 | 0.03193 | 0.97129 | -0.20208 | 0.97115 | -0.20308 | 11.826

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.17905 | 0.045073

## res_load
| p_mw | q_mvar
0 | 0.0005715 | 0.00014323
1 | 0.000474 | 0.0001188
2 | 0.00091139 | 0.00022842
3 | 0.0005483 | 0.00013742
4 | 0.00044096 | 0.00011052
5 | 0.00047289 | 0.00011852
6 | 0.00024945 | 6.2517e-05
7 | 0.00082835 | 0.0002076
8 | 0.0022415 | 0.00056176
9 | 8.7991e-05 | 2.2053e-05
10 | 0.0013861 | 0.0003474
11 | 0.0007324 | 0.00018356
12 | 0.0002838 | 7.1126e-05
13 | 0.0001425 | 3.5713e-05
14 | 8.7084e-05 | 2.1825e-05
15 | 0.00030491 | 7.6418e-05
16 | 0.00093172 | 0.00023351
17 | 0.011044 | 0.0027678
18 | 0.0023515 | 0.00058935
19 | 0.0011793 | 0.00029555
20 | 0.004192 | 0.0010506
21 | 0.0041058 | 0.001029
22 | 0.0046942 | 0.0011765
23 | 0.0073992 | 0.0018544
24 | 0.00097908 | 0.00024538
25 | 0.0012164 | 0.00030486
26 | 0.0013125 | 0.00032895
27 | 0.0016022 | 0.00040155
28 | 0.0020246 | 0.00050741
29 | 0.0014589 | 0.00036564
30 | 0.0023785 | 0.00059612
31 | 0.0012133 | 0.00030408
32 | 0.00065946 | 0.00016528
33 | 0.0012164 | 0.00030486
34 | 0.002495 | 0.00062532
35 | 0.00084853 | 0.00021266
36 | 8.8542e-05 | 2.2191e-05
37 | 0.00017364 | 4.3517e-05
38 | 0.00048043 | 0.00012041
39 | 8.4861e-05 | 2.1268e-05
40 | 8.8448e-05 | 2.2167e-05
41 | 0.0013841 | 0.00034688
42 | 0.00013507 | 3.3853e-05
43 | 0.00014617 | 3.6634e-05
44 | 0.00014622 | 3.6645e-05
45 | 0.0004873 | 0.00012213
46 | 0.00052751 | 0.00013221
47 | 0.0012153 | 0.00030458
48 | 0.0010247 | 0.00025682
49 | 0.00073818 | 0.00018501
50 | 0.00072065 | 0.00018061
51 | 8.9505e-05 | 2.2432e-05
52 | 8.6943e-05 | 2.179e-05
53 | 8.9414e-05 | 2.2409e-05
54 | 8.6916e-05 | 2.1783e-05
55 | 0.00051489 | 0.00012904
56 | 0.00036159 | 9.0624e-05
57 | 0.00012845 | 3.2192e-05
58 | 0.00012829 | 3.2152e-05
59 | 0.00011172 | 2.8e-05
60 | 0.00063561 | 0.0001593
61 | 0.0007238 | 0.0001814
62 | 0.00011172 | 2.8e-05
63 | 0.00094619 | 0.00023714
64 | 0.00019751 | 4.95e-05
65 | 0.00033739 | 8.4558e-05
66 | 0.00028213 | 7.0708e-05
67 | 0.00029668 | 7.4355e-05
68 | 0.00036204 | 9.0735e-05
69 | 0.0006532 | 0.00016371
70 | 0.00024077 | 6.0342e-05
71 | 0.00037712 | 9.4514e-05
72 | 0.00045612 | 0.00011431
73 | 0.00045473 | 0.00011397
74 | 0.00047788 | 0.00011977
75 | 0.0012215 | 0.00030615
76 | 0.00076761 | 0.00019238
77 | 0.0014067 | 0.00035256
78 | 0.0013937 | 0.0003493
79 | 0.00068912 | 0.00017271
80 | 8.4861e-05 | 2.1268e-05
81 | 0.0011787 | 0.00029541
82 | 0.0011493 | 0.00028804
83 | 0.00049395 | 0.0001238
84 | 0.00051625 | 0.00012938
85 | 8.6916e-05 | 2.1783e-05
86 | 8.9414e-05 | 2.2409e-05
87 | 8.8448e-05 | 2.2167e-05
88 | 8.4796e-05 | 2.1252e-05
89 | 8.8542e-05 | 2.2191e-05
90 | 0.00027331 | 6.8498e-05
91 | 0.0025427 | 0.00063726
92 | 0.010052 | 0.0025194
93 | 0.0026708 | 0.00066937
94 | 0.0037065 | 0.00092893
95 | 0.0023775 | 0.00059585
96 | 0.0039622 | 0.00099303
97 | 0.0025581 | 0.00064112
98 | 0.013939 | 0.0034934
99 | 0.0040261 | 0.001009
100 | 0.001156 | 0.00028971
101 | 0.0024995 | 0.00062644
102 | 0.0016044 | 0.00040211
103 | 0.0035215 | 0.00088257
104 | 0.0015897 | 0.00039842
105 | 0.0014852 | 0.00037221
106 | 0.0036221 | 0.0009078
107 | 0.005605 | 0.0014047
108 | 0.0041859 | 0.0010491
109 | 0.0023292 | 0.00058375
110 | 0.0041817 | 0.001048
111 | 0.0030198 | 0.00075683
112 | 0.0031153 | 0.00078077
113 | 0.0028686 | 0.00071893

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1