## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1146-1_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1146-1_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1146-1_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1146-1_0_6_node_19 | 0.4 | n |  | TRUE
4 | bus_LV_1146-1_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1146-1_0_6_node_85 | 0.4 | n |  | TRUE
6 | bus_LV_1146-1_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1146-1_0_6_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1146-1_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1146-1_0_6_node_80 | 0.4 | n |  | TRUE
10 | bus_LV_1146-1_0_6_node_11 | 0.4 | n |  | TRUE
11 | bus_LV_1146-1_0_6_node_69 | 0.4 | n |  | TRUE
12 | bus_LV_1146-1_0_6_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1146-1_0_6_node_12 | 0.4 | n |  | TRUE
14 | bus_LV_1146-1_0_6_node_63 | 0.4 | n |  | TRUE
15 | bus_LV_1146-1_0_6_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1146-1_0_6_node_61 | 0.4 | n |  | TRUE
17 | bus_LV_1146-1_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1146-1_0_6_node_57 | 0.4 | n |  | TRUE
19 | bus_LV_1146-1_0_6_node_9 | 0.4 | n |  | TRUE
20 | bus_LV_1146-1_0_6_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1146-1_0_6_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1146-1_0_6_node_64 | 0.4 | n |  | TRUE
23 | bus_LV_1146-1_0_6_node_62 | 0.4 | n |  | TRUE
24 | bus_LV_1146-1_0_6_node_55 | 0.4 | n |  | TRUE
25 | bus_LV_1146-1_0_6_node_50 | 0.4 | n |  | TRUE
26 | bus_LV_1146-1_0_6_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_1146-1_0_6_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_1146-1_0_6_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1146-1_0_6_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1146-1_0_6_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_1146-1_0_6_node_59 | 0.4 | n |  | TRUE
32 | bus_LV_1146-1_0_6_node_20 | 0.4 | n |  | TRUE
33 | bus_LV_1146-1_0_6_node_25 | 0.4 | n |  | TRUE
34 | bus_LV_1146-1_0_6_node_49 | 0.4 | n |  | TRUE
35 | bus_LV_1146-1_0_6_node_60 | 0.4 | n |  | TRUE
36 | bus_LV_1146-1_0_6_node_56 | 0.4 | n |  | TRUE
37 | bus_LV_1146-1_0_6_node_74 | 0.4 | n |  | TRUE
38 | bus_LV_1146-1_0_6_node_68 | 0.4 | n |  | TRUE
39 | bus_LV_1146-1_0_6_node_53 | 0.4 | n |  | TRUE
40 | bus_LV_1146-1_0_6_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_1146-1_0_6_node_78 | 0.4 | n |  | TRUE
42 | bus_LV_1146-1_0_6_node_76 | 0.4 | n |  | TRUE
43 | bus_LV_1146-1_0_6_node_77 | 0.4 | n |  | TRUE
44 | bus_LV_1146-1_0_6_node_47 | 0.4 | n |  | TRUE
45 | bus_LV_1146-1_0_6_node_23 | 0.4 | n |  | TRUE
46 | bus_LV_1146-1_0_6_node_24 | 0.4 | n |  | TRUE
47 | bus_LV_1146-1_0_6_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_1146-1_0_6_node_28 | 0.4 | n |  | TRUE
49 | bus_LV_1146-1_0_6_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_1146-1_0_6_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_1146-1_0_6_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_1146-1_0_6_node_33 | 0.4 | n |  | TRUE
53 | bus_LV_1146-1_0_6_node_31 | 0.4 | n |  | TRUE
54 | bus_LV_1146-1_0_6_node_32 | 0.4 | n |  | TRUE
55 | bus_LV_1146-1_0_6_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_1146-1_0_6_node_39 | 0.4 | n |  | TRUE
57 | bus_LV_1146-1_0_6_node_37 | 0.4 | n |  | TRUE
58 | bus_LV_1146-1_0_6_node_36 | 0.4 | n |  | TRUE
59 | bus_LV_1146-1_0_6_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_1146-1_0_6_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_1146-1_0_6_node_44 | 0.4 | n |  | TRUE
62 | bus_LV_1146-1_0_6_node_42 | 0.4 | n |  | TRUE
63 | bus_LV_1146-1_0_6_node_41 | 0.4 | n |  | TRUE
64 | bus_LV_1146-1_0_6_node_45 | 0.4 | n |  | TRUE
65 | bus_LV_1146-1_0_6_node_46 | 0.4 | n |  | TRUE
66 | bus_LV_1146-1_0_6_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_1146-1_0_6_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_1146-1_0_6_node_71 | 0.4 | n |  | TRUE
69 | bus_LV_1146-1_0_6_node_70 | 0.4 | n |  | TRUE
70 | bus_LV_1146-1_0_6_node_67 | 0.4 | n |  | TRUE
71 | bus_LV_1146-1_0_6_node_65 | 0.4 | n |  | TRUE
72 | bus_LV_1146-1_0_6_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_1146-1_0_6_node_72 | 0.4 | n |  | TRUE
74 | bus_LV_1146-1_0_6_node_73 | 0.4 | n |  | TRUE
75 | bus_LV_1146-1_0_6_node_83 | 0.4 | n |  | TRUE
76 | bus_LV_1146-1_0_6_node_84 | 0.4 | n |  | TRUE
77 | bus_LV_1146-1_0_6_node_79 | 0.4 | n |  | TRUE
78 | bus_LV_1146-1_0_6_node_81 | 0.4 | n |  | TRUE
79 | bus_LV_1146-1_0_6_node_82 | 0.4 | n |  | TRUE
80 | bus_MV_131_0_node_203 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1146-1_0_6_load_0 | 0 | 0.0016443 | 0.0004121 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1146-1_0_6_load_1 | 1 | 0.0026213 | 0.00065696 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1146-1_0_6_load_3 | 2 | 0.0019182 | 0.00048075 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1146-1_0_6_load_85 | 5 | 0.0021226 | 0.00053197 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1146-1_0_6_load_80 | 9 | 0.010253 | 0.0025696 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1146-1_0_6_load_69 | 11 | 0.012827 | 0.0032148 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1146-1_0_6_load_63 | 14 | 0.0082245 | 0.0020613 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1146-1_0_6_load_57 | 18 | 0.0015245 | 0.00038206 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1146-1_0_6_load_21 | 21 | 0.0013231 | 0.00033161 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1146-1_0_6_load_64 | 22 | 0.01072 | 0.0026868 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1146-1_0_6_load_62 | 23 | 0.0034414 | 0.0008625 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1146-1_0_6_load_50 | 25 | 0.0015694 | 0.00039333 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1146-1_0_6_load_58 | 27 | 0.0033023 | 0.00082764 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1146-1_0_6_load_48 | 30 | 0.0090157 | 0.0022596 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1146-1_0_6_load_59 | 31 | 0.013806 | 0.0034602 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1146-1_0_6_load_49 | 34 | 0.0090622 | 0.0022712 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1146-1_0_6_load_60 | 35 | 0.013574 | 0.003402 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1146-1_0_6_load_56 | 36 | 0.0030288 | 0.00075908 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1146-1_0_6_load_74 | 37 | 0.0022048 | 0.00055257 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1146-1_0_6_load_68 | 38 | 0.0051733 | 0.0012966 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1146-1_0_6_load_75 | 40 | 0.0039663 | 0.00099404 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1146-1_0_6_load_78 | 41 | 0.003406 | 0.00085362 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1146-1_0_6_load_76 | 42 | 0.0029933 | 0.0007502 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1146-1_0_6_load_23 | 45 | 0.00042912 | 0.00010755 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1146-1_0_6_load_24 | 46 | 0.00056128 | 0.00014067 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1146-1_0_6_load_26 | 47 | 0.0005088 | 0.00012752 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1146-1_0_6_load_34 | 49 | 0.00047404 | 0.0001188 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1146-1_0_6_load_30 | 50 | 0.00031597 | 7.9189e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1146-1_0_6_load_29 | 51 | 0.00045981 | 0.00011524 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1146-1_0_6_load_32 | 54 | 0.0057675 | 0.0014455 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1146-1_0_6_load_35 | 55 | 0.0034269 | 0.00085885 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1146-1_0_6_load_39 | 56 | 0.0058395 | 0.0014635 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1146-1_0_6_load_37 | 57 | 0.0029464 | 0.00073843 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1146-1_0_6_load_36 | 58 | 0.0053832 | 0.0013492 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1146-1_0_6_load_38 | 59 | 0.0039918 | 0.0010004 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1146-1_0_6_load_40 | 60 | 0.0062629 | 0.0015696 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1146-1_0_6_load_42 | 62 | 0.00043148 | 0.00010814 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1146-1_0_6_load_41 | 63 | 0.00077442 | 0.00019409 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1146-1_0_6_load_45 | 64 | 0.013646 | 0.0034199 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1146-1_0_6_load_46 | 65 | 0.0063256 | 0.0015854 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1146-1_0_6_load_51 | 66 | 0.0032347 | 0.0008107 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1146-1_0_6_load_52 | 67 | 0.0012045 | 0.00030188 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1146-1_0_6_load_71 | 68 | 0.0016605 | 0.00041617 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1146-1_0_6_load_70 | 69 | 0.0020447 | 0.00051246 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1146-1_0_6_load_67 | 70 | 0.0032497 | 0.00081445 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1146-1_0_6_load_65 | 71 | 0.0067301 | 0.0016867 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1146-1_0_6_load_66 | 72 | 0.0025384 | 0.00063618 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1146-1_0_6_load_72 | 73 | 0.0027009 | 0.00067691 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1146-1_0_6_load_73 | 74 | 0.0033732 | 0.0008454 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1146-1_0_6_load_83 | 75 | 0.001281 | 0.00032105 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1146-1_0_6_load_84 | 76 | 0.001201 | 0.00030101 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1146-1_0_6_load_79 | 77 | 0.0038326 | 0.00096053 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1146-1_0_6_load_81 | 78 | 0.0012243 | 0.00030684 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1146-1_0_6_load_82 | 79 | 0.0011934 | 0.00029909 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1146-1_0_6_line_0 | NAYY 4x150 SE | 0 | 1 | 0.039661 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1146-1_0_6_line_1 | NAYY 4x150 SE | 1 | 2 | 0.03743 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1146-1_0_6_line_2 | NAYY 4x150 SE | 2 | 3 | 0.032109 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1146-1_0_6_line_3 | NAYY 4x150 SE | 3 | 32 | 0.007843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1146-1_0_6_line_4 | NAYY 4x150 SE | 3 | 29 | 0.056856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1146-1_0_6_line_5 | NAYY 4x150 SE | 4 | 5 | 0.069025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1146-1_0_6_line_6 | NAYY 4x150 SE | 4 | 6 | 0.10588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1146-1_0_6_line_7 | NAYY 4x150 SE | 4 | 7 | 0.10055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
8 | LV_1146-1_0_6_line_8 | NAYY 4x150 SE | 6 | 10 | 0.050615 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1146-1_0_6_line_9 | NAYY 4x150 SE | 6 | 11 | 0.023264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1146-1_0_6_line_10 | NAYY 4x150 SE | 6 | 8 | 0.034162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1146-1_0_6_line_11 | NAYY 4x150 SE | 7 | 25 | 0.044271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
12 | LV_1146-1_0_6_line_12 | NAYY 4x150 SE | 8 | 9 | 0.011791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1146-1_0_6_line_13 | NAYY 4x150 SE | 10 | 22 | 0.031647 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1146-1_0_6_line_14 | NAYY 4x150 SE | 10 | 23 | 0.055715 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1146-1_0_6_line_15 | NAYY 4x150 SE | 10 | 15 | 0.050799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1146-1_0_6_line_16 | NAYY 4x150 SE | 12 | 13 | 0.05768 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1146-1_0_6_line_17 | NAYY 4x150 SE | 12 | 14 | 0.06196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1146-1_0_6_line_18 | NAYY 4x150 SE | 13 | 24 | 0.02237 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1146-1_0_6_line_19 | NAYY 4x150 SE | 14 | 23 | 0.028167 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1146-1_0_6_line_20 | NAYY 4x150 SE | 15 | 16 | 0.004405 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1146-1_0_6_line_21 | NAYY 4x150 SE | 15 | 17 | 0.01677 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1146-1_0_6_line_22 | NAYY 4x150 SE | 15 | 18 | 0.029909 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1146-1_0_6_line_23 | NAYY 4x150 SE | 16 | 35 | 0.022993 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1146-1_0_6_line_24 | NAYY 4x150 SE | 17 | 21 | 0.015242 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1146-1_0_6_line_25 | NAYY 4x150 SE | 18 | 36 | 0.020928 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1146-1_0_6_line_26 | NAYY 4x150 SE | 19 | 20 | 0.013563 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1146-1_0_6_line_27 | NAYY 4x150 SE | 19 | 21 | 0.0084233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1146-1_0_6_line_28 | NAYY 4x150 SE | 20 | 37 | 0.035055 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1146-1_0_6_line_29 | NAYY 4x150 SE | 22 | 38 | 0.013926 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1146-1_0_6_line_30 | NAYY 4x150 SE | 24 | 39 | 0.034383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1146-1_0_6_line_31 | NAYY 4x150 SE | 25 | 34 | 0.045178 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
32 | LV_1146-1_0_6_line_32 | NAYY 4x150 SE | 26 | 27 | 0.019802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1146-1_0_6_line_33 | NAYY 4x150 SE | 26 | 28 | 0.033589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1146-1_0_6_line_34 | NAYY 4x150 SE | 27 | 41 | 0.024671 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1146-1_0_6_line_35 | NAYY 4x150 SE | 28 | 31 | 0.021297 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1146-1_0_6_line_36 | NAYY 4x150 SE | 29 | 30 | 0.030031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1146-1_0_6_line_37 | NAYY 4x150 SE | 30 | 44 | 0.032791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1146-1_0_6_line_38 | NAYY 4x150 SE | 31 | 35 | 0.033585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1146-1_0_6_line_39 | NAYY 4x150 SE | 32 | 33 | 0.094023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
40 | LV_1146-1_0_6_line_40 | NAYY 4x150 SE | 32 | 34 | 0.019875 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
41 | LV_1146-1_0_6_line_41 | NAYY 4x150 SE | 33 | 45 | 0.016003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
42 | LV_1146-1_0_6_line_42 | NAYY 4x150 SE | 37 | 40 | 0.021838 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1146-1_0_6_line_43 | NAYY 4x150 SE | 38 | 70 | 0.01709 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1146-1_0_6_line_44 | NAYY 4x150 SE | 39 | 66 | 0.072976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1146-1_0_6_line_45 | NAYY 4x150 SE | 41 | 43 | 0.014864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1146-1_0_6_line_46 | NAYY 4x150 SE | 42 | 43 | 0.0087535 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1146-1_0_6_line_47 | NAYY 4x150 SE | 43 | 77 | 0.013806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1146-1_0_6_line_48 | NAYY 4x150 SE | 44 | 65 | 0.023798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
49 | LV_1146-1_0_6_line_49 | NAYY 4x150 SE | 45 | 46 | 0.028252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
50 | LV_1146-1_0_6_line_50 | NAYY 4x150 SE | 46 | 47 | 0.02978 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1146-1_0_6_line_51 | NAYY 4x150 SE | 47 | 48 | 0.026767 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1146-1_0_6_line_52 | NAYY 4x150 SE | 48 | 49 | 0.0034962 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1146-1_0_6_line_53 | NAYY 4x150 SE | 49 | 52 | 0.016447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1146-1_0_6_line_54 | NAYY 4x150 SE | 50 | 51 | 0.02575 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1146-1_0_6_line_55 | NAYY 4x150 SE | 51 | 53 | 0.027177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1146-1_0_6_line_56 | NAYY 4x150 SE | 52 | 55 | 0.016868 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1146-1_0_6_line_57 | NAYY 4x150 SE | 52 | 53 | 0.02409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1146-1_0_6_line_58 | NAYY 4x150 SE | 53 | 54 | 0.0021273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1146-1_0_6_line_59 | NAYY 4x150 SE | 55 | 56 | 0.014803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1146-1_0_6_line_60 | NAYY 4x150 SE | 56 | 57 | 0.001572 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1146-1_0_6_line_61 | NAYY 4x150 SE | 57 | 58 | 0.037611 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1146-1_0_6_line_62 | NAYY 4x150 SE | 58 | 59 | 0.001236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1146-1_0_6_line_63 | NAYY 4x150 SE | 59 | 60 | 0.020491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1146-1_0_6_line_64 | NAYY 4x150 SE | 60 | 61 | 0.040471 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1146-1_0_6_line_65 | NAYY 4x150 SE | 61 | 62 | 0.0093404 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1146-1_0_6_line_66 | NAYY 4x150 SE | 62 | 63 | 0.027738 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1146-1_0_6_line_67 | NAYY 4x150 SE | 64 | 65 | 0.018283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1146-1_0_6_line_68 | NAYY 4x150 SE | 66 | 67 | 2.9094e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1146-1_0_6_line_69 | NAYY 4x150 SE | 68 | 69 | 0.0020115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1146-1_0_6_line_70 | NAYY 4x150 SE | 69 | 73 | 0.019137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1146-1_0_6_line_71 | NAYY 4x150 SE | 70 | 71 | 0.00093954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1146-1_0_6_line_72 | NAYY 4x150 SE | 71 | 72 | 0.019808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1146-1_0_6_line_73 | NAYY 4x150 SE | 73 | 74 | 0.012044 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1146-1_0_6_line_74 | NAYY 4x150 SE | 74 | 75 | 0.0066957 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1146-1_0_6_line_75 | NAYY 4x150 SE | 75 | 76 | 0.0075546 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1146-1_0_6_line_76 | NAYY 4x150 SE | 76 | 79 | 0.007315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1146-1_0_6_line_77 | NAYY 4x150 SE | 77 | 78 | 0.00074468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1146-1_0_6_line_78 | NAYY 4x150 SE | 78 | 79 | 0.0074434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1146-1_0_6_trafo_6 | 0.25 MVA 20/0.4 kV | 80 | 6 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12
0 | 2644099.8413 | 1226068.1939 | 2644070.8804 | 1226062.7793 | 2644060.7035 | 1226062.1146
1 | 2644060.7035 | 1226062.1146 | 2644023.3531 | 1226059.6752
2 | 2643991.5105 | 1226059.9797 | 2643999.4679 | 1226058.1151 | 2644023.3531 | 1226059.6752
3 | 2643986.8561 | 1226053.8861 | 2643988.8091 | 1226055.268 | 2643990.2722 | 1226057.28 | 2643991.5105 | 1226059.9797
4 | 2643991.5105 | 1226059.9797 | 2644002.384 | 1226112.7479 | 2644005.3426 | 1226112.4029
5 | 2644147.3354 | 1226180.5844 | 2644108.8792 | 1226172.0276 | 2644096.0073 | 1226198.8487
6 | 2644096.0073 | 1226198.8487 | 2644111.4748 | 1226204.2999 | 2644119.9389 | 1226206.653 | 2644130.9867 | 1226209.1363 | 2644147.1623 | 1226211.0796 | 2644160.0927 | 1226211.1311 | 2644160.0638 | 1226211.9536 | 2644159.8447 | 1226216.9773 | 2644159.6146 | 1226222.4456 | 2644159.5502 | 1226223.9794 | 2644179.9268 | 1226231.7797 | 2644183.2612 | 1226232.8829 | 2644184.8979 | 1226233.9624
7 | 2644006.364 | 1226160.8402 | 2644012.2166 | 1226160.6944 | 2644016.2047 | 1226160.5349 | 2644016.689 | 1226162.6843 | 2644019.4207 | 1226167.3962 | 2644024.3947 | 1226171.2576 | 2644027.311 | 1226172.5355 | 2644039.31 | 1226176.5822 | 2644068.7617 | 1226188.2072 | 2644077.1355 | 1226191.5045 | 2644096.0073 | 1226198.8487
8 | 2644184.8979 | 1226233.9624 | 2644188.7486 | 1226231.8897 | 2644190.6739 | 1226230.8478 | 2644192.5489 | 1226234.5529 | 2644195.9712 | 1226239.1255 | 2644200.6936 | 1226243.163 | 2644206.8374 | 1226246.6552 | 2644221.1387 | 1226258.0573 | 2644223.2797 | 1226256.55
9 | 2644184.8979 | 1226233.9624 | 2644192.3272 | 1226238.8872 | 2644202.9303 | 1226248.5571
10 | 2644184.8979 | 1226233.9624 | 2644188.7486 | 1226231.8897 | 2644190.6739 | 1226230.8478 | 2644192.9654 | 1226230.5201 | 2644194.5134 | 1226230.287 | 2644197.1463 | 1226229.9063 | 2644201.3008 | 1226229.7815 | 2644201.4742 | 1226228.8934 | 2644201.9546 | 1226227.485 | 2644205.2449 | 1226224.3075 | 2644207.691 | 1226223.5807 | 2644215.0682 | 1226223.2686
11 | 2644006.364 | 1226160.8402 | 2644006.9145 | 1226157.1197 | 2644006.7714 | 1226150.8482 | 2643999.7471 | 1226117.3399
12 | 2644215.0682 | 1226223.2686 | 2644226.8552 | 1226222.9454
13 | 2644223.2797 | 1226256.55 | 2644226.137 | 1226254.5367 | 2644230.5948 | 1226252.3573 | 2644253.722 | 1226250.6593
14 | 2644223.2797 | 1226256.55 | 2644244.7705 | 1226275.5435 | 2644252.7407 | 1226282.129 | 2644258.0223 | 1226285.3591 | 2644265.9805 | 1226292.2148
15 | 2644242.9326 | 1226294.3859 | 2644243.9729 | 1226291.0805 | 2644244.5602 | 1226288.5388 | 2644246.2396 | 1226279.8015 | 2644221.1387 | 1226258.0573 | 2644223.2797 | 1226256.55
16 | 2644340.4739 | 1226367.5117 | 2644342.3163 | 1226363.3673 | 2644340.43 | 1226351.0235 | 2644343.9517 | 1226329.014 | 2644344.3524 | 1226314.8972 | 2644348.2308 | 1226313.1694
17 | 2644348.2308 | 1226313.1694 | 2644344.5854 | 1226306.0046 | 2644340.5384 | 1226302.8948 | 2644335.1189 | 1226300.8865 | 2644327.1705 | 1226299.5376 | 2644315.6924 | 1226298.8963 | 2644292.2129 | 1226298.8033
18 | 2644331.3779 | 1226387.9566 | 2644340.4739 | 1226367.5117
19 | 2644265.9805 | 1226292.2148 | 2644270.7802 | 1226296.3496 | 2644274.5953 | 1226298.0345 | 2644280.5777 | 1226298.7572 | 2644292.2129 | 1226298.8033
20 | 2644242.9326 | 1226294.3859 | 2644238.6194 | 1226293.431
21 | 2644242.9326 | 1226294.3859 | 2644243.9729 | 1226291.0805 | 2644253.6064 | 1226300.2577
22 | 2644242.9326 | 1226294.3859 | 2644239.3662 | 1226303.0869 | 2644235.5013 | 1226308.1057 | 2644229.7413 | 1226313.155 | 2644223.4235 | 1226314.7312 | 2644223.4235 | 1226314.7312
23 | 2644238.6194 | 1226293.431 | 2644216.2442 | 1226288.1374
24 | 2644253.6064 | 1226300.2577 | 2644257.0952 | 1226296.8926 | 2644264.8268 | 1226303.8408
25 | 2644202.8686 | 1226311.9683 | 2644215.9021 | 1226315.0756 | 2644223.4235 | 1226314.7312
26 | 2644260.8742 | 1226316.6884 | 2644264.5258 | 1226316.9157 | 2644271.0919 | 1226309.471
27 | 2644271.0919 | 1226309.471 | 2644264.8268 | 1226303.8408
28 | 2644260.8742 | 1226316.6884 | 2644255.2016 | 1226340.5609 | 2644254.0877 | 1226348.6687 | 2644256.368 | 1226349.1661
29 | 2644253.722 | 1226250.6593 | 2644255.6209 | 1226250.5199 | 2644267.6401 | 1226250.7872 | 2644267.6401 | 1226250.7872
30 | 2644316.2 | 1226418.0176 | 2644321.5208 | 1226411.8979 | 2644324.1385 | 1226408.4708 | 2644329.4931 | 1226397.8041 | 2644331.3779 | 1226387.9566
31 | 2643990.959 | 1226073.028 | 2643995.0277 | 1226094.8271 | 2643999.7471 | 1226117.3399
32 | 2644160.9346 | 1226301.9708 | 2644156.6303 | 1226321.2992
33 | 2644160.9346 | 1226301.9708 | 2644153.8981 | 1226300.2954 | 2644162.8364 | 1226275.502
34 | 2644156.6303 | 1226321.2992 | 2644151.2677 | 1226345.3799
35 | 2644162.8364 | 1226275.502 | 2644183.5611 | 1226280.4051
36 | 2644005.3426 | 1226112.4029 | 2644013.8922 | 1226111.4211 | 2644021.0496 | 1226111.1293 | 2644026.6268 | 1226111.3262 | 2644035.2647 | 1226112.1891
37 | 2644061.9681 | 1226127.075 | 2644059.121 | 1226121.5728 | 2644056.0831 | 1226118.2816 | 2644051.6479 | 1226115.3582 | 2644048.0058 | 1226113.8303 | 2644043.3353 | 1226112.9952 | 2644035.2647 | 1226112.1891
38 | 2644183.5611 | 1226280.4051 | 2644216.2442 | 1226288.1374
39 | 2643986.8561 | 1226053.8861 | 2643987.3356 | 1226048.4974 | 2643950.3676 | 1226044.5776 | 2643952.3229 | 1226027.1592 | 2643980.7581 | 1226030.8158 | 2643981.7815 | 1226025.6757
40 | 2643986.8561 | 1226053.8861 | 2643986.9006 | 1226059.1452 | 2643989.1511 | 1226063.3421 | 2643990.959 | 1226073.028
41 | 2643981.7815 | 1226025.6757 | 2643996.8529 | 1226027.3547 | 2643997.687 | 1226027.4416
42 | 2644256.368 | 1226349.1661 | 2644277.7041 | 1226353.8201
43 | 2644284.6123 | 1226252.7923 | 2644267.6401 | 1226250.7872
44 | 2644316.2 | 1226418.0176 | 2644306.9321 | 1226419.8387 | 2644252.4957 | 1226417.0211 | 2644243.4921 | 1226416.4534
45 | 2644148.0368 | 1226359.8885 | 2644151.2677 | 1226345.3799
46 | 2644148.0368 | 1226359.8885 | 2644139.5042 | 1226357.9342
47 | 2644148.0368 | 1226359.8885 | 2644161.4949 | 1226362.9689
48 | 2644061.9681 | 1226127.075 | 2644085.3094 | 1226131.7167
49 | 2643997.687 | 1226027.4416 | 2644025.7873 | 1226030.3674
50 | 2644025.7873 | 1226030.3674 | 2644055.4068 | 1226033.4514
51 | 2644082.0298 | 1226036.2233 | 2644055.4068 | 1226033.4514
52 | 2644082.0298 | 1226036.2233 | 2644082.9993 | 1226036.3195 | 2644085.48 | 1226036.7739
53 | 2644101.6582 | 1226039.7375 | 2644085.48 | 1226036.7739
54 | 2644047.9038 | 1226009.6144 | 2644073.5349 | 1226012.0912
55 | 2644100.4721 | 1226015.6806 | 2644076.264 | 1226012.3549 | 2644073.5349 | 1226012.0912
56 | 2644101.6582 | 1226039.7375 | 2644108.2341 | 1226041.2093 | 2644118.1183 | 1226043.4227
57 | 2644101.6582 | 1226039.7375 | 2644100.4721 | 1226015.6806
58 | 2644100.4721 | 1226015.6806 | 2644100.3562 | 1226013.5565
59 | 2644118.1183 | 1226043.4227 | 2644132.5638 | 1226046.6575
60 | 2644132.5638 | 1226046.6575 | 2644134.0978 | 1226047.001
61 | 2644170.8001 | 1226055.2199 | 2644134.0978 | 1226047.001
62 | 2644172.0063 | 1226055.49 | 2644170.8001 | 1226055.2199
63 | 2644172.0063 | 1226055.49 | 2644192.0025 | 1226059.9678
64 | 2644231.3232 | 1226064.5809 | 2644228.1895 | 1226066.0363 | 2644222.8471 | 1226066.8749 | 2644192.0025 | 1226059.9678
65 | 2644231.3232 | 1226064.5809 | 2644232.4479 | 1226055.3085
66 | 2644235.788 | 1226027.7723 | 2644232.4479 | 1226055.3085
67 | 2644103.2416 | 1226135.2827 | 2644085.3094 | 1226131.7167
68 | 2644243.4631 | 1226416.4516 | 2644243.4921 | 1226416.4534
69 | 2644221.1759 | 1226375.0492 | 2644223.1669 | 1226375.3356
70 | 2644221.1759 | 1226375.0492 | 2644202.6066 | 1226372.3787 | 2644202.239 | 1226372.2946
71 | 2644285.5454 | 1226252.9025 | 2644284.6123 | 1226252.7923
72 | 2644285.5454 | 1226252.9025 | 2644305.217 | 1226255.2265
73 | 2644202.239 | 1226372.2946 | 2644190.4983 | 1226369.6073
74 | 2644190.4983 | 1226369.6073 | 2644183.9713 | 1226368.1134
75 | 2644176.6072 | 1226366.4279 | 2644183.9713 | 1226368.1134
76 | 2644169.4766 | 1226364.7958 | 2644176.6072 | 1226366.4279
77 | 2644162.2208 | 1226363.135 | 2644161.4949 | 1226362.9689
78 | 2644162.2208 | 1226363.135 | 2644169.4766 | 1226364.7958

## bus_geodata
| x | y | coords
0 | 2644099.8413 | 1226068.1939
1 | 2644060.7035 | 1226062.1146
2 | 2644023.3531 | 1226059.6752
3 | 2643991.5105 | 1226059.9797
4 | 2644096.0073 | 1226198.8487
5 | 2644147.3354 | 1226180.5844
6 | 2644184.8979 | 1226233.9624
7 | 2644006.364 | 1226160.8402
8 | 2644215.0682 | 1226223.2686
9 | 2644226.8552 | 1226222.9454
10 | 2644223.2797 | 1226256.55
11 | 2644202.9303 | 1226248.5571
12 | 2644348.2308 | 1226313.1694
13 | 2644340.4739 | 1226367.5117
14 | 2644292.2129 | 1226298.8033
15 | 2644242.9326 | 1226294.3859
16 | 2644238.6194 | 1226293.431
17 | 2644253.6064 | 1226300.2577
18 | 2644223.4235 | 1226314.7312
19 | 2644271.0919 | 1226309.471
20 | 2644260.8742 | 1226316.6884
21 | 2644264.8268 | 1226303.8408
22 | 2644253.722 | 1226250.6593
23 | 2644265.9805 | 1226292.2148
24 | 2644331.3779 | 1226387.9566
25 | 2643999.7471 | 1226117.3399
26 | 2644160.9346 | 1226301.9708
27 | 2644156.6303 | 1226321.2992
28 | 2644162.8364 | 1226275.502
29 | 2644005.3426 | 1226112.4029
30 | 2644035.2647 | 1226112.1891
31 | 2644183.5611 | 1226280.4051
32 | 2643986.8561 | 1226053.8861
33 | 2643981.7815 | 1226025.6757
34 | 2643990.959 | 1226073.028
35 | 2644216.2442 | 1226288.1374
36 | 2644202.8686 | 1226311.9683
37 | 2644256.368 | 1226349.1661
38 | 2644267.6401 | 1226250.7872
39 | 2644316.2 | 1226418.0176
40 | 2644277.7041 | 1226353.8201
41 | 2644151.2677 | 1226345.3799
42 | 2644139.5042 | 1226357.9342
43 | 2644148.0368 | 1226359.8885
44 | 2644061.9681 | 1226127.075
45 | 2643997.687 | 1226027.4416
46 | 2644025.7873 | 1226030.3674
47 | 2644055.4068 | 1226033.4514
48 | 2644082.0298 | 1226036.2233
49 | 2644085.48 | 1226036.7739
50 | 2644047.9038 | 1226009.6144
51 | 2644073.5349 | 1226012.0912
52 | 2644101.6582 | 1226039.7375
53 | 2644100.4721 | 1226015.6806
54 | 2644100.3562 | 1226013.5565
55 | 2644118.1183 | 1226043.4227
56 | 2644132.5638 | 1226046.6575
57 | 2644134.0978 | 1226047.001
58 | 2644170.8001 | 1226055.2199
59 | 2644172.0063 | 1226055.49
60 | 2644192.0025 | 1226059.9678
61 | 2644231.3232 | 1226064.5809
62 | 2644232.4479 | 1226055.3085
63 | 2644235.788 | 1226027.7723
64 | 2644103.2416 | 1226135.2827
65 | 2644085.3094 | 1226131.7167
66 | 2644243.4921 | 1226416.4534
67 | 2644243.4631 | 1226416.4516
68 | 2644223.1669 | 1226375.3356
69 | 2644221.1759 | 1226375.0492
70 | 2644284.6123 | 1226252.7923
71 | 2644285.5454 | 1226252.9025
72 | 2644305.217 | 1226255.2265
73 | 2644202.239 | 1226372.2946
74 | 2644190.4983 | 1226369.6073
75 | 2644183.9713 | 1226368.1134
76 | 2644176.6072 | 1226366.4278
77 | 2644161.4949 | 1226362.9689
78 | 2644162.2208 | 1226363.135
79 | 2644169.4766 | 1226364.7958
80 | 2644179.9268 | 1226231.7797

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97978 | -0.14111 | 0.0016443 | 0.0004121
1 | 0.97987 | -0.14043 | 0.0026213 | 0.00065696
2 | 0.9801 | -0.13877 | 0.0019182 | 0.00048075
3 | 0.98039 | -0.1367 | 0 | 0
4 | 0.99338 | -0.045549 | 0 | 0
5 | 0.99317 | -0.047034 | 0.0021226 | 0.00053197
6 | 1 | 0 | -0.22485 | -0.056561
7 | 0.98725 | -0.088265 | 0 | 0
8 | 0.9995 | -0.0034984 | 0 | 0
9 | 0.99933 | -0.0047064 | 0.010253 | 0.0025696
10 | 0.99591 | -0.028468 | 0 | 0
11 | 0.99957 | -0.0029798 | 0.012827 | 0.0032148
12 | 0.99372 | -0.043925 | 0 | 0
13 | 0.99335 | -0.046523 | 0 | 0
14 | 0.99411 | -0.041133 | 0.0082245 | 0.0020613
15 | 0.99094 | -0.063239 | 0 | 0
16 | 0.99059 | -0.06573 | 0 | 0
17 | 0.99076 | -0.064518 | 0 | 0
18 | 0.99074 | -0.064624 | 0.0015245 | 0.00038206
19 | 0.99052 | -0.06621 | 0 | 0
20 | 0.9904 | -0.067062 | 0 | 0
21 | 0.9906 | -0.065681 | 0.0013231 | 0.00033161
22 | 0.99462 | -0.037529 | 0.01072 | 0.0026868
23 | 0.99462 | -0.037525 | 0.0034414 | 0.0008625
24 | 0.99321 | -0.04753 | 0 | 0
25 | 0.98456 | -0.10724 | 0.0015694 | 0.00039333
26 | 0.98444 | -0.10912 | 0 | 0
27 | 0.98363 | -0.11488 | 0.0033023 | 0.00082764
28 | 0.98582 | -0.099374 | 0 | 0
29 | 0.97798 | -0.15386 | 0 | 0
30 | 0.97671 | -0.16296 | 0.0090157 | 0.0022596
31 | 0.98669 | -0.093205 | 0.013806 | 0.0034602
32 | 0.9808 | -0.13384 | 0 | 0
33 | 0.9782 | -0.15223 | 0 | 0
34 | 0.98185 | -0.12634 | 0.0090622 | 0.0022712
35 | 0.98874 | -0.07876 | 0.013574 | 0.003402
36 | 0.99065 | -0.065269 | 0.0030288 | 0.00075908
37 | 0.99009 | -0.069266 | 0.0022048 | 0.00055257
38 | 0.99427 | -0.040016 | 0.0051733 | 0.0012966
39 | 0.99299 | -0.049077 | 0 | 0
40 | 0.98996 | -0.070148 | 0.0039663 | 0.00099404
41 | 0.98274 | -0.12123 | 0.003406 | 0.00085362
42 | 0.98224 | -0.12481 | 0.0029933 | 0.0007502
43 | 0.98228 | -0.12454 | 0 | 0
44 | 0.97575 | -0.16982 | 0 | 0
45 | 0.97776 | -0.15537 | 0.00042912 | 0.00010755
46 | 0.97699 | -0.16086 | 0.00056128 | 0.00014067
47 | 0.97539 | -0.17228 | 0.0005088 | 0.00012752
48 | 0.97398 | -0.18243 | 0 | 0
49 | 0.97379 | -0.18376 | 0.00047404 | 0.0001188
50 | 0.97266 | -0.1919 | 0.00031597 | 7.9189e-05
51 | 0.97267 | -0.19182 | 0.00045981 | 0.00011524
52 | 0.97293 | -0.18993 | 0 | 0
53 | 0.9727 | -0.1916 | 0 | 0
54 | 0.97268 | -0.19172 | 0.0057675 | 0.0014455
55 | 0.97221 | -0.19511 | 0.0034269 | 0.00085885
56 | 0.97166 | -0.19912 | 0.0058395 | 0.0014635
57 | 0.97161 | -0.19944 | 0.0029464 | 0.00073843
58 | 0.97068 | -0.20615 | 0.0053832 | 0.0013492
59 | 0.97066 | -0.2063 | 0.0039918 | 0.0010004
60 | 0.97044 | -0.20793 | 0.0062629 | 0.0015696
61 | 0.97036 | -0.20845 | 0 | 0
62 | 0.97035 | -0.20857 | 0.00043148 | 0.00010814
63 | 0.97032 | -0.20879 | 0.00077442 | 0.00019409
64 | 0.97469 | -0.17743 | 0.013646 | 0.0034199
65 | 0.97506 | -0.17481 | 0.0063256 | 0.0015854
66 | 0.99252 | -0.052361 | 0.0032347 | 0.0008107
67 | 0.99252 | -0.052361 | 0.0012045 | 0.00030188
68 | 0.98118 | -0.13238 | 0.0016605 | 0.00041617
69 | 0.98118 | -0.13234 | 0.0020447 | 0.00051246
70 | 0.99396 | -0.042177 | 0.0032497 | 0.00081445
71 | 0.99395 | -0.042265 | 0.0067301 | 0.0016867
72 | 0.99388 | -0.042773 | 0.0025384 | 0.00063618
73 | 0.98128 | -0.13161 | 0.0027009 | 0.00067691
74 | 0.9814 | -0.13081 | 0.0033732 | 0.0008454
75 | 0.98149 | -0.13013 | 0.001281 | 0.00032105
76 | 0.98161 | -0.12926 | 0.001201 | 0.00030101
77 | 0.9819 | -0.12718 | 0.0038326 | 0.00096053
78 | 0.98189 | -0.1273 | 0.0012243 | 0.00030684
79 | 0.98174 | -0.12834 | 0.0011934 | 0.00029909
80 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0016443 | -0.0004121 | 0.0016444 | 0.00041166 | 1.5433e-07 | -4.4019e-07 | 0.0024972 | 0.002497 | 0.0024972 | 0.97978 | -0.14111 | 0.97987 | -0.14043 | 0.9249
1 | -0.0042657 | -0.0010686 | 0.0042667 | 0.0010685 | 9.8002e-07 | -9.4668e-08 | 0.0064777 | 0.0064775 | 0.0064777 | 0.97987 | -0.14043 | 0.9801 | -0.13877 | 2.3991
2 | -0.0061849 | -0.0015493 | 0.0061867 | 0.0015495 | 1.7665e-06 | 2.7465e-07 | 0.0093898 | 0.0093896 | 0.0093898 | 0.9801 | -0.13877 | 0.98039 | -0.1367 | 3.4777
3 | -0.035318 | -0.0088677 | 0.035332 | 0.008873 | 1.4066e-05 | 5.3109e-06 | 0.05361 | 0.05361 | 0.05361 | 0.98039 | -0.1367 | 0.9808 | -0.13384 | 19.8555
4 | 0.029131 | 0.0073181 | -0.029061 | -0.0072921 | 6.9375e-05 | 2.5967e-05 | 0.04422 | 0.044221 | 0.044221 | 0.98039 | -0.1367 | 0.97798 | -0.15386 | 16.378
5 | 0.002123 | 0.00053124 | -0.0021226 | -0.00053197 | 4.3556e-07 | -7.2591e-07 | 0.0031798 | 0.0031802 | 0.0031802 | 0.99338 | -0.045549 | 0.99317 | -0.047034 | 1.1778
6 | -0.087032 | -0.022 | 0.087594 | 0.022214 | 0.00056202 | 0.0002134 | 0.13043 | 0.13043 | 0.13043 | 0.99338 | -0.045549 | 1 | 0 | 24.1544
7 | 0.084909 | 0.021469 | -0.084401 | -0.021276 | 0.00050803 | 0.00019281 | 0.12725 | 0.12725 | 0.12725 | 0.99338 | -0.045549 | 0.98725 | -0.088265 | 23.5657
8 | 0.11336 | 0.028559 | -0.11291 | -0.028388 | 0.00044962 | 0.00017161 | 0.16874 | 0.16874 | 0.16874 | 1 | 0 | 0.99591 | -0.028468 | 31.2473
9 | 0.012833 | 0.0032166 | -0.012827 | -0.0032148 | 5.2932e-06 | 1.7308e-06 | 0.019095 | 0.019095 | 0.019095 | 1 | 0 | 0.99957 | -0.0029798 | 7.0724
10 | 0.010259 | 0.0025716 | -0.010254 | -0.0025701 | 4.9682e-06 | 1.4629e-06 | 0.015266 | 0.015267 | 0.015267 | 1 | 0 | 0.9995 | -0.0034984 | 5.6543
11 | 0.084401 | 0.021276 | -0.084177 | -0.021191 | 0.00022368 | 8.4901e-05 | 0.12725 | 0.12726 | 0.12726 | 0.98725 | -0.088265 | 0.98456 | -0.10724 | 23.5658
12 | 0.010254 | 0.0025701 | -0.010253 | -0.0025696 | 1.7149e-06 | 5.0505e-07 | 0.015267 | 0.015267 | 0.015267 | 0.9995 | -0.0034984 | 0.99933 | -0.0047064 | 5.6543
13 | 0.028458 | 0.0071372 | -0.028422 | -0.0071239 | 3.5705e-05 | 1.3321e-05 | 0.042521 | 0.042521 | 0.042521 | 0.99591 | -0.028468 | 0.99462 | -0.037529 | 15.7487
14 | 0.016139 | 0.0040449 | -0.016118 | -0.0040378 | 2.0215e-05 | 7.0509e-06 | 0.024113 | 0.024114 | 0.024114 | 0.99591 | -0.028468 | 0.99462 | -0.037525 | 8.9309
15 | 0.068315 | 0.017206 | -0.067985 | -0.017079 | 0.00033045 | 0.00012644 | 0.1021 | 0.1021 | 0.1021 | 0.99591 | -0.028468 | 0.99094 | -0.063239 | 37.8153
16 | 0.0044444 | 0.0011121 | -0.0044428 | -0.0011123 | 1.5939e-06 | -1.3391e-07 | 0.0066546 | 0.0066549 | 0.0066549 | 0.99372 | -0.043925 | 0.99335 | -0.046523 | 2.4648
17 | -0.0044444 | -0.0011121 | 0.0044461 | 0.001112 | 1.7121e-06 | -1.4452e-07 | 0.0066546 | 0.0066543 | 0.0066546 | 0.99372 | -0.043925 | 0.99411 | -0.041133 | 2.4647
18 | 0.0044428 | 0.0011123 | -0.0044422 | -0.0011123 | 6.1821e-07 | -5.1773e-08 | 0.0066549 | 0.006655 | 0.006655 | 0.99335 | -0.046523 | 0.99321 | -0.04753 | 2.4648
19 | -0.012671 | -0.0031733 | 0.012677 | 0.0031753 | 6.3217e-06 | 2.066e-06 | 0.018965 | 0.018965 | 0.018965 | 0.99411 | -0.041133 | 0.99462 | -0.037525 | 7.0241
20 | 0.05593 | 0.014059 | -0.05591 | -0.014052 | 1.9395e-05 | 7.4029e-06 | 0.084 | 0.084 | 0.084 | 0.99094 | -0.063239 | 0.99059 | -0.06573 | 31.1112
21 | 0.0075003 | 0.0018791 | -0.007499 | -0.0018788 | 1.3274e-06 | 2.9452e-07 | 0.011262 | 0.011262 | 0.011262 | 0.99094 | -0.063239 | 0.99076 | -0.064518 | 4.1713
22 | 0.0045543 | 0.0011409 | -0.0045535 | -0.001141 | 8.7287e-07 | -4.9516e-08 | 0.0068387 | 0.0068389 | 0.0068389 | 0.99094 | -0.063239 | 0.99074 | -0.064624 | 2.5329
23 | 0.05591 | 0.014052 | -0.055809 | -0.014013 | 0.00010124 | 3.8642e-05 | 0.084 | 0.084 | 0.084 | 0.99059 | -0.06573 | 0.98874 | -0.07876 | 31.1112
24 | 0.007499 | 0.0018788 | -0.0074978 | -0.0018786 | 1.2064e-06 | 2.6775e-07 | 0.011262 | 0.011263 | 0.011263 | 0.99076 | -0.064518 | 0.9906 | -0.065681 | 4.1713
25 | 0.003029 | 0.00075891 | -0.0030288 | -0.00075908 | 2.7027e-07 | -1.6553e-07 | 0.0045493 | 0.0045494 | 0.0045494 | 0.99074 | -0.064624 | 0.99065 | -0.065269 | 1.6849
26 | 0.0061742 | 0.0015469 | -0.0061734 | -0.0015468 | 7.2807e-07 | 1.0547e-07 | 0.009275 | 0.0092751 | 0.0092751 | 0.99052 | -0.06621 | 0.9904 | -0.067062 | 3.4352
27 | -0.0061742 | -0.0015469 | 0.0061746 | 0.001547 | 4.5216e-07 | 6.5477e-08 | 0.009275 | 0.009275 | 0.009275 | 0.99052 | -0.06621 | 0.9906 | -0.065681 | 3.4352
28 | 0.0061734 | 0.0015468 | -0.0061715 | -0.0015465 | 1.8818e-06 | 2.7281e-07 | 0.0092751 | 0.0092752 | 0.0092752 | 0.9904 | -0.067062 | 0.99009 | -0.069266 | 3.4353
29 | 0.017702 | 0.0044371 | -0.017696 | -0.004435 | 6.0947e-06 | 2.1634e-06 | 0.026483 | 0.026483 | 0.026483 | 0.99462 | -0.037529 | 0.99427 | -0.040016 | 9.8085
30 | 0.0044422 | 0.0011123 | -0.0044413 | -0.0011124 | 9.5024e-07 | -7.94e-08 | 0.006655 | 0.0066551 | 0.0066551 | 0.99321 | -0.04753 | 0.99299 | -0.049077 | 2.4649
31 | 0.082607 | 0.020798 | -0.082388 | -0.020715 | 0.00021983 | 8.3404e-05 | 0.12488 | 0.12488 | 0.12488 | 0.98456 | -0.10724 | 0.98185 | -0.12634 | 23.1266
32 | 0.028282 | 0.0070954 | -0.028259 | -0.0070869 | 2.2583e-05 | 8.4343e-06 | 0.042751 | 0.042751 | 0.042751 | 0.98444 | -0.10912 | 0.98363 | -0.11488 | 15.8338
33 | -0.028282 | -0.0070954 | 0.02832 | 0.0071097 | 3.8306e-05 | 1.4306e-05 | 0.042751 | 0.042751 | 0.042751 | 0.98444 | -0.10912 | 0.98582 | -0.099374 | 15.8338
34 | 0.024957 | 0.0062593 | -0.024935 | -0.0062512 | 2.1945e-05 | 8.1274e-06 | 0.037756 | 0.037756 | 0.037756 | 0.98363 | -0.11488 | 0.98274 | -0.12123 | 13.9836
35 | -0.02832 | -0.0071097 | 0.028344 | 0.0071187 | 2.4288e-05 | 9.0697e-06 | 0.042751 | 0.042751 | 0.042751 | 0.98582 | -0.099374 | 0.98669 | -0.093205 | 15.8337
36 | 0.029061 | 0.0072921 | -0.029025 | -0.0072784 | 3.6644e-05 | 1.3717e-05 | 0.044221 | 0.044221 | 0.044221 | 0.97798 | -0.15386 | 0.97671 | -0.16296 | 16.378
37 | 0.020009 | 0.0050189 | -0.01999 | -0.005012 | 1.9016e-05 | 6.9039e-06 | 0.030485 | 0.030485 | 0.030485 | 0.97671 | -0.16296 | 0.97575 | -0.16982 | 11.2909
38 | -0.042151 | -0.010579 | 0.042235 | 0.010611 | 8.4697e-05 | 3.2146e-05 | 0.063572 | 0.063572 | 0.063572 | 0.98669 | -0.093205 | 0.98874 | -0.07876 | 23.5452
39 | 0.037917 | 0.0095415 | -0.03782 | -0.0095065 | 9.7126e-05 | 3.4989e-05 | 0.05754 | 0.057541 | 0.057541 | 0.9808 | -0.13384 | 0.9782 | -0.15223 | 10.6557
40 | -0.073249 | -0.018414 | 0.073325 | 0.018443 | 7.6608e-05 | 2.8962e-05 | 0.11115 | 0.11115 | 0.11115 | 0.9808 | -0.13384 | 0.98185 | -0.12634 | 20.5833
41 | 0.03782 | 0.0095065 | -0.037804 | -0.0095006 | 1.6532e-05 | 5.9567e-06 | 0.057541 | 0.057541 | 0.057541 | 0.9782 | -0.15223 | 0.97776 | -0.15537 | 10.6557
42 | 0.0039668 | 0.00099395 | -0.0039663 | -0.00099404 | 4.8432e-07 | -9.4535e-08 | 0.0059616 | 0.0059617 | 0.0059617 | 0.99009 | -0.069266 | 0.98996 | -0.070148 | 2.208
43 | 0.012522 | 0.0031384 | -0.012518 | -0.0031372 | 3.7455e-06 | 1.219e-06 | 0.018741 | 0.018741 | 0.018741 | 0.99427 | -0.040016 | 0.99396 | -0.042177 | 6.941
44 | 0.0044413 | 0.0011124 | -0.0044393 | -0.0011126 | 2.017e-06 | -1.6781e-07 | 0.0066551 | 0.0066555 | 0.0066555 | 0.99299 | -0.049077 | 0.99252 | -0.052361 | 2.465
45 | 0.021529 | 0.0053975 | -0.021519 | -0.0053939 | 9.8564e-06 | 3.6027e-06 | 0.032599 | 0.032599 | 0.032599 | 0.98274 | -0.12123 | 0.98228 | -0.12454 | 12.0735
46 | -0.0029933 | -0.0007502 | 0.0029934 | 0.00075013 | 1.1232e-07 | -6.7601e-08 | 0.0045347 | 0.0045346 | 0.0045347 | 0.98224 | -0.12481 | 0.98228 | -0.12454 | 1.6795
47 | 0.018525 | 0.0046438 | -0.018519 | -0.0046414 | 6.7851e-06 | 2.435e-06 | 0.028064 | 0.028064 | 0.028064 | 0.98228 | -0.12454 | 0.9819 | -0.12718 | 10.3941
48 | 0.01999 | 0.005012 | -0.019976 | -0.005007 | 1.3801e-05 | 5.0111e-06 | 0.030485 | 0.030485 | 0.030485 | 0.97575 | -0.16982 | 0.97506 | -0.17481 | 11.2909
49 | 0.037374 | 0.009393 | -0.037346 | -0.0093828 | 2.8527e-05 | 1.0264e-05 | 0.056888 | 0.056888 | 0.056888 | 0.97776 | -0.15537 | 0.97699 | -0.16086 | 10.5349
50 | 0.036785 | 0.0092421 | -0.036726 | -0.00922 | 5.8344e-05 | 2.2068e-05 | 0.056033 | 0.056033 | 0.056033 | 0.97699 | -0.16086 | 0.97539 | -0.17228 | 20.7531
51 | 0.036217 | 0.0090925 | -0.036166 | -0.0090732 | 5.0999e-05 | 1.9281e-05 | 0.055257 | 0.055257 | 0.055257 | 0.97539 | -0.17228 | 0.97398 | -0.18243 | 20.4657
52 | 0.036166 | 0.0090732 | -0.03616 | -0.0090707 | 6.6614e-06 | 2.5186e-06 | 0.055257 | 0.055257 | 0.055257 | 0.97398 | -0.18243 | 0.97379 | -0.18376 | 20.4657
53 | 0.035686 | 0.0089519 | -0.035655 | -0.0089404 | 3.0521e-05 | 1.1535e-05 | 0.054533 | 0.054533 | 0.054533 | 0.97379 | -0.18376 | 0.97293 | -0.18993 | 20.1975
54 | -0.00031597 | -7.9189e-05 | 0.00031597 | 7.8871e-05 | 3.7536e-09 | -3.1817e-07 | 0.00048338 | 0.00048327 | 0.00048338 | 0.97266 | -0.1919 | 0.97267 | -0.19182 | 0.17903
55 | -0.00077579 | -0.00019411 | 0.00077581 | 0.00019378 | 2.388e-08 | -3.2815e-07 | 0.0011867 | 0.0011866 | 0.0011867 | 0.97267 | -0.19182 | 0.9727 | -0.1916 | 0.43952
56 | 0.02911 | 0.0073008 | -0.029089 | -0.007293 | 2.0865e-05 | 7.8157e-06 | 0.044524 | 0.044524 | 0.044524 | 0.97293 | -0.18993 | 0.97221 | -0.19511 | 16.4902
57 | 0.0065449 | 0.0016395 | -0.0065434 | -0.0016393 | 1.5061e-06 | 2.8018e-07 | 0.01001 | 0.01001 | 0.01001 | 0.97293 | -0.18993 | 0.9727 | -0.1916 | 3.7073
58 | 0.0057676 | 0.0014455 | -0.0057675 | -0.0014455 | 1.0334e-07 | 1.334e-08 | 0.0088231 | 0.0088231 | 0.0088231 | 0.9727 | -0.1916 | 0.97268 | -0.19172 | 3.2678
59 | 0.025663 | 0.0064342 | -0.025648 | -0.0064289 | 1.4251e-05 | 5.2978e-06 | 0.039279 | 0.039279 | 0.039279 | 0.97221 | -0.19511 | 0.97166 | -0.19912 | 14.5477
60 | 0.019809 | 0.0049654 | -0.019808 | -0.004965 | 9.027e-07 | 3.2772e-07 | 0.030336 | 0.030336 | 0.030336 | 0.97166 | -0.19912 | 0.97161 | -0.19944 | 11.2356
61 | 0.016862 | 0.0042266 | -0.016846 | -0.004221 | 1.5651e-05 | 5.5542e-06 | 0.025824 | 0.025824 | 0.025824 | 0.97161 | -0.19944 | 0.97068 | -0.20615 | 9.5644
62 | 0.011463 | 0.0028719 | -0.011462 | -0.0028718 | 2.3814e-07 | 7.6314e-08 | 0.017572 | 0.017572 | 0.017572 | 0.97068 | -0.20615 | 0.97066 | -0.2063 | 6.508
63 | 0.0074706 | 0.0018714 | -0.007469 | -0.001871 | 1.677e-06 | 3.9177e-07 | 0.011452 | 0.011452 | 0.011452 | 0.97066 | -0.2063 | 0.97044 | -0.20793 | 4.2416
64 | 0.001206 | 0.00030132 | -0.0012059 | -0.00030179 | 8.6341e-08 | -4.6678e-07 | 0.0018489 | 0.0018491 | 0.0018491 | 0.97044 | -0.20793 | 0.97036 | -0.20845 | 0.68486
65 | 0.0012059 | 0.00030179 | -0.0012059 | -0.00030189 | 1.9929e-08 | -1.0772e-07 | 0.0018491 | 0.0018492 | 0.0018492 | 0.97036 | -0.20845 | 0.97035 | -0.20857 | 0.68487
66 | 0.00077445 | 0.00019376 | -0.00077442 | -0.00019409 | 2.4409e-08 | -3.3324e-07 | 0.0011875 | 0.0011876 | 0.0011876 | 0.97035 | -0.20857 | 0.97032 | -0.20879 | 0.43985
67 | -0.013646 | -0.0034199 | 0.013651 | 0.0034216 | 4.9512e-06 | 1.6763e-06 | 0.020832 | 0.020832 | 0.020832 | 0.97469 | -0.17743 | 0.97506 | -0.17481 | 7.7156
68 | 0.0012045 | 0.00030188 | -0.0012045 | -0.00030188 | 5.8858e-11 | -3.5455e-10 | 0.0018059 | 0.0018059 | 0.0018059 | 0.99252 | -0.052361 | 0.99252 | -0.052361 | 0.66883
69 | -0.0016605 | -0.00041617 | 0.0016605 | 0.00041614 | 7.9598e-09 | -2.2344e-08 | 0.0025183 | 0.0025183 | 0.0025183 | 0.98118 | -0.13238 | 0.98118 | -0.13234 | 0.9327
70 | -0.0037052 | -0.0009286 | 0.0037056 | 0.0009285 | 3.7706e-07 | -9.6711e-08 | 0.0056192 | 0.0056191 | 0.0056192 | 0.98118 | -0.13234 | 0.98128 | -0.13161 | 2.0812
71 | 0.0092687 | 0.0023227 | -0.0092686 | -0.0023227 | 1.1288e-07 | 3.1238e-08 | 0.013876 | 0.013876 | 0.013876 | 0.99396 | -0.042177 | 0.99395 | -0.042265 | 5.1392
72 | 0.0025386 | 0.00063599 | -0.0025384 | -0.00063618 | 1.7852e-07 | -1.8806e-07 | 0.0038004 | 0.0038004 | 0.0038004 | 0.99395 | -0.042265 | 0.99388 | -0.042773 | 1.4076
73 | -0.0064065 | -0.0016054 | 0.0064072 | 0.0016055 | 7.093e-07 | 1.2064e-07 | 0.0097148 | 0.0097147 | 0.0097148 | 0.98128 | -0.13161 | 0.9814 | -0.13081 | 3.5981
74 | -0.0097804 | -0.0024509 | 0.0097814 | 0.0024512 | 9.1879e-07 | 2.6877e-07 | 0.014829 | 0.014829 | 0.014829 | 0.9814 | -0.13081 | 0.98149 | -0.13013 | 5.4923
75 | -0.011062 | -0.0027723 | 0.011064 | 0.0027727 | 1.326e-06 | 4.145e-07 | 0.016771 | 0.016771 | 0.016771 | 0.98149 | -0.13013 | 0.98161 | -0.12926 | 6.2116
76 | -0.012265 | -0.0030737 | 0.012266 | 0.0030742 | 1.5778e-06 | 5.1435e-07 | 0.018592 | 0.018592 | 0.018592 | 0.98161 | -0.12926 | 0.98174 | -0.12834 | 6.8859
77 | 0.014686 | 0.0036808 | -0.014686 | -0.0036808 | 2.3017e-07 | 7.9107e-08 | 0.022256 | 0.022256 | 0.022256 | 0.9819 | -0.12718 | 0.98189 | -0.1273 | 8.243
78 | 0.013462 | 0.0033739 | -0.01346 | -0.0033733 | 1.933e-06 | 6.4935e-07 | 0.020401 | 0.020401 | 0.020401 | 0.98189 | -0.1273 | 0.98174 | -0.12834 | 7.5558

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.22485 | 0.056561

## res_load
| p_mw | q_mvar
0 | 0.0016443 | 0.0004121
1 | 0.0026213 | 0.00065696
2 | 0.0019182 | 0.00048075
3 | 0.0021226 | 0.00053197
4 | 0.010253 | 0.0025696
5 | 0.012827 | 0.0032148
6 | 0.0082245 | 0.0020613
7 | 0.0015245 | 0.00038206
8 | 0.0013231 | 0.00033161
9 | 0.01072 | 0.0026868
10 | 0.0034414 | 0.0008625
11 | 0.0015694 | 0.00039333
12 | 0.0033023 | 0.00082764
13 | 0.0090157 | 0.0022596
14 | 0.013806 | 0.0034602
15 | 0.0090622 | 0.0022712
16 | 0.013574 | 0.003402
17 | 0.0030288 | 0.00075908
18 | 0.0022048 | 0.00055257
19 | 0.0051733 | 0.0012966
20 | 0.0039663 | 0.00099404
21 | 0.003406 | 0.00085362
22 | 0.0029933 | 0.0007502
23 | 0.00042912 | 0.00010755
24 | 0.00056128 | 0.00014067
25 | 0.0005088 | 0.00012752
26 | 0.00047404 | 0.0001188
27 | 0.00031597 | 7.9189e-05
28 | 0.00045981 | 0.00011524
29 | 0.0057675 | 0.0014455
30 | 0.0034269 | 0.00085885
31 | 0.0058395 | 0.0014635
32 | 0.0029464 | 0.00073843
33 | 0.0053832 | 0.0013492
34 | 0.0039918 | 0.0010004
35 | 0.0062629 | 0.0015696
36 | 0.00043148 | 0.00010814
37 | 0.00077442 | 0.00019409
38 | 0.013646 | 0.0034199
39 | 0.0063256 | 0.0015854
40 | 0.0032347 | 0.0008107
41 | 0.0012045 | 0.00030188
42 | 0.0016605 | 0.00041617
43 | 0.0020447 | 0.00051246
44 | 0.0032497 | 0.00081445
45 | 0.0067301 | 0.0016867
46 | 0.0025384 | 0.00063618
47 | 0.0027009 | 0.00067691
48 | 0.0033732 | 0.0008454
49 | 0.001281 | 0.00032105
50 | 0.001201 | 0.00030101
51 | 0.0038326 | 0.00096053
52 | 0.0012243 | 0.00030684
53 | 0.0011934 | 0.00029909

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1