## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1146-5_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1146-5_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1146-5_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1146-5_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1146-5_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1146-5_0_3_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1146-5_0_3_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1146-5_0_3_node_21 | 0.4 | n |  | TRUE
8 | bus_LV_1146-5_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1146-5_0_3_node_23 | 0.4 | n |  | TRUE
10 | bus_LV_1146-5_0_3_node_22 | 0.4 | n |  | TRUE
11 | bus_LV_1146-5_0_3_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_1146-5_0_3_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_1146-5_0_3_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1146-5_0_3_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1146-5_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1146-5_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1146-5_0_3_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1146-5_0_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_1146-5_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1146-5_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1146-5_0_3_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1146-5_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1146-5_0_3_node_29 | 0.4 | n |  | TRUE
24 | bus_LV_1146-5_0_3_node_32 | 0.4 | n |  | TRUE
25 | bus_LV_1146-5_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1146-5_0_3_node_31 | 0.4 | n |  | TRUE
27 | bus_LV_1146-5_0_3_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_1146-5_0_3_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_1146-5_0_3_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1146-5_0_3_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_1146-5_0_3_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_1146-5_0_3_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_1146-5_0_3_node_30 | 0.4 | n |  | TRUE
34 | bus_MV_131_0_node_88 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1146-5_0_3_load_0 | 0 | 0.0027155 | 0.00068057 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1146-5_0_3_load_1 | 1 | 0.0028236 | 0.00070765 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1146-5_0_3_load_2 | 2 | 0.0058168 | 0.0014578 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1146-5_0_3_load_4 | 4 | 0.0046845 | 0.001174 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1146-5_0_3_load_21 | 7 | 0.0021322 | 0.00053437 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1146-5_0_3_load_23 | 9 | 0.0082097 | 0.0020576 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1146-5_0_3_load_22 | 10 | 0.0023002 | 0.00057649 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1146-5_0_3_load_5 | 11 | 0.016776 | 0.0042044 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1146-5_0_3_load_7 | 12 | 0.0040335 | 0.0010109 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1146-5_0_3_load_6 | 13 | 0.040913 | 0.010254 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1146-5_0_3_load_9 | 14 | 0.0042997 | 0.0010776 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1146-5_0_3_load_19 | 17 | 0.0016858 | 0.00042251 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1146-5_0_3_load_17 | 18 | 0.0038545 | 0.00096602 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1146-5_0_3_load_24 | 19 | 0.0082579 | 0.0020696 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1146-5_0_3_load_20 | 21 | 0.0036195 | 0.00090712 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1146-5_0_3_load_32 | 24 | 0.0023373 | 0.00058578 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1146-5_0_3_load_18 | 25 | 0.0032085 | 0.00080413 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1146-5_0_3_load_31 | 26 | 0.0037508 | 0.00094003 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1146-5_0_3_load_27 | 27 | 0.0072327 | 0.0018127 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1146-5_0_3_load_33 | 28 | 0.0012692 | 0.00031808 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1146-5_0_3_load_16 | 29 | 0.011718 | 0.0029368 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1146-5_0_3_load_25 | 30 | 0.0073798 | 0.0018495 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1146-5_0_3_load_26 | 31 | 0.0015455 | 0.00038735 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1146-5_0_3_load_28 | 32 | 0.0059126 | 0.0014818 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1146-5_0_3_load_30 | 33 | 0.0025494 | 0.00063894 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 7 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1146-5_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.018241 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1146-5_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.019734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1146-5_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.010461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1146-5_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.023195 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1146-5_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.041525 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1146-5_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.010434 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1146-5_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.046479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1146-5_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.015929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1146-5_0_3_line_8 | NAYY 4x150 SE | 6 | 9 | 0.018143 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1146-5_0_3_line_9 | NAYY 4x150 SE | 6 | 10 | 0.0022374 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1146-5_0_3_line_10 | NAYY 4x150 SE | 8 | 13 | 0.052315 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1146-5_0_3_line_11 | NAYY 4x150 SE | 9 | 19 | 0.026919 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1146-5_0_3_line_12 | NAYY 4x150 SE | 11 | 12 | 0.053559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1146-5_0_3_line_13 | NAYY 4x150 SE | 12 | 14 | 0.034151 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1146-5_0_3_line_14 | NAYY 4x150 SE | 14 | 15 | 0.068217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1146-5_0_3_line_15 | NAYY 4x150 SE | 15 | 16 | 0.005589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1146-5_0_3_line_16 | NAYY 4x150 SE | 16 | 20 | 0.010534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1146-5_0_3_line_17 | NAYY 4x150 SE | 16 | 21 | 0.057869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1146-5_0_3_line_18 | NAYY 4x150 SE | 17 | 18 | 0.034629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1146-5_0_3_line_19 | NAYY 4x150 SE | 18 | 29 | 0.043006 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1146-5_0_3_line_20 | NAYY 4x150 SE | 19 | 30 | 0.0402 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1146-5_0_3_line_21 | NAYY 4x150 SE | 20 | 22 | 0.10858 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
22 | LV_1146-5_0_3_line_22 | NAYY 4x150 SE | 21 | 25 | 0.037293 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1146-5_0_3_line_23 | NAYY 4x150 SE | 22 | 23 | 0.025835 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1146-5_0_3_line_24 | NAYY 4x150 SE | 22 | 24 | 0.063539 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
25 | LV_1146-5_0_3_line_25 | NAYY 4x150 SE | 23 | 26 | 0.038921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1146-5_0_3_line_26 | NAYY 4x150 SE | 23 | 27 | 0.028272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1146-5_0_3_line_27 | NAYY 4x150 SE | 24 | 28 | 0.021712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1146-5_0_3_line_28 | NAYY 4x150 SE | 25 | 29 | 0.036812 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1146-5_0_3_line_29 | NAYY 4x150 SE | 27 | 32 | 0.029798 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1146-5_0_3_line_30 | NAYY 4x150 SE | 28 | 31 | 0.020366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
31 | LV_1146-5_0_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.028496 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1146-5_0_3_line_32 | NAYY 4x150 SE | 32 | 33 | 0.036802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1146-5_0_3_trafo_21 | 0.25 MVA 20/0.4 kV | 34 | 7 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2643847.8818 | 1226147.656 | 2643866.0167 | 1226149.6172
1 | 2643847.8818 | 1226147.656 | 2643828.262 | 1226145.5343
2 | 2643876.4172 | 1226150.7419 | 2643866.0167 | 1226149.6172
3 | 2643805.2015 | 1226143.0405 | 2643828.262 | 1226145.5343
4 | 2643876.4172 | 1226150.7419 | 2643878.9183 | 1226130.2144 | 2643881.1706 | 1226109.4961
5 | 2643876.4172 | 1226150.7419 | 2643878.9317 | 1226151.0162 | 2643878.4993 | 1226155.1711 | 2643877.9567 | 1226158.8582
6 | 2643805.2015 | 1226143.0405 | 2643758.9917 | 1226138.0432
7 | 2643870.5985 | 1226101.0464 | 2643881.6247 | 1226105.4748 | 2643881.1706 | 1226109.4961
8 | 2643877.9567 | 1226158.8582 | 2643859.9084 | 1226157.0102
9 | 2643877.9567 | 1226158.8582 | 2643880.1788 | 1226159.1195
10 | 2643870.5985 | 1226101.0464 | 2643865.8215 | 1226101.2891 | 2643819.0953 | 1226092.5767
11 | 2643859.9084 | 1226157.0102 | 2643833.1299 | 1226154.2684
12 | 2643696.2293 | 1226081.1272 | 2643642.703 | 1226079.2566
13 | 2643642.703 | 1226079.2566 | 2643608.5724 | 1226078.0638
14 | 2643551.055 | 1226100.7566 | 2643551.855 | 1226097.0824 | 2643554.3029 | 1226091.9527 | 2643557.0483 | 1226088.6375 | 2643566.164 | 1226081.7555 | 2643582.8048 | 1226077.1633 | 2643608.5724 | 1226078.0638
15 | 2643551.055 | 1226100.7566 | 2643556.5419 | 1226101.8974
16 | 2643564.2542 | 1226108.6469 | 2643559.3256 | 1226105.7757 | 2643556.7556 | 1226102.744 | 2643556.5419 | 1226101.8974
17 | 2643556.5419 | 1226101.8974 | 2643556.0339 | 1226099.848 | 2643556.7296 | 1226096.9624 | 2643559.2294 | 1226093.0339 | 2643565.4404 | 1226087.4203 | 2643570.3421 | 1226084.6322 | 2643579.9859 | 1226082.2347 | 2643589.0022 | 1226081.6892 | 2643604.149 | 1226082.088
18 | 2643721.2045 | 1226085.5338 | 2643730.4309 | 1226086.0508 | 2643755.6879 | 1226088.6322
19 | 2643721.2045 | 1226085.5338 | 2643708.9663 | 1226084.8481 | 2643678.2286 | 1226084.0387
20 | 2643833.1299 | 1226154.2684 | 2643793.1387 | 1226150.1736
21 | 2643564.2542 | 1226108.6469 | 2643563.1724 | 1226114.5759 | 2643607.3965 | 1226123.316 | 2643660.3947 | 1226131.4426 | 2643659.8664 | 1226135.2633
22 | 2643641.4294 | 1226083.0697 | 2643604.149 | 1226082.088
23 | 2643656.3437 | 1226160.8531 | 2643659.682 | 1226136.6294 | 2643659.8664 | 1226135.2633
24 | 2643659.8664 | 1226135.2633 | 2643674.4123 | 1226137.26 | 2643723.0055 | 1226142.3287
25 | 2643656.3437 | 1226160.8531 | 2643651.1741 | 1226169.1537 | 2643643.5033 | 1226175.3901 | 2643635.3062 | 1226177.9316 | 2643624.6711 | 1226177.0236
26 | 2643656.3437 | 1226160.8531 | 2643684.2987 | 1226165.0716
27 | 2643723.0055 | 1226142.3287 | 2643744.6005 | 1226144.5813
28 | 2643641.4294 | 1226083.0697 | 2643678.2286 | 1226084.0387
29 | 2643684.2987 | 1226165.0716 | 2643687.5524 | 1226165.5626 | 2643701.2447 | 1226168.1758 | 2643704.0797 | 1226170.2201 | 2643706.2628 | 1226174.3164 | 2643708.0486 | 1226178.3719
30 | 2643744.6005 | 1226144.5813 | 2643756.9674 | 1226145.8713 | 2643764.8394 | 1226146.8416
31 | 2643764.8394 | 1226146.8416 | 2643785.6456 | 1226149.4064 | 2643793.1387 | 1226150.1736
32 | 2643737.268 | 1226196.3573 | 2643722.2091 | 1226193.056 | 2643715.5024 | 1226189.7937 | 2643711.4592 | 1226186.1173 | 2643708.0486 | 1226178.3719

## bus_geodata
| x | y | coords
0 | 2643847.8818 | 1226147.656
1 | 2643866.0167 | 1226149.6172
2 | 2643828.262 | 1226145.5343
3 | 2643876.4172 | 1226150.7419
4 | 2643805.2015 | 1226143.0405
5 | 2643881.1706 | 1226109.4961
6 | 2643877.9567 | 1226158.8582
7 | 2643758.9917 | 1226138.0432
8 | 2643870.5985 | 1226101.0464
9 | 2643859.9084 | 1226157.0102
10 | 2643880.1788 | 1226159.1195
11 | 2643696.2293 | 1226081.1272
12 | 2643642.703 | 1226079.2566
13 | 2643819.0953 | 1226092.5767
14 | 2643608.5724 | 1226078.0638
15 | 2643551.055 | 1226100.7566
16 | 2643556.5419 | 1226101.8974
17 | 2643755.6879 | 1226088.6322
18 | 2643721.2045 | 1226085.5338
19 | 2643833.1299 | 1226154.2684
20 | 2643564.2542 | 1226108.6469
21 | 2643604.149 | 1226082.088
22 | 2643659.8664 | 1226135.2633
23 | 2643656.3437 | 1226160.8531
24 | 2643723.0055 | 1226142.3287
25 | 2643641.4294 | 1226083.0697
26 | 2643624.6711 | 1226177.0236
27 | 2643684.2987 | 1226165.0716
28 | 2643744.6005 | 1226144.5813
29 | 2643678.2286 | 1226084.0387
30 | 2643793.1387 | 1226150.1736
31 | 2643764.8394 | 1226146.8416
32 | 2643708.0486 | 1226178.3719
33 | 2643737.268 | 1226196.3573
34 | 2643876.4172 | 1226150.7419

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99337 | -0.045971 | 0.0027155 | 0.00068057
1 | 0.9921 | -0.054827 | 0.0028236 | 0.00070765
2 | 0.99477 | -0.036234 | 0.0058168 | 0.0014578
3 | 0.99138 | -0.059816 | 0 | 0
4 | 0.99647 | -0.024373 | 0.0046845 | 0.001174
5 | 0.98893 | -0.077114 | 0 | 0
6 | 0.99088 | -0.063352 | 0 | 0
7 | 1 | 0 | -0.16038 | -0.040332
8 | 0.98798 | -0.083772 | 0 | 0
9 | 0.99002 | -0.069368 | 0.0082097 | 0.0020576
10 | 0.99087 | -0.063405 | 0.0023002 | 0.00057649
11 | 0.97291 | -0.19071 | 0.016776 | 0.0042044
12 | 0.97423 | -0.18125 | 0.0040335 | 0.0010109
13 | 0.98489 | -0.10573 | 0.040913 | 0.010254
14 | 0.97527 | -0.17378 | 0.0042997 | 0.0010776
15 | 0.97778 | -0.15585 | 0 | 0
16 | 0.97798 | -0.15438 | 0 | 0
17 | 0.97346 | -0.18679 | 0.0016858 | 0.00042251
18 | 0.97355 | -0.18617 | 0.0038545 | 0.00096602
19 | 0.98885 | -0.07756 | 0.0082579 | 0.0020696
20 | 0.97874 | -0.14897 | 0 | 0
21 | 0.97595 | -0.16897 | 0.0036195 | 0.00090712
22 | 0.98265 | -0.12123 | 0 | 0
23 | 0.98192 | -0.12643 | 0 | 0
24 | 0.98478 | -0.10622 | 0.0023373 | 0.00058578
25 | 0.97483 | -0.17698 | 0.0032085 | 0.00080413
26 | 0.98171 | -0.12795 | 0.0037508 | 0.00094003
27 | 0.98128 | -0.13103 | 0.0072327 | 0.0018127
28 | 0.98553 | -0.10093 | 0.0012692 | 0.00031808
29 | 0.9739 | -0.18366 | 0.011718 | 0.0029368
30 | 0.98726 | -0.088695 | 0.0073798 | 0.0018495
31 | 0.98624 | -0.09589 | 0.0015455 | 0.00038735
32 | 0.98091 | -0.13365 | 0.0059126 | 0.0014818
33 | 0.98078 | -0.13462 | 0.0025494 | 0.00063894
34 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.14536 | 0.036637 | -0.14518 | -0.036568 | 0.00018001 | 6.8528e-05 | 0.21782 | 0.21782 | 0.21782 | 0.99337 | -0.045971 | 0.9921 | -0.054827 | 26.8914
1 | -0.14808 | -0.037317 | 0.14828 | 0.037394 | 0.00020209 | 7.696e-05 | 0.22189 | 0.22189 | 0.22189 | 0.99337 | -0.045971 | 0.99477 | -0.036234 | 27.3936
2 | 0.14236 | 0.035861 | -0.14226 | -0.035823 | 9.9263e-05 | 3.7773e-05 | 0.21359 | 0.21359 | 0.21359 | 0.9921 | -0.054827 | 0.99138 | -0.059816 | 26.3686
3 | -0.1541 | -0.038852 | 0.15435 | 0.03895 | 0.00025653 | 9.7759e-05 | 0.23059 | 0.23059 | 0.23059 | 0.99477 | -0.036234 | 0.99647 | -0.024373 | 28.4677
4 | 0.041174 | 0.010353 | -0.041075 | -0.010315 | 9.9003e-05 | 3.7544e-05 | 0.061813 | 0.061813 | 0.061813 | 0.99138 | -0.059816 | 0.98893 | -0.077114 | 22.8936
5 | 0.10109 | 0.02547 | -0.10104 | -0.025451 | 4.999e-05 | 1.8824e-05 | 0.15177 | 0.15177 | 0.15177 | 0.99138 | -0.059816 | 0.99088 | -0.063352 | 18.7374
6 | -0.15904 | -0.040124 | 0.15958 | 0.040332 | 0.0005457 | 0.00020806 | 0.23758 | 0.23758 | 0.23758 | 0.99647 | -0.024373 | 1 | 0 | 29.3313
7 | 0.041075 | 0.010315 | -0.041037 | -0.010301 | 3.7978e-05 | 1.4403e-05 | 0.061813 | 0.061813 | 0.061813 | 0.98893 | -0.077114 | 0.98798 | -0.083772 | 22.8936
8 | 0.098736 | 0.024874 | -0.098653 | -0.024843 | 8.3015e-05 | 3.1228e-05 | 0.14832 | 0.14832 | 0.14832 | 0.99088 | -0.063352 | 0.99002 | -0.069368 | 18.311
9 | 0.0023002 | 0.00057647 | -0.0023002 | -0.00057649 | 1.6659e-08 | -2.2413e-08 | 0.0034543 | 0.0034543 | 0.0034543 | 0.99088 | -0.063352 | 0.99087 | -0.063405 | 1.2794
10 | 0.041037 | 0.010301 | -0.040913 | -0.010254 | 0.00012473 | 4.7305e-05 | 0.061813 | 0.061813 | 0.061813 | 0.98798 | -0.083772 | 0.98489 | -0.10573 | 22.8937
11 | 0.090443 | 0.022786 | -0.09034 | -0.022747 | 0.00010353 | 3.8782e-05 | 0.13598 | 0.13598 | 0.13598 | 0.99002 | -0.069368 | 0.98885 | -0.07756 | 16.7877
12 | -0.016776 | -0.0042044 | 0.016798 | 0.0042122 | 2.2001e-05 | 7.796e-06 | 0.025658 | 0.025657 | 0.025658 | 0.97291 | -0.19071 | 0.97423 | -0.18125 | 9.5029
13 | -0.020831 | -0.0052231 | 0.020853 | 0.005231 | 2.1575e-05 | 7.8722e-06 | 0.031818 | 0.031818 | 0.031818 | 0.97423 | -0.18125 | 0.97527 | -0.17378 | 11.7845
14 | -0.025153 | -0.0063086 | 0.025215 | 0.0063319 | 6.2696e-05 | 2.326e-05 | 0.038378 | 0.038378 | 0.038378 | 0.97527 | -0.17378 | 0.97778 | -0.15585 | 14.2142
15 | -0.025215 | -0.0063319 | 0.02522 | 0.0063338 | 5.1367e-06 | 1.9055e-06 | 0.038378 | 0.038378 | 0.038378 | 0.97778 | -0.15585 | 0.97798 | -0.15438 | 14.2141
16 | -0.049396 | -0.012402 | 0.049434 | 0.012416 | 3.7137e-05 | 1.4151e-05 | 0.075165 | 0.075165 | 0.075165 | 0.97798 | -0.15438 | 0.97874 | -0.14897 | 27.839
17 | 0.024176 | 0.0060685 | -0.024127 | -0.0060504 | 4.8869e-05 | 1.8071e-05 | 0.036787 | 0.036788 | 0.036788 | 0.97798 | -0.15438 | 0.97595 | -0.16897 | 13.625
18 | -0.0016858 | -0.00042251 | 0.001686 | 0.00042213 | 1.4348e-07 | -3.7538e-07 | 0.0025769 | 0.0025767 | 0.0025769 | 0.97346 | -0.18679 | 0.97355 | -0.18617 | 0.95441
19 | -0.0055404 | -0.0013882 | 0.0055424 | 0.0013884 | 1.9243e-06 | 2.0517e-07 | 0.0084681 | 0.0084679 | 0.0084681 | 0.97355 | -0.18617 | 0.9739 | -0.18366 | 3.1363
20 | 0.082082 | 0.020677 | -0.081954 | -0.02063 | 0.00012765 | 4.755e-05 | 0.12355 | 0.12355 | 0.12355 | 0.98885 | -0.07756 | 0.98726 | -0.088695 | 15.2536
21 | -0.049434 | -0.012416 | 0.049625 | 0.012487 | 0.0001914 | 7.0874e-05 | 0.075165 | 0.075164 | 0.075165 | 0.97874 | -0.14897 | 0.98265 | -0.12123 | 13.9195
22 | 0.020508 | 0.0051433 | -0.020485 | -0.005135 | 2.2753e-05 | 8.2858e-06 | 0.031269 | 0.031269 | 0.031269 | 0.97595 | -0.16897 | 0.97483 | -0.17698 | 11.5812
23 | 0.019474 | 0.0048823 | -0.01946 | -0.0048773 | 1.4019e-05 | 5.065e-06 | 0.029489 | 0.029489 | 0.029489 | 0.98265 | -0.12123 | 0.98192 | -0.12643 | 10.922
24 | -0.069099 | -0.01737 | 0.069243 | 0.017423 | 0.00014475 | 5.3252e-05 | 0.10465 | 0.10465 | 0.10465 | 0.98265 | -0.12123 | 0.98478 | -0.10622 | 12.9202
25 | 0.0037515 | 0.00093984 | -0.0037508 | -0.00094003 | 7.8494e-07 | -1.9031e-07 | 0.005685 | 0.0056852 | 0.0056852 | 0.98192 | -0.12643 | 0.98171 | -0.12795 | 2.1056
26 | 0.015708 | 0.0039374 | -0.015698 | -0.0039339 | 9.9967e-06 | 3.4875e-06 | 0.023805 | 0.023805 | 0.023805 | 0.98192 | -0.12643 | 0.98128 | -0.13103 | 8.8165
27 | -0.071581 | -0.018009 | 0.071633 | 0.018028 | 5.2856e-05 | 1.95e-05 | 0.10818 | 0.10818 | 0.10818 | 0.98478 | -0.10622 | 0.98553 | -0.10093 | 13.3561
28 | 0.017276 | 0.0043308 | -0.01726 | -0.0043252 | 1.5975e-05 | 5.6859e-06 | 0.026372 | 0.026372 | 0.026372 | 0.97483 | -0.17698 | 0.9739 | -0.18366 | 9.7673
29 | 0.0084654 | 0.0021213 | -0.0084624 | -0.0021204 | 3.0641e-06 | 8.022e-07 | 0.012837 | 0.012837 | 0.012837 | 0.98128 | -0.13103 | 0.98091 | -0.13365 | 4.7545
30 | -0.072903 | -0.018346 | 0.072954 | 0.018365 | 5.135e-05 | 1.8971e-05 | 0.1101 | 0.1101 | 0.1101 | 0.98553 | -0.10093 | 0.98624 | -0.09589 | 13.5926
31 | 0.074574 | 0.01878 | -0.0745 | -0.018752 | 7.4925e-05 | 2.7725e-05 | 0.11243 | 0.11243 | 0.11243 | 0.98726 | -0.088695 | 0.98624 | -0.09589 | 13.8805
32 | 0.0025497 | 0.00063861 | -0.0025494 | -0.00063894 | 3.4355e-07 | -3.3236e-07 | 0.0038677 | 0.0038679 | 0.0038679 | 0.98091 | -0.13365 | 0.98078 | -0.13462 | 1.4326

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.16252 | 0.040866

## res_load
| p_mw | q_mvar
0 | 0.0027155 | 0.00068057
1 | 0.0028236 | 0.00070765
2 | 0.0058168 | 0.0014578
3 | 0.0046845 | 0.001174
4 | 0.0021322 | 0.00053437
5 | 0.0082097 | 0.0020576
6 | 0.0023002 | 0.00057649
7 | 0.016776 | 0.0042044
8 | 0.0040335 | 0.0010109
9 | 0.040913 | 0.010254
10 | 0.0042997 | 0.0010776
11 | 0.0016858 | 0.00042251
12 | 0.0038545 | 0.00096602
13 | 0.0082579 | 0.0020696
14 | 0.0036195 | 0.00090712
15 | 0.0023373 | 0.00058578
16 | 0.0032085 | 0.00080413
17 | 0.0037508 | 0.00094003
18 | 0.0072327 | 0.0018127
19 | 0.0012692 | 0.00031808
20 | 0.011718 | 0.0029368
21 | 0.0073798 | 0.0018495
22 | 0.0015455 | 0.00038735
23 | 0.0059126 | 0.0014818
24 | 0.0025494 | 0.00063894

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1