## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1150-1_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1150-1_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1150-1_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1150-1_0_7_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1150-1_0_7_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1150-1_0_7_node_54 | 0.4 | n |  | TRUE
6 | bus_LV_1150-1_0_7_node_56 | 0.4 | n |  | TRUE
7 | bus_LV_1150-1_0_7_node_28 | 0.4 | n |  | TRUE
8 | bus_LV_1150-1_0_7_node_52 | 0.4 | n |  | TRUE
9 | bus_LV_1150-1_0_7_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1150-1_0_7_node_23 | 0.4 | n |  | TRUE
11 | bus_LV_1150-1_0_7_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_1150-1_0_7_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_1150-1_0_7_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1150-1_0_7_node_22 | 0.4 | n |  | TRUE
15 | bus_LV_1150-1_0_7_node_27 | 0.4 | n |  | TRUE
16 | bus_LV_1150-1_0_7_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1150-1_0_7_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1150-1_0_7_node_6 | 0.4 | n |  | TRUE
19 | bus_LV_1150-1_0_7_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_1150-1_0_7_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_1150-1_0_7_node_9 | 0.4 | n |  | TRUE
22 | bus_LV_1150-1_0_7_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_1150-1_0_7_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1150-1_0_7_node_48 | 0.4 | n |  | TRUE
25 | bus_LV_1150-1_0_7_node_45 | 0.4 | n |  | TRUE
26 | bus_LV_1150-1_0_7_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_1150-1_0_7_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1150-1_0_7_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_1150-1_0_7_node_47 | 0.4 | n |  | TRUE
30 | bus_LV_1150-1_0_7_node_43 | 0.4 | n |  | TRUE
31 | bus_LV_1150-1_0_7_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_1150-1_0_7_node_19 | 0.4 | n |  | TRUE
33 | bus_LV_1150-1_0_7_node_49 | 0.4 | n |  | TRUE
34 | bus_LV_1150-1_0_7_node_51 | 0.4 | n |  | TRUE
35 | bus_LV_1150-1_0_7_node_50 | 0.4 | n |  | TRUE
36 | bus_LV_1150-1_0_7_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_1150-1_0_7_node_44 | 0.4 | n |  | TRUE
38 | bus_LV_1150-1_0_7_node_13 | 0.4 | n |  | TRUE
39 | bus_LV_1150-1_0_7_node_20 | 0.4 | n |  | TRUE
40 | bus_LV_1150-1_0_7_node_60 | 0.4 | n |  | TRUE
41 | bus_LV_1150-1_0_7_node_58 | 0.4 | n |  | TRUE
42 | bus_LV_1150-1_0_7_node_59 | 0.4 | n |  | TRUE
43 | bus_LV_1150-1_0_7_node_29 | 0.4 | n |  | TRUE
44 | bus_LV_1150-1_0_7_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_1150-1_0_7_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_1150-1_0_7_node_105 | 0.4 | n |  | TRUE
47 | bus_LV_1150-1_0_7_node_102 | 0.4 | n |  | TRUE
48 | bus_LV_1150-1_0_7_node_109 | 0.4 | n |  | TRUE
49 | bus_LV_1150-1_0_7_node_103 | 0.4 | n |  | TRUE
50 | bus_LV_1150-1_0_7_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_1150-1_0_7_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_1150-1_0_7_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_1150-1_0_7_node_35 | 0.4 | n |  | TRUE
54 | bus_LV_1150-1_0_7_node_37 | 0.4 | n |  | TRUE
55 | bus_LV_1150-1_0_7_node_38 | 0.4 | n |  | TRUE
56 | bus_LV_1150-1_0_7_node_40 | 0.4 | n |  | TRUE
57 | bus_LV_1150-1_0_7_node_41 | 0.4 | n |  | TRUE
58 | bus_LV_1150-1_0_7_node_39 | 0.4 | n |  | TRUE
59 | bus_LV_1150-1_0_7_node_42 | 0.4 | n |  | TRUE
60 | bus_LV_1150-1_0_7_node_53 | 0.4 | n |  | TRUE
61 | bus_LV_1150-1_0_7_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_1150-1_0_7_node_57 | 0.4 | n |  | TRUE
63 | bus_LV_1150-1_0_7_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_1150-1_0_7_node_64 | 0.4 | n |  | TRUE
65 | bus_LV_1150-1_0_7_node_93 | 0.4 | n |  | TRUE
66 | bus_LV_1150-1_0_7_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_1150-1_0_7_node_94 | 0.4 | n |  | TRUE
68 | bus_LV_1150-1_0_7_node_63 | 0.4 | n |  | TRUE
69 | bus_LV_1150-1_0_7_node_66 | 0.4 | n |  | TRUE
70 | bus_LV_1150-1_0_7_node_67 | 0.4 | n |  | TRUE
71 | bus_LV_1150-1_0_7_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_1150-1_0_7_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_1150-1_0_7_node_87 | 0.4 | n |  | TRUE
74 | bus_LV_1150-1_0_7_node_85 | 0.4 | n |  | TRUE
75 | bus_LV_1150-1_0_7_node_71 | 0.4 | n |  | TRUE
76 | bus_LV_1150-1_0_7_node_72 | 0.4 | n |  | TRUE
77 | bus_LV_1150-1_0_7_node_73 | 0.4 | n |  | TRUE
78 | bus_LV_1150-1_0_7_node_74 | 0.4 | n |  | TRUE
79 | bus_LV_1150-1_0_7_node_75 | 0.4 | n |  | TRUE
80 | bus_LV_1150-1_0_7_node_91 | 0.4 | n |  | TRUE
81 | bus_LV_1150-1_0_7_node_92 | 0.4 | n |  | TRUE
82 | bus_LV_1150-1_0_7_node_82 | 0.4 | n |  | TRUE
83 | bus_LV_1150-1_0_7_node_76 | 0.4 | n |  | TRUE
84 | bus_LV_1150-1_0_7_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_1150-1_0_7_node_79 | 0.4 | n |  | TRUE
86 | bus_LV_1150-1_0_7_node_96 | 0.4 | n |  | TRUE
87 | bus_LV_1150-1_0_7_node_81 | 0.4 | n |  | TRUE
88 | bus_LV_1150-1_0_7_node_89 | 0.4 | n |  | TRUE
89 | bus_LV_1150-1_0_7_node_90 | 0.4 | n |  | TRUE
90 | bus_LV_1150-1_0_7_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_1150-1_0_7_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_1150-1_0_7_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_1150-1_0_7_node_88 | 0.4 | n |  | TRUE
94 | bus_LV_1150-1_0_7_node_95 | 0.4 | n |  | TRUE
95 | bus_LV_1150-1_0_7_node_117 | 0.4 | n |  | TRUE
96 | bus_LV_1150-1_0_7_node_122 | 0.4 | n |  | TRUE
97 | bus_LV_1150-1_0_7_node_124 | 0.4 | n |  | TRUE
98 | bus_LV_1150-1_0_7_node_100 | 0.4 | n |  | TRUE
99 | bus_LV_1150-1_0_7_node_123 | 0.4 | n |  | TRUE
100 | bus_LV_1150-1_0_7_node_97 | 0.4 | n |  | TRUE
101 | bus_LV_1150-1_0_7_node_98 | 0.4 | n |  | TRUE
102 | bus_LV_1150-1_0_7_node_99 | 0.4 | n |  | TRUE
103 | bus_LV_1150-1_0_7_node_101 | 0.4 | n |  | TRUE
104 | bus_LV_1150-1_0_7_node_114 | 0.4 | n |  | TRUE
105 | bus_LV_1150-1_0_7_node_118 | 0.4 | n |  | TRUE
106 | bus_LV_1150-1_0_7_node_119 | 0.4 | n |  | TRUE
107 | bus_LV_1150-1_0_7_node_104 | 0.4 | n |  | TRUE
108 | bus_LV_1150-1_0_7_node_106 | 0.4 | n |  | TRUE
109 | bus_LV_1150-1_0_7_node_107 | 0.4 | n |  | TRUE
110 | bus_LV_1150-1_0_7_node_108 | 0.4 | n |  | TRUE
111 | bus_LV_1150-1_0_7_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_1150-1_0_7_node_112 | 0.4 | n |  | TRUE
113 | bus_LV_1150-1_0_7_node_110 | 0.4 | n |  | TRUE
114 | bus_LV_1150-1_0_7_node_111 | 0.4 | n |  | TRUE
115 | bus_LV_1150-1_0_7_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_1150-1_0_7_node_116 | 0.4 | n |  | TRUE
117 | bus_LV_1150-1_0_7_node_120 | 0.4 | n |  | TRUE
118 | bus_LV_1150-1_0_7_node_121 | 0.4 | n |  | TRUE
119 | bus_MV_129_0_node_251 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1150-1_0_7_load_0 | 0 | 0.00058826 | 0.00014743 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1150-1_0_7_load_1 | 1 | 0.0010829 | 0.00027139 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1150-1_0_7_load_2 | 2 | 0.00017632 | 4.4191e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1150-1_0_7_load_3 | 3 | 0.0002766 | 6.9323e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1150-1_0_7_load_4 | 4 | 0.00016969 | 4.2529e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1150-1_0_7_load_54 | 5 | 0.00017991 | 4.5089e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1150-1_0_7_load_52 | 8 | 0.00010746 | 2.6932e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1150-1_0_7_load_23 | 10 | 0.00070494 | 0.00017667 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1150-1_0_7_load_24 | 12 | 0.0011224 | 0.00028131 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1150-1_0_7_load_17 | 13 | 0.0003155 | 7.9073e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1150-1_0_7_load_22 | 14 | 0.0018051 | 0.00045239 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1150-1_0_7_load_25 | 16 | 0.00031902 | 7.9954e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1150-1_0_7_load_15 | 17 | 0.00029764 | 7.4596e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1150-1_0_7_load_6 | 18 | 0.027032 | 0.0067748 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1150-1_0_7_load_48 | 24 | 0.026309 | 0.0065937 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1150-1_0_7_load_45 | 25 | 0.0039881 | 0.00099951 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1150-1_0_7_load_46 | 26 | 0.0056898 | 0.001426 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1150-1_0_7_load_16 | 27 | 0.011286 | 0.0028286 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1150-1_0_7_load_18 | 28 | 0.0077708 | 0.0019475 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1150-1_0_7_load_47 | 29 | 0.012553 | 0.003146 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1150-1_0_7_load_14 | 31 | 0.00053852 | 0.00013497 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1150-1_0_7_load_19 | 32 | 0.0146 | 0.003659 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1150-1_0_7_load_49 | 33 | 0.00028524 | 7.1489e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1150-1_0_7_load_51 | 34 | 0.00092059 | 0.00023072 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1150-1_0_7_load_44 | 37 | 0.0099596 | 0.0024961 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1150-1_0_7_load_13 | 38 | 0.0023156 | 0.00058033 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1150-1_0_7_load_20 | 39 | 0.033416 | 0.0083748 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1150-1_0_7_load_60 | 40 | 0.00011959 | 2.9973e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1150-1_0_7_load_58 | 41 | 0.00018785 | 4.708e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1150-1_0_7_load_59 | 42 | 3.8974e-05 | 9.7679e-06 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1150-1_0_7_load_29 | 43 | 0.0011792 | 0.00029554 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1150-1_0_7_load_102 | 47 | 0.0010162 | 0.00025468 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1150-1_0_7_load_109 | 48 | 0.00014422 | 3.6145e-05 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1150-1_0_7_load_103 | 49 | 0.0014416 | 0.00036129 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1150-1_0_7_load_32 | 50 | 0.002685 | 0.00067292 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1150-1_0_7_load_33 | 51 | 0.0012081 | 0.00030277 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1150-1_0_7_load_35 | 53 | 0.00038159 | 9.5635e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1150-1_0_7_load_37 | 54 | 0.0025338 | 0.00063502 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1150-1_0_7_load_41 | 57 | 0.027823 | 0.006973 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1150-1_0_7_load_39 | 58 | 0.00066388 | 0.00016638 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1150-1_0_7_load_42 | 59 | 0.0033513 | 0.00083991 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1150-1_0_7_load_53 | 60 | 5.5009e-05 | 1.3787e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1150-1_0_7_load_55 | 61 | 0.00028836 | 7.2271e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1150-1_0_7_load_64 | 64 | 0.00010925 | 2.738e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1150-1_0_7_load_93 | 65 | 9.8917e-05 | 2.4791e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1150-1_0_7_load_62 | 66 | 0.0004431 | 0.00011105 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1150-1_0_7_load_94 | 67 | 0.0001354 | 3.3936e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1150-1_0_7_load_63 | 68 | 0.00013177 | 3.3025e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1150-1_0_7_load_66 | 69 | 0.0004852 | 0.0001216 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1150-1_0_7_load_67 | 70 | 0.00049613 | 0.00012434 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1150-1_0_7_load_68 | 71 | 4.2681e-05 | 1.0697e-05 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1150-1_0_7_load_69 | 72 | 0.00017584 | 4.4071e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1150-1_0_7_load_71 | 75 | 9.6851e-05 | 2.4273e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1150-1_0_7_load_72 | 76 | 0.00017108 | 4.2878e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1150-1_0_7_load_73 | 77 | 0.00016824 | 4.2165e-05 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1150-1_0_7_load_74 | 78 | 0.00010639 | 2.6665e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1150-1_0_7_load_75 | 79 | 0.00053681 | 0.00013454 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1150-1_0_7_load_82 | 82 | 0.00020358 | 5.1022e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1150-1_0_7_load_76 | 83 | 0.00121 | 0.00030325 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1150-1_0_7_load_96 | 86 | 0.00013409 | 3.3606e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1150-1_0_7_load_81 | 87 | 0.00018329 | 4.5937e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1150-1_0_7_load_83 | 90 | 8.4619e-05 | 2.1207e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1150-1_0_7_load_84 | 91 | 5.189e-05 | 1.3005e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1150-1_0_7_load_86 | 92 | 7.589e-05 | 1.902e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1150-1_0_7_load_88 | 93 | 0.00013555 | 3.3971e-05 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1150-1_0_7_load_122 | 96 | 8.6926e-05 | 2.1786e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1150-1_0_7_load_124 | 97 | 0.00021329 | 5.3455e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1150-1_0_7_load_123 | 99 | 0.00025799 | 6.4659e-05 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1150-1_0_7_load_97 | 100 | 0.00029014 | 7.2716e-05 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1150-1_0_7_load_98 | 101 | 0.00088765 | 0.00022247 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1150-1_0_7_load_99 | 102 | 0.00031813 | 7.9732e-05 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1150-1_0_7_load_101 | 103 | 0.00046641 | 0.00011689 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1150-1_0_7_load_114 | 104 | 5.0687e-05 | 1.2703e-05 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1150-1_0_7_load_118 | 105 | 0.00012049 | 3.0198e-05 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1150-1_0_7_load_119 | 106 | 0.00046352 | 0.00011617 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1150-1_0_7_load_104 | 107 | 0.00066781 | 0.00016737 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1150-1_0_7_load_106 | 108 | 0.00077211 | 0.00019351 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1150-1_0_7_load_107 | 109 | 0.00017234 | 4.3191e-05 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1150-1_0_7_load_108 | 110 | 8.2678e-05 | 2.0721e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1150-1_0_7_load_113 | 111 | 0.0007242 | 0.0001815 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1150-1_0_7_load_112 | 112 | 0.00045273 | 0.00011346 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1150-1_0_7_load_110 | 113 | 0.00020898 | 5.2376e-05 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1150-1_0_7_load_111 | 114 | 0.0002211 | 5.5412e-05 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1150-1_0_7_load_115 | 115 | 6.0727e-05 | 1.522e-05 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1150-1_0_7_load_121 | 118 | 0.0001419 | 3.5563e-05 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1150-1_0_7_line_0 | NAYY 4x150 SE | 0 | 1 | 0.020376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1150-1_0_7_line_1 | NAYY 4x150 SE | 0 | 2 | 0.073573 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1150-1_0_7_line_2 | NAYY 4x150 SE | 1 | 3 | 0.0049956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1150-1_0_7_line_3 | NAYY 4x150 SE | 2 | 4 | 0.018017 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
4 | LV_1150-1_0_7_line_4 | NAYY 4x150 SE | 3 | 9 | 0.036349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1150-1_0_7_line_5 | NAYY 4x150 SE | 3 | 10 | 0.15354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1150-1_0_7_line_6 | NAYY 4x150 SE | 4 | 11 | 0.052532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1150-1_0_7_line_7 | NAYY 4x150 SE | 5 | 6 | 0.20367 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
8 | LV_1150-1_0_7_line_8 | NAYY 4x150 SE | 5 | 7 | 0.21493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
9 | LV_1150-1_0_7_line_9 | NAYY 4x150 SE | 5 | 8 | 0.051579 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1150-1_0_7_line_10 | NAYY 4x150 SE | 6 | 62 | 0.40223 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
11 | LV_1150-1_0_7_line_11 | NAYY 4x150 SE | 7 | 42 | 0.041897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
12 | LV_1150-1_0_7_line_12 | NAYY 4x150 SE | 8 | 60 | 0.0077985 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1150-1_0_7_line_13 | NAYY 4x150 SE | 9 | 12 | 0.056658 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1150-1_0_7_line_14 | NAYY 4x150 SE | 9 | 13 | 0.0063678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1150-1_0_7_line_15 | NAYY 4x150 SE | 10 | 14 | 0.030811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1150-1_0_7_line_16 | NAYY 4x150 SE | 11 | 15 | 0.40753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1150-1_0_7_line_17 | NAYY 4x150 SE | 12 | 16 | 0.041303 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1150-1_0_7_line_18 | NAYY 4x150 SE | 13 | 17 | 0.015005 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1150-1_0_7_line_19 | NAYY 4x150 SE | 15 | 40 | 0.013491 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1150-1_0_7_line_20 | NAYY 4x150 SE | 15 | 41 | 0.16056 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1150-1_0_7_line_21 | NAYY 4x150 SE | 16 | 36 | 0.022336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1150-1_0_7_line_22 | NAYY 4x150 SE | 17 | 38 | 0.023184 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1150-1_0_7_line_23 | NAYY 4x150 SE | 18 | 19 | 0.019653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1150-1_0_7_line_24 | NAYY 4x150 SE | 18 | 20 | 0.033235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1150-1_0_7_line_25 | NAYY 4x150 SE | 19 | 21 | 0.004292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1150-1_0_7_line_26 | NAYY 4x150 SE | 19 | 22 | 0.045166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
27 | LV_1150-1_0_7_line_27 | NAYY 4x150 SE | 20 | 23 | 0.004595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1150-1_0_7_line_28 | NAYY 4x150 SE | 21 | 24 | 0.019737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1150-1_0_7_line_29 | NAYY 4x150 SE | 21 | 25 | 0.032974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1150-1_0_7_line_30 | NAYY 4x150 SE | 21 | 26 | 0.015162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1150-1_0_7_line_31 | NAYY 4x150 SE | 22 | 27 | 0.019412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1150-1_0_7_line_32 | NAYY 4x150 SE | 22 | 28 | 0.015911 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1150-1_0_7_line_33 | NAYY 4x150 SE | 23 | 29 | 0.015432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1150-1_0_7_line_34 | NAYY 4x150 SE | 25 | 30 | 0.010185 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1150-1_0_7_line_35 | NAYY 4x150 SE | 27 | 31 | 0.040742 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1150-1_0_7_line_36 | NAYY 4x150 SE | 28 | 32 | 0.042181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1150-1_0_7_line_37 | NAYY 4x150 SE | 29 | 37 | 0.011604 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1150-1_0_7_line_38 | NAYY 4x150 SE | 30 | 57 | 0.014534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1150-1_0_7_line_39 | NAYY 4x150 SE | 30 | 54 | 0.011594 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1150-1_0_7_line_40 | NAYY 4x150 SE | 31 | 38 | 0.039101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1150-1_0_7_line_41 | NAYY 4x150 SE | 32 | 39 | 0.0079162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1150-1_0_7_line_42 | NAYY 4x150 SE | 33 | 34 | 0.045508 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1150-1_0_7_line_43 | NAYY 4x150 SE | 34 | 35 | 0.0046622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1150-1_0_7_line_44 | NAYY 4x150 SE | 35 | 36 | 0.04699 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1150-1_0_7_line_45 | NAYY 4x150 SE | 37 | 59 | 0.027251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1150-1_0_7_line_46 | NAYY 4x150 SE | 41 | 42 | 0.025864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1150-1_0_7_line_47 | NAYY 4x150 SE | 43 | 44 | 0.21048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
48 | LV_1150-1_0_7_line_48 | NAYY 4x150 SE | 44 | 45 | 0.30779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1150-1_0_7_line_49 | NAYY 4x150 SE | 45 | 46 | 0.23147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1150-1_0_7_line_50 | NAYY 4x150 SE | 45 | 47 | 0.13569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
51 | LV_1150-1_0_7_line_51 | NAYY 4x150 SE | 46 | 48 | 0.12448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
52 | LV_1150-1_0_7_line_52 | NAYY 4x150 SE | 47 | 49 | 0.012533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
53 | LV_1150-1_0_7_line_53 | NAYY 4x150 SE | 48 | 110 | 0.15077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
54 | LV_1150-1_0_7_line_54 | NAYY 4x150 SE | 49 | 107 | 0.001439 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
55 | LV_1150-1_0_7_line_55 | NAYY 4x150 SE | 50 | 51 | 0.076723 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1150-1_0_7_line_56 | NAYY 4x150 SE | 50 | 52 | 0.022864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1150-1_0_7_line_57 | NAYY 4x150 SE | 51 | 53 | 0.0059194 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1150-1_0_7_line_58 | NAYY 4x150 SE | 52 | 54 | 0.058672 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1150-1_0_7_line_59 | NAYY 4x150 SE | 53 | 55 | 0.40701 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1150-1_0_7_line_60 | NAYY 4x150 SE | 55 | 56 | 0.60333 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1150-1_0_7_line_61 | NAYY 4x150 SE | 56 | 58 | 0.017307 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1150-1_0_7_line_62 | NAYY 4x150 SE | 60 | 61 | 0.023524 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1150-1_0_7_line_63 | NAYY 4x150 SE | 62 | 63 | 0.54313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_1150-1_0_7_line_64 | NAYY 4x150 SE | 63 | 64 | 0.091997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1150-1_0_7_line_65 | NAYY 4x150 SE | 63 | 65 | 0.015759 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_1150-1_0_7_line_66 | NAYY 4x150 SE | 64 | 66 | 0.0087657 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1150-1_0_7_line_67 | NAYY 4x150 SE | 65 | 67 | 0.014634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
68 | LV_1150-1_0_7_line_68 | NAYY 4x150 SE | 66 | 68 | 0.023493 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1150-1_0_7_line_69 | NAYY 4x150 SE | 67 | 94 | 0.05349 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_1150-1_0_7_line_70 | NAYY 4x150 SE | 69 | 70 | 0.062992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1150-1_0_7_line_71 | NAYY 4x150 SE | 69 | 71 | 0.045925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1150-1_0_7_line_72 | NAYY 4x150 SE | 70 | 72 | 0.0039135 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1150-1_0_7_line_73 | NAYY 4x150 SE | 72 | 73 | 0.034874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1150-1_0_7_line_74 | NAYY 4x150 SE | 73 | 74 | 0.17192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1150-1_0_7_line_75 | NAYY 4x150 SE | 74 | 93 | 0.01996 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_1150-1_0_7_line_76 | NAYY 4x150 SE | 74 | 90 | 0.0068327 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1150-1_0_7_line_77 | NAYY 4x150 SE | 75 | 76 | 0.0068287 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1150-1_0_7_line_78 | NAYY 4x150 SE | 75 | 77 | 0.028445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1150-1_0_7_line_79 | NAYY 4x150 SE | 76 | 78 | 0.0087772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1150-1_0_7_line_80 | NAYY 4x150 SE | 77 | 79 | 0.029099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1150-1_0_7_line_81 | NAYY 4x150 SE | 78 | 80 | 0.032929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1150-1_0_7_line_82 | NAYY 4x150 SE | 80 | 81 | 0.04412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
83 | LV_1150-1_0_7_line_83 | NAYY 4x150 SE | 80 | 82 | 0.28153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
84 | LV_1150-1_0_7_line_84 | NAYY 4x150 SE | 81 | 95 | 0.28851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
85 | LV_1150-1_0_7_line_85 | NAYY 4x150 SE | 81 | 96 | 0.30035 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1150-1_0_7_line_86 | NAYY 4x150 SE | 82 | 84 | 0.023435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
87 | LV_1150-1_0_7_line_87 | NAYY 4x150 SE | 83 | 84 | 0.063889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1150-1_0_7_line_88 | NAYY 4x150 SE | 84 | 85 | 0.042354 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
89 | LV_1150-1_0_7_line_89 | NAYY 4x150 SE | 85 | 86 | 0.12227 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
90 | LV_1150-1_0_7_line_90 | NAYY 4x150 SE | 86 | 89 | 0.046807 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
91 | LV_1150-1_0_7_line_91 | NAYY 4x150 SE | 87 | 88 | 0.018679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1150-1_0_7_line_92 | NAYY 4x150 SE | 88 | 89 | 0.068281 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1150-1_0_7_line_93 | NAYY 4x150 SE | 89 | 93 | 0.18696 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
94 | LV_1150-1_0_7_line_94 | NAYY 4x150 SE | 90 | 91 | 0.01771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
95 | LV_1150-1_0_7_line_95 | NAYY 4x150 SE | 91 | 92 | 0.001273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
96 | LV_1150-1_0_7_line_96 | NAYY 4x150 SE | 92 | 94 | 0.064368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
97 | LV_1150-1_0_7_line_97 | NAYY 4x150 SE | 95 | 97 | 0.024624 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1150-1_0_7_line_98 | NAYY 4x150 SE | 95 | 98 | 0.11309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
99 | LV_1150-1_0_7_line_99 | NAYY 4x150 SE | 96 | 99 | 0.02509 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1150-1_0_7_line_100 | NAYY 4x150 SE | 98 | 104 | 0.14313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1150-1_0_7_line_101 | NAYY 4x150 SE | 98 | 101 | 0.080302 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
102 | LV_1150-1_0_7_line_102 | NAYY 4x150 SE | 100 | 101 | 0.017007 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
103 | LV_1150-1_0_7_line_103 | NAYY 4x150 SE | 100 | 102 | 0.036278 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
104 | LV_1150-1_0_7_line_104 | NAYY 4x150 SE | 102 | 103 | 0.0040527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
105 | LV_1150-1_0_7_line_105 | NAYY 4x150 SE | 103 | 105 | 0.01433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
106 | LV_1150-1_0_7_line_106 | NAYY 4x150 SE | 105 | 106 | 0.036734 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
107 | LV_1150-1_0_7_line_107 | NAYY 4x150 SE | 106 | 116 | 0.058115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
108 | LV_1150-1_0_7_line_108 | NAYY 4x150 SE | 107 | 108 | 0.0063656 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
109 | LV_1150-1_0_7_line_109 | NAYY 4x150 SE | 108 | 109 | 0.0056585 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1150-1_0_7_line_110 | NAYY 4x150 SE | 109 | 111 | 0.0028659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1150-1_0_7_line_111 | NAYY 4x150 SE | 110 | 113 | 0.020115 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
112 | LV_1150-1_0_7_line_112 | NAYY 4x150 SE | 111 | 112 | 0.012019 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1150-1_0_7_line_113 | NAYY 4x150 SE | 113 | 114 | 0.020894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
114 | LV_1150-1_0_7_line_114 | NAYY 4x150 SE | 114 | 115 | 0.00043843 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
115 | LV_1150-1_0_7_line_115 | NAYY 4x150 SE | 115 | 116 | 0.38845 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
116 | LV_1150-1_0_7_line_116 | NAYY 4x150 SE | 116 | 117 | 0.28324 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1150-1_0_7_line_117 | NAYY 4x150 SE | 117 | 118 | 0.18203 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1150-1_0_7_trafo_5 | 0.25 MVA 20/0.4 kV | 119 | 9 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38
0 | 2637662.4151 | 1220577.6222 | 2637672.6942 | 1220584.2038 | 2637679.0854 | 1220589.2939
1 | 2637662.4151 | 1220577.6222 | 2637648.3712 | 1220568.6298 | 2637627.25 | 1220556.6005 | 2637599.8793 | 1220546.6441 | 2637596.705 | 1220545.2545
2 | 2637679.0854 | 1220589.2939 | 2637682.9931 | 1220592.406
3 | 2637580.2001 | 1220538.0293 | 2637596.705 | 1220545.2545
4 | 2637706.7766 | 1220619.6736 | 2637704.4221 | 1220616.4902 | 2637689.1577 | 1220597.3156 | 2637682.9931 | 1220592.406
5 | 2637682.9931 | 1220592.406 | 2637808.9474 | 1220504.5945
6 | 2637531.4249 | 1220518.8853 | 2637542.9843 | 1220521.7375 | 2637580.2001 | 1220538.0293
7 | 2637712.7364 | 1219816.8574 | 2637704.6268 | 1219844.2001 | 2637698.8819 | 1219859.962 | 2637691.2212 | 1219872.7211 | 2637675.074 | 1219892.075 | 2637665.3738 | 1219904.6101 | 2637659.6143 | 1219914.3128 | 2637653.9891 | 1219935.1785 | 2637650.2424 | 1219948.1403 | 2637643.9012 | 1219961.0635 | 2637623.7373 | 1219988.1412 | 2637618.0049 | 1219993.5749
8 | 2637618.0049 | 1219993.5749 | 2637565.037 | 1220201.8756
9 | 2637592.9447 | 1219963.4416 | 2637590.268 | 1219971.498 | 2637591.0704 | 1219981.4201 | 2637594.89 | 1219988.137 | 2637602.3895 | 1219993.6653 | 2637610.2608 | 1219995.5605 | 2637618.0049 | 1219993.5749
10 | 2637712.7364 | 1219816.8574 | 2637528.6222 | 1219781.9975 | 2637511.4989 | 1219778.0541 | 2637496.7304 | 1219772.4691 | 2637474.9728 | 1219762.204 | 2637435.4335 | 1219738.0192 | 2637343.526 | 1219692.8051 | 2637333.9834 | 1219691.1333
11 | 2637565.037 | 1220201.8756 | 2637576.7995 | 1220202.6835 | 2637592.6443 | 1220207.0415 | 2637604.5075 | 1220213.841
12 | 2637592.9447 | 1219963.4416 | 2637595.4035 | 1219956.0409
13 | 2637706.7766 | 1220619.6736 | 2637708.235 | 1220625.3862 | 2637699.7064 | 1220655.5613 | 2637691.4387 | 1220668.4945 | 2637691.4131 | 1220672.5492
14 | 2637706.7766 | 1220619.6736 | 2637711.2385 | 1220624.2168
15 | 2637839.349 | 1220509.5571 | 2637817.4374 | 1220505.6734 | 2637808.9474 | 1220504.5945
16 | 2637531.4249 | 1220518.8853 | 2637536.5964 | 1220506.0547 | 2637542.0133 | 1220500.0519 | 2637561.399 | 1220482.9527 | 2637579.7806 | 1220472.3067 | 2637596.7751 | 1220463.8754 | 2637604.9185 | 1220455.0215 | 2637608.8452 | 1220445.9187 | 2637612.183 | 1220432.7541 | 2637617.3287 | 1220391.6066 | 2637620.2171 | 1220384.7319 | 2637624.9757 | 1220380.8818 | 2637632.8683 | 1220379.3307 | 2637639.179 | 1220379.5707 | 2637645.2633 | 1220382.0439 | 2637651.3385 | 1220387.152 | 2637665.4798 | 1220402.8617 | 2637669.3451 | 1220403.4976 | 2637674.498 | 1220400.873 | 2637687.8008 | 1220389.5948 | 2637695.1314 | 1220380.936 | 2637755.3071 | 1220294.0874 | 2637778.4608 | 1220268.0631
17 | 2637691.4131 | 1220672.5492 | 2637691.3596 | 1220681.0126 | 2637689.5219 | 1220684.881 | 2637685.1092 | 1220688.055 | 2637663.4227 | 1220696.0732
18 | 2637721.5571 | 1220635.1017 | 2637719.0711 | 1220632.1921 | 2637711.2385 | 1220624.2168
19 | 2637778.4608 | 1220268.0631 | 2637791.9437 | 1220267.6021
20 | 2637778.4608 | 1220268.0631 | 2637744.6717 | 1220269.8835 | 2637714.8373 | 1220265.4143 | 2637678.886 | 1220254.0248 | 2637646.7773 | 1220239.6468 | 2637626.6254 | 1220227.2438
21 | 2637641.6731 | 1220694.5957 | 2637647.37 | 1220695.888 | 2637654.0209 | 1220697.4642 | 2637659.536 | 1220697.5102 | 2637663.4227 | 1220696.0732
22 | 2637721.5571 | 1220635.1017 | 2637736.6179 | 1220652.7281
23 | 2637823.9949 | 1220747.9256 | 2637843.5351 | 1220750.0289
24 | 2637876.6108 | 1220753.2738 | 2637853.8499 | 1220751.1391 | 2637843.5351 | 1220750.0289
25 | 2637823.9949 | 1220747.9256 | 2637823.9221 | 1220752.2165
26 | 2637804.8195 | 1220723.5228 | 2637801.7028 | 1220741.2469 | 2637801.0853 | 1220745.3121 | 2637823.9949 | 1220747.9256
27 | 2637876.6108 | 1220753.2738 | 2637877.3102 | 1220757.8143
28 | 2637823.9221 | 1220752.2165 | 2637804.3122 | 1220749.9837
29 | 2637823.9221 | 1220752.2165 | 2637823.477 | 1220776.9284 | 2637821.8817 | 1220785.0308
30 | 2637823.9221 | 1220752.2165 | 2637832.193 | 1220753.1473 | 2637838.9911 | 1220753.8971
31 | 2637804.8195 | 1220723.5228 | 2637798.4841 | 1220721.2368 | 2637793.2497 | 1220717.6015 | 2637788.7871 | 1220713.1492
32 | 2637804.8195 | 1220723.5228 | 2637811.6944 | 1220710.114 | 2637812.0946 | 1220709.3721
33 | 2637877.3102 | 1220757.8143 | 2637879.6445 | 1220773.0689
34 | 2637817.1032 | 1220793.8647 | 2637821.4153 | 1220787.3993 | 2637821.8817 | 1220785.0308
35 | 2637788.7871 | 1220713.1492 | 2637785.1078 | 1220709.4784 | 2637762.018 | 1220682.4551
36 | 2637834.7228 | 1220673.9335 | 2637831.641 | 1220677.5767 | 2637822.6032 | 1220689.8933 | 2637812.0946 | 1220709.3721
37 | 2637879.9846 | 1220784.6425 | 2637880.0417 | 1220775.6645 | 2637879.6445 | 1220773.0689
38 | 2637817.1032 | 1220793.8647 | 2637824.5568 | 1220798.0478 | 2637830.4621 | 1220799.0353
39 | 2637817.1032 | 1220793.8647 | 2637809.2681 | 1220802.41
40 | 2637762.018 | 1220682.4551 | 2637736.6179 | 1220652.7281
41 | 2637839.8353 | 1220667.8896 | 2637834.7228 | 1220673.9335
42 | 2637660.0339 | 1220731.4598 | 2637614.719 | 1220727.2672
43 | 2637610.0766 | 1220726.8377 | 2637614.719 | 1220727.2672
44 | 2637610.0766 | 1220726.8377 | 2637610.4387 | 1220723.5602 | 2637610.9952 | 1220720.7287 | 2637612.6833 | 1220717.7042 | 2637619.7934 | 1220710.2558 | 2637638.9373 | 1220695.3233 | 2637641.6731 | 1220694.5957
45 | 2637866.2612 | 1220803.7552 | 2637871.1209 | 1220802.9907 | 2637877.2446 | 1220799.1718 | 2637879.9295 | 1220793.3076 | 2637879.9846 | 1220784.6425
46 | 2637626.6254 | 1220227.2438 | 2637609.4724 | 1220216.6866 | 2637604.5075 | 1220213.841
47 | 2636491.0625 | 1218062.5347 | 2636486.8327 | 1218061.6639 | 2636473.5829 | 1218058.8368 | 2636458.6836 | 1218055.188 | 2636447.6056 | 1218052.1852 | 2636437.3547 | 1218047.9646 | 2636427.1898 | 1218042.099 | 2636419.7047 | 1218036.1276 | 2636409.7956 | 1218026.8839 | 2636331.4224 | 1217936.211
48 | 2636425.8052 | 1218358.1652 | 2636444.5121 | 1218300.0008 | 2636453.6986 | 1218261.0007 | 2636495.6411 | 1218063.4522 | 2636491.0625 | 1218062.5347
49 | 2636318.4856 | 1218554.5041 | 2636334.6799 | 1218545.9755 | 2636350.9047 | 1218533.6893 | 2636365.572 | 1218517.9472 | 2636377.3297 | 1218500.2196 | 2636386.701 | 1218478.086 | 2636425.8052 | 1218358.1652
50 | 2636425.8052 | 1218358.1652 | 2636546.0807 | 1218373.4098 | 2636554.3889 | 1218379.9645 | 2636557.6117 | 1218382.1039
51 | 2636318.4856 | 1218554.5041 | 2636314.3215 | 1218556.6133 | 2636292.1204 | 1218568.2628 | 2636273.1603 | 1218579.8655 | 2636259.3596 | 1218592.9337 | 2636249.5261 | 1218605.0811 | 2636234.359 | 1218630.7151 | 2636230.5681 | 1218637.8594
52 | 2636557.6117 | 1218382.1039 | 2636568.0532 | 1218389.035
53 | 2636159.9003 | 1218771.0407 | 2636230.5681 | 1218637.8594
54 | 2636569.2521 | 1218389.8308 | 2636568.0532 | 1218389.035
55 | 2637765.4449 | 1220870.833 | 2637731.112 | 1220935.1706 | 2637729.5244 | 1220938.6211
56 | 2637776.2091 | 1220850.6615 | 2637765.4449 | 1220870.833
57 | 2637729.5244 | 1220938.6211 | 2637727.0502 | 1220943.9986
58 | 2637776.2091 | 1220850.6615 | 2637779.3591 | 1220845.6117 | 2637791.7372 | 1220825.7117 | 2637799.8538 | 1220812.6776 | 2637809.2681 | 1220802.41
59 | 2637591.0611 | 1221137.5286 | 2637625.0728 | 1221139.3108 | 2637636.4793 | 1221137.3483 | 2637644.442 | 1221132.9404 | 2637648.115 | 1221125.5147 | 2637649.2185 | 1221117.7615 | 2637647.6388 | 1221109.6356 | 2637634.8819 | 1221093.59 | 2637629.0417 | 1221083.814 | 2637623.8953 | 1221067.494 | 2637623.9734 | 1221055.1205 | 2637626.2241 | 1221047.0855 | 2637633.8208 | 1221036.9941 | 2637642.4532 | 1221028.6658 | 2637647.9798 | 1221024.4426 | 2637654.9134 | 1221022.0517 | 2637662.1903 | 1221022.9648 | 2637667.2587 | 1221025.2315 | 2637670.939 | 1221029.8575 | 2637677.0749 | 1221050.453 | 2637679.6789 | 1221056.1395 | 2637684.1695 | 1221060.9819 | 2637690.0074 | 1221063.9205 | 2637696.5593 | 1221064.3066 | 2637704.3084 | 1221061.3094 | 2637735.7879 | 1221031.7576 | 2637742.5974 | 1221023.8182 | 2637746.5188 | 1221015.527 | 2637746.5728 | 1221007.0112 | 2637743.1166 | 1220999.3403 | 2637724.9646 | 1220981.1146 | 2637721.9129 | 1220974.2579 | 2637720.1769 | 1220965.664 | 2637721.6201 | 1220955.8006 | 2637727.0502 | 1220943.9986
60 | 2637591.0611 | 1221137.5286 | 2637583.1229 | 1221156.1007 | 2637582.4887 | 1221165.2466 | 2637586.5741 | 1221171.7873 | 2637602.1909 | 1221186.628 | 2637610.5107 | 1221190.5383 | 2637619.8126 | 1221192.6872 | 2637636.6814 | 1221195.4286 | 2637644.2266 | 1221199.4675 | 2637657.7554 | 1221209.7591 | 2637670.6966 | 1221221.8035 | 2637681.0466 | 1221226.1271 | 2637693.4476 | 1221227.6286 | 2637710.5416 | 1221227.1253 | 2637720.7085 | 1221229.2242 | 2637732.6818 | 1221233.5581 | 2637744.2862 | 1221238.6456 | 2637760.9088 | 1221249.0904 | 2637768.426 | 1221250.3499 | 2637776.1237 | 1221249.4537 | 2637782.0841 | 1221246.1784 | 2637800.6546 | 1221231.7542 | 2637806.7675 | 1221229.5694 | 2637813.0761 | 1221230.0097 | 2637818.797 | 1221232.214 | 2637824.8252 | 1221237.3886 | 2637840.4283 | 1221254.2643 | 2637845.0416 | 1221264.8333 | 2637849.592 | 1221279.3263 | 2637853.538 | 1221298.2182 | 2637862.4277 | 1221315.0513 | 2637873.6965 | 1221327.5526 | 2637898.0206 | 1221348.3306 | 2637910.7895 | 1221356.3277 | 2637950.775 | 1221371.5911 | 2637963.5393 | 1221373.14 | 2638019.1268 | 1221367.2129 | 2638034.998 | 1221366.9028 | 2638053.4992 | 1221369.3112
61 | 2638053.4992 | 1221369.3112 | 2638067.2017 | 1221379.8838
62 | 2637595.4035 | 1219956.0409 | 2637602.8205 | 1219933.7166
63 | 2637186.3298 | 1219338.8915 | 2637183.948 | 1219344.8357 | 2637185.3276 | 1219352.3598 | 2637189.5097 | 1219360.7242 | 2637231.971 | 1219404.8152 | 2637245.1231 | 1219415.448 | 2637260.1888 | 1219423.4357 | 2637419.5978 | 1219473.3521 | 2637430.1825 | 1219480.7007 | 2637435.2255 | 1219488.4369 | 2637438.3725 | 1219497.2063 | 2637438.9222 | 1219506.3373 | 2637432.9257 | 1219529.6135 | 2637425.0043 | 1219551.2988 | 2637410.65 | 1219577.5576 | 2637393.344 | 1219602.6306 | 2637374.5234 | 1219626.0264 | 2637347.483 | 1219653.451 | 2637340.0848 | 1219665.5786 | 2637335.8846 | 1219678.3487 | 2637333.3361 | 1219686.6599 | 2637333.9834 | 1219691.1333
64 | 2637186.3298 | 1219338.8915 | 2637190.7514 | 1219323.4544 | 2637197.7847 | 1219305.3764 | 2637205.1805 | 1219293.6601 | 2637214.4051 | 1219283.167 | 2637227.5917 | 1219290.7538 | 2637234.6882 | 1219297.8134 | 2637236.7285 | 1219300.6462
65 | 2637186.3298 | 1219338.8915 | 2637171.4705 | 1219333.6419
66 | 2637241.8515 | 1219307.759 | 2637236.7285 | 1219300.6462
67 | 2637171.4705 | 1219333.6419 | 2637157.6719 | 1219328.767
68 | 2637241.8515 | 1219307.759 | 2637249.2151 | 1219317.9826 | 2637256.0973 | 1219324.1181 | 2637257.3999 | 1219325.1691
69 | 2637107.2372 | 1219310.949 | 2637157.6719 | 1219328.767
70 | 2637085.6589 | 1219151.5492 | 2637081.3162 | 1219148.6253 | 2637072.2065 | 1219140.6529 | 2637061.0492 | 1219134.9024 | 2637030.2504 | 1219122.7781
71 | 2637085.6589 | 1219151.5492 | 2637088.6161 | 1219153.5403 | 2637099.7935 | 1219156.0446 | 2637112.0129 | 1219154.4975 | 2637122.8223 | 1219151.5186 | 2637128.5475 | 1219147.2961 | 2637128.6486 | 1219147.0545
72 | 2637030.2504 | 1219122.7781 | 2637026.6089 | 1219121.3446
73 | 2636993.6965 | 1219110.014 | 2637005.0086 | 1219112.8414 | 2637026.6089 | 1219121.3446
74 | 2636993.6965 | 1219110.014 | 2636994.0262 | 1219121.7007 | 2636996.449 | 1219134.8124 | 2637020.9557 | 1219217.3465 | 2637025.6839 | 1219241.668 | 2637026.5143 | 1219264.3643 | 2637023.6183 | 1219277.354
75 | 2637023.6183 | 1219277.354 | 2637005.2859 | 1219269.4595
76 | 2637023.6183 | 1219277.354 | 2637029.7517 | 1219280.3652
77 | 2636391.5646 | 1219337.3677 | 2636392.8674 | 1219330.6645
78 | 2636391.5646 | 1219337.3677 | 2636391.1959 | 1219339.2651 | 2636387.1339 | 1219365.4645
79 | 2636392.8674 | 1219330.6645 | 2636394.3296 | 1219323.1414 | 2636394.761 | 1219322.1151
80 | 2636382.6755 | 1219394.2203 | 2636387.1339 | 1219365.4645
81 | 2636412.0789 | 1219294.4995 | 2636405.2434 | 1219301.7064 | 2636398.6647 | 1219312.8284 | 2636394.761 | 1219322.1151
82 | 2636412.0789 | 1219294.4995 | 2636405.7508 | 1219289.4467 | 2636381.8762 | 1219262.3962
83 | 2636412.0789 | 1219294.4995 | 2636423.3879 | 1219300.3053 | 2636524.9984 | 1219359.1613 | 2636576.1157 | 1219387.0688 | 2636602.6902 | 1219398.0717 | 2636628.1182 | 1219404.2203 | 2636664.4929 | 1219409.6137 | 2636665.9422 | 1219409.7908
84 | 2636275.3468 | 1219143.455 | 2636288.1758 | 1219142.7215 | 2636299.762 | 1219145.4381 | 2636304.2029 | 1219148.9116 | 2636306.2954 | 1219155.4504 | 2636303.5058 | 1219161.1924 | 2636297.8688 | 1219167.2283 | 2636279.1167 | 1219178.6209 | 2636256.1603 | 1219200.0718 | 2636241.9491 | 1219218.4851 | 2636240.2237 | 1219225.2008 | 2636241.6169 | 1219230.6903 | 2636245.0537 | 1219234.5579 | 2636251.758 | 1219236.4331 | 2636270.0472 | 1219241.2027 | 2636290.3564 | 1219248.2303 | 2636294.8037 | 1219253.1269 | 2636329.61 | 1219253.339 | 2636357.4761 | 1219255.5323 | 2636372.1125 | 1219258.2676 | 2636381.8762 | 1219262.3962
85 | 2636381.8762 | 1219262.3962 | 2636365.3312 | 1219239.1705 | 2636362.7719 | 1219228.3041 | 2636364.0405 | 1219219.3843 | 2636367.7293 | 1219213.0142 | 2636397.7966 | 1219192.7745 | 2636461.0594 | 1219129.7904 | 2636487.6832 | 1219105.6723 | 2636511.0011 | 1219087.3487 | 2636517.569 | 1219078.0612 | 2636540.6835 | 1219043.1996
86 | 2636689.204 | 1219412.6341 | 2636665.9422 | 1219409.7908
87 | 2636689.204 | 1219412.6341 | 2636685.6292 | 1219415.2247 | 2636682.3278 | 1219421.4859 | 2636676.3559 | 1219433.8342 | 2636668.5614 | 1219442.7138 | 2636649.5202 | 1219461.6635
88 | 2636728.1201 | 1219427.9604 | 2636717.343 | 1219420.8899 | 2636694.1894 | 1219412.6314 | 2636689.204 | 1219412.6341
89 | 2636728.1201 | 1219427.9604 | 2636739.6017 | 1219417.9919 | 2636789.6086 | 1219384.5915 | 2636812.1966 | 1219366.4869 | 2636824.2794 | 1219353.1661
90 | 2636854.508 | 1219317.4414 | 2636832.3133 | 1219344.3091 | 2636824.2794 | 1219353.1661
91 | 2636786.9314 | 1219325.3512 | 2636783.2388 | 1219329.7977 | 2636779.7324 | 1219337.2805 | 2636776.5995 | 1219340.6972
92 | 2636786.9314 | 1219325.3512 | 2636792.8397 | 1219323.3642 | 2636800.5857 | 1219322.3892 | 2636816.2548 | 1219322.4859 | 2636832.5461 | 1219321.3748 | 2636842.5355 | 1219318.3903 | 2636854.508 | 1219317.4414
93 | 2636854.508 | 1219317.4414 | 2636902.805 | 1219258.9611 | 2636914.8099 | 1219250.3525 | 2636924.8079 | 1219246.0118 | 2636938.4619 | 1219244.3732 | 2636953.1291 | 1219246.9989 | 2637005.2859 | 1219269.4595
94 | 2637029.7517 | 1219280.3652 | 2637040.9805 | 1219285.8779 | 2637045.8446 | 1219287.7185
95 | 2637047.0352 | 1219288.169 | 2637045.8446 | 1219287.7185
96 | 2637107.2372 | 1219310.949 | 2637047.0352 | 1219288.169
97 | 2636275.3468 | 1219143.455 | 2636279.1601 | 1219119.1306
98 | 2636180.1055 | 1219188.2252 | 2636198.7304 | 1219191.4846 | 2636208.5111 | 1219189.1092 | 2636215.0527 | 1219185.3022 | 2636226.534 | 1219171.5638 | 2636239.4428 | 1219156.4333 | 2636248.2378 | 1219150.1942 | 2636260.4706 | 1219146.4108 | 2636275.3468 | 1219143.455
99 | 2636554.5485 | 1219022.2881 | 2636540.6835 | 1219043.1996
100 | 2636180.1055 | 1219188.2252 | 2636181.744 | 1219173.3264 | 2636186.7426 | 1219153.6784 | 2636194.5909 | 1219135.8711 | 2636207.722 | 1219117.8847 | 2636224.3098 | 1219101.7536 | 2636247.8094 | 1219085.8648 | 2636259.9584 | 1219077.7015
101 | 2636180.1055 | 1219188.2252 | 2636175.959 | 1219187.4996 | 2636162.9463 | 1219184.7747 | 2636100.9153 | 1219174.9924
102 | 2636084.3236 | 1219171.2636 | 2636100.1136 | 1219174.866 | 2636100.9153 | 1219174.9924
103 | 2636084.3236 | 1219171.2636 | 2636059.867 | 1219165.6838 | 2636049.4248 | 1219161.6527
104 | 2636045.6441 | 1219160.1932 | 2636049.4248 | 1219161.6527
105 | 2636032.2755 | 1219155.0324 | 2636045.6441 | 1219160.1932
106 | 2636032.2755 | 1219155.0324 | 2636022.5053 | 1219151.2607 | 2636009.723 | 1219144.2794 | 2636001.1934 | 1219141.7931 | 2635998.3973 | 1219141.4987
107 | 2635941.7642 | 1219138.6662 | 2635949.1285 | 1219143.1243 | 2635954.7573 | 1219143.4362 | 2635964.4807 | 1219141.7494 | 2635988.9837 | 1219140.5076 | 2635998.3973 | 1219141.4987
108 | 2636569.2521 | 1218389.8308 | 2636574.5556 | 1218393.3513
109 | 2636574.5556 | 1218393.3513 | 2636579.27 | 1218396.4807
110 | 2636581.6577 | 1218398.0657 | 2636579.27 | 1218396.4807
111 | 2636159.9003 | 1218771.0407 | 2636150.4722 | 1218788.8091
112 | 2636578.4421 | 1218408.5707 | 2636582.7716 | 1218398.8052 | 2636581.6577 | 1218398.0657
113 | 2636140.7593 | 1218807.308 | 2636145.8144 | 1218797.5872 | 2636150.4722 | 1218788.8091
114 | 2636140.557 | 1218807.697 | 2636140.7593 | 1218807.308
115 | 2635941.7642 | 1219138.6662 | 2636006.8445 | 1219060.5127 | 2636031.1838 | 1219027.4068 | 2636050.7986 | 1218995.0618 | 2636066.8083 | 1218965.3522 | 2636126.5186 | 1218834.6922 | 2636140.557 | 1218807.697
116 | 2635827.0014 | 1219103.733 | 2635818.1582 | 1219152.164 | 2635814.0712 | 1219188.2607 | 2635813.3207 | 1219210.8695 | 2635813.8799 | 1219220.1116 | 2635815.8748 | 1219225.2933 | 2635817.7579 | 1219227.6171 | 2635819.8294 | 1219230.1644 | 2635854.9744 | 1219210.6863 | 2635879.6506 | 1219197.0155 | 2635904.6449 | 1219178.4216 | 2635928.3893 | 1219154.4505 | 2635941.7642 | 1219138.6662
117 | 2635827.0014 | 1219103.733 | 2635811.9241 | 1219071.9793 | 2635798.7389 | 1219030.9205 | 2635785.2559 | 1218971.1822 | 2635779.4572 | 1218952.3696 | 2635768.376 | 1218932.4137

## bus_geodata
| x | y | coords
0 | 2637662.4151 | 1220577.6222
1 | 2637679.0854 | 1220589.2939
2 | 2637596.705 | 1220545.2545
3 | 2637682.9931 | 1220592.406
4 | 2637580.2001 | 1220538.0293
5 | 2637618.0049 | 1219993.5749
6 | 2637712.7364 | 1219816.8574
7 | 2637565.037 | 1220201.8756
8 | 2637592.9447 | 1219963.4416
9 | 2637706.7766 | 1220619.6736
10 | 2637808.9474 | 1220504.5945
11 | 2637531.4249 | 1220518.8853
12 | 2637691.4131 | 1220672.5492
13 | 2637711.2385 | 1220624.2168
14 | 2637839.349 | 1220509.5571
15 | 2637778.4608 | 1220268.0631
16 | 2637663.4227 | 1220696.0732
17 | 2637721.5571 | 1220635.1017
18 | 2637843.5351 | 1220750.0289
19 | 2637823.9949 | 1220747.9256
20 | 2637876.6108 | 1220753.2738
21 | 2637823.9221 | 1220752.2165
22 | 2637804.8195 | 1220723.5228
23 | 2637877.3102 | 1220757.8143
24 | 2637804.3122 | 1220749.9837
25 | 2637821.8817 | 1220785.0308
26 | 2637838.9911 | 1220753.8971
27 | 2637788.7871 | 1220713.1492
28 | 2637812.0946 | 1220709.3721
29 | 2637879.6445 | 1220773.0689
30 | 2637817.1032 | 1220793.8647
31 | 2637762.018 | 1220682.4551
32 | 2637834.7228 | 1220673.9335
33 | 2637660.0339 | 1220731.4598
34 | 2637614.719 | 1220727.2672
35 | 2637610.0766 | 1220726.8377
36 | 2637641.6731 | 1220694.5957
37 | 2637879.9846 | 1220784.6425
38 | 2637736.6179 | 1220652.7281
39 | 2637839.8353 | 1220667.8896
40 | 2637791.9437 | 1220267.6021
41 | 2637626.6254 | 1220227.2438
42 | 2637604.5075 | 1220213.841
43 | 2636331.4224 | 1217936.211
44 | 2636491.0625 | 1218062.5347
45 | 2636425.8052 | 1218358.1652
46 | 2636318.4856 | 1218554.5041
47 | 2636557.6117 | 1218382.1039
48 | 2636230.5681 | 1218637.8594
49 | 2636568.0532 | 1218389.035
50 | 2637765.4449 | 1220870.833
51 | 2637729.5244 | 1220938.6211
52 | 2637776.2091 | 1220850.6615
53 | 2637727.0502 | 1220943.9986
54 | 2637809.2681 | 1220802.41
55 | 2637591.0611 | 1221137.5286
56 | 2638053.4992 | 1221369.3112
57 | 2637830.4621 | 1220799.0353
58 | 2638067.2017 | 1221379.8838
59 | 2637866.2612 | 1220803.7552
60 | 2637595.4035 | 1219956.0409
61 | 2637602.8205 | 1219933.7166
62 | 2637333.9834 | 1219691.1333
63 | 2637186.3298 | 1219338.8915
64 | 2637236.7285 | 1219300.6462
65 | 2637171.4705 | 1219333.6419
66 | 2637241.8515 | 1219307.759
67 | 2637157.6719 | 1219328.767
68 | 2637257.3999 | 1219325.1691
69 | 2637085.6589 | 1219151.5492
70 | 2637030.2504 | 1219122.7781
71 | 2637128.6486 | 1219147.0545
72 | 2637026.6089 | 1219121.3446
73 | 2636993.6965 | 1219110.014
74 | 2637023.6183 | 1219277.354
75 | 2636391.5646 | 1219337.3677
76 | 2636392.8674 | 1219330.6645
77 | 2636387.1339 | 1219365.4645
78 | 2636394.761 | 1219322.1151
79 | 2636382.6755 | 1219394.2203
80 | 2636412.0789 | 1219294.4995
81 | 2636381.8762 | 1219262.3962
82 | 2636665.9422 | 1219409.7908
83 | 2636649.5202 | 1219461.6635
84 | 2636689.204 | 1219412.6341
85 | 2636728.1201 | 1219427.9604
86 | 2636824.2794 | 1219353.1661
87 | 2636776.5995 | 1219340.6972
88 | 2636786.9314 | 1219325.3512
89 | 2636854.508 | 1219317.4414
90 | 2637029.7517 | 1219280.3652
91 | 2637045.8446 | 1219287.7185
92 | 2637047.0352 | 1219288.169
93 | 2637005.2859 | 1219269.4595
94 | 2637107.2372 | 1219310.949
95 | 2636275.3468 | 1219143.455
96 | 2636540.6835 | 1219043.1996
97 | 2636279.1601 | 1219119.1306
98 | 2636180.1055 | 1219188.2252
99 | 2636554.5485 | 1219022.2881
100 | 2636084.3236 | 1219171.2635
101 | 2636100.9153 | 1219174.9924
102 | 2636049.4248 | 1219161.6527
103 | 2636045.6441 | 1219160.1932
104 | 2636259.9584 | 1219077.7015
105 | 2636032.2755 | 1219155.0324
106 | 2635998.3973 | 1219141.4987
107 | 2636569.2521 | 1218389.8308
108 | 2636574.5556 | 1218393.3513
109 | 2636579.27 | 1218396.4807
110 | 2636159.9003 | 1218771.0407
111 | 2636581.6577 | 1218398.0657
112 | 2636578.4421 | 1218408.5708
113 | 2636150.4722 | 1218788.8091
114 | 2636140.7593 | 1218807.308
115 | 2636140.557 | 1218807.697
116 | 2635941.7642 | 1219138.6662
117 | 2635827.0014 | 1219103.733
118 | 2635768.376 | 1218932.4137
119 | 2637641.6731 | 1220694.5957

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9994 | -0.0044529 | 0.00058826 | 0.00014743
1 | 0.99958 | -0.0031439 | 0.0010829 | 0.00027139
2 | 0.9988 | -0.0090353 | 0.00017632 | 4.4191e-05
3 | 0.99962 | -0.002805 | 0.0002766 | 6.9323e-05
4 | 0.99865 | -0.010147 | 0.00016969 | 4.2529e-05
5 | 0.99139 | -0.06498 | 0.00017991 | 4.5089e-05
6 | 0.98983 | -0.076751 | 0 | 0
7 | 0.99309 | -0.052091 | 0 | 0
8 | 0.99135 | -0.065219 | 0.00010746 | 2.6932e-05
9 | 1 | 0 | -0.2236 | -0.056112
10 | 0.99907 | -0.0066725 | 0.00070494 | 0.00017667
11 | 0.99822 | -0.013358 | 0 | 0
12 | 0.99979 | -0.0015077 | 0.0011224 | 0.00028131
13 | 0.9994 | -0.0041314 | 0.0003155 | 7.9073e-05
14 | 0.99899 | -0.0072291 | 0.0018051 | 0.00045239
15 | 0.99492 | -0.038273 | 0 | 0
16 | 0.9997 | -0.0021423 | 0.00031902 | 7.9954e-05
17 | 0.99799 | -0.01387 | 0.00029764 | 7.4596e-05
18 | 0.98112 | -0.13226 | 0.027032 | 0.0067748
19 | 0.98264 | -0.1215 | 0 | 0
20 | 0.97987 | -0.14119 | 0 | 0
21 | 0.98219 | -0.12467 | 0 | 0
22 | 0.98671 | -0.092602 | 0 | 0
23 | 0.9797 | -0.14243 | 0 | 0
24 | 0.98144 | -0.13005 | 0.026309 | 0.0065937
25 | 0.98031 | -0.13814 | 0.0039881 | 0.00099951
26 | 0.98207 | -0.12556 | 0.0056898 | 0.001426
27 | 0.98841 | -0.080676 | 0.011286 | 0.0028286
28 | 0.98543 | -0.10171 | 0.0077708 | 0.0019475
29 | 0.97912 | -0.14658 | 0.012553 | 0.003146
30 | 0.97978 | -0.14188 | 0 | 0
31 | 0.99218 | -0.054221 | 0.00053852 | 0.00013497
32 | 0.98249 | -0.12259 | 0.0146 | 0.003659
33 | 0.99955 | -0.00317 | 0.00028524 | 7.1489e-05
34 | 0.99957 | -0.0030393 | 0.00092059 | 0.00023072
35 | 0.99958 | -0.0029829 | 0 | 0
36 | 0.99966 | -0.0024136 | 0 | 0
37 | 0.97889 | -0.14819 | 0.0099596 | 0.0024961
38 | 0.99581 | -0.028949 | 0.0023156 | 0.00058033
39 | 0.9821 | -0.12533 | 0.033416 | 0.0083748
40 | 0.99492 | -0.038289 | 0.00011959 | 2.9973e-05
41 | 0.99363 | -0.048024 | 0.00018785 | 4.708e-05
42 | 0.99343 | -0.049579 | 3.8974e-05 | 9.7679e-06
43 | 0.9703 | -0.22463 | 0.0011792 | 0.00029554
44 | 0.97048 | -0.22329 | 0 | 0
45 | 0.97066 | -0.22192 | 0 | 0
46 | 0.97139 | -0.21651 | 0 | 0
47 | 0.97031 | -0.22445 | 0.0010162 | 0.00025468
48 | 0.97178 | -0.21358 | 0.00014422 | 3.6145e-05
49 | 0.97028 | -0.22464 | 0.0014416 | 0.00036129
50 | 0.97907 | -0.14708 | 0.002685 | 0.00067292
51 | 0.97882 | -0.14896 | 0.0012081 | 0.00030277
52 | 0.97924 | -0.14588 | 0 | 0
53 | 0.97881 | -0.14903 | 0.00038159 | 9.5635e-05
54 | 0.97966 | -0.1428 | 0.0025338 | 0.00063502
55 | 0.97842 | -0.15217 | 0 | 0
56 | 0.97784 | -0.15654 | 0 | 0
57 | 0.97919 | -0.14609 | 0.027823 | 0.006973
58 | 0.97782 | -0.15666 | 0.00066388 | 0.00016638
59 | 0.97876 | -0.14914 | 0.0033513 | 0.00083991
60 | 0.99135 | -0.065246 | 5.5009e-05 | 1.3787e-05
61 | 0.99134 | -0.065316 | 0.00028836 | 7.2271e-05
62 | 0.98676 | -0.099987 | 0 | 0
63 | 0.98261 | -0.13134 | 0 | 0
64 | 0.98252 | -0.132 | 0.00010925 | 2.738e-05
65 | 0.9825 | -0.13221 | 9.8917e-05 | 2.4791e-05
66 | 0.98251 | -0.13205 | 0.0004431 | 0.00011105
67 | 0.98239 | -0.13302 | 0.0001354 | 3.3936e-05
68 | 0.98251 | -0.13208 | 0.00013177 | 3.3025e-05
69 | 0.98094 | -0.14384 | 0.0004852 | 0.0001216
70 | 0.98099 | -0.14349 | 0.00049613 | 0.00012434
71 | 0.98094 | -0.14386 | 4.2681e-05 | 1.0697e-05
72 | 0.981 | -0.14345 | 0.00017584 | 4.4071e-05
73 | 0.98106 | -0.14301 | 0 | 0
74 | 0.98136 | -0.14083 | 0 | 0
75 | 0.9769 | -0.17468 | 9.6851e-05 | 2.4273e-05
76 | 0.97691 | -0.17462 | 0.00017108 | 4.2878e-05
77 | 0.97687 | -0.17489 | 0.00016824 | 4.2165e-05
78 | 0.97692 | -0.17453 | 0.00010639 | 2.6665e-05
79 | 0.97685 | -0.17505 | 0.00053681 | 0.00013454
80 | 0.97697 | -0.17415 | 0 | 0
81 | 0.97675 | -0.17587 | 0 | 0
82 | 0.97855 | -0.16212 | 0.00020358 | 5.1022e-05
83 | 0.97857 | -0.16191 | 0.00121 | 0.00030325
84 | 0.97869 | -0.1611 | 0 | 0
85 | 0.97895 | -0.15908 | 0 | 0
86 | 0.97972 | -0.15324 | 0.00013409 | 3.3606e-05
87 | 0.98 | -0.15115 | 0.00018329 | 4.5937e-05
88 | 0.98 | -0.15111 | 0 | 0
89 | 0.98002 | -0.15098 | 0 | 0
90 | 0.98141 | -0.14046 | 8.4619e-05 | 2.1207e-05
91 | 0.98153 | -0.13951 | 5.189e-05 | 1.3005e-05
92 | 0.98154 | -0.13944 | 7.589e-05 | 1.902e-05
93 | 0.98123 | -0.14182 | 0.00013555 | 3.3971e-05
94 | 0.982 | -0.13593 | 0 | 0
95 | 0.97533 | -0.18667 | 0 | 0
96 | 0.9766 | -0.177 | 8.6926e-05 | 2.1786e-05
97 | 0.97532 | -0.18673 | 0.00021329 | 5.3455e-05
98 | 0.97478 | -0.19081 | 0 | 0
99 | 0.97659 | -0.17707 | 0.00025799 | 6.4659e-05
100 | 0.97432 | -0.19429 | 0.00029014 | 7.2716e-05
101 | 0.9744 | -0.19372 | 0.00088765 | 0.00022247
102 | 0.97417 | -0.19545 | 0.00031813 | 7.9732e-05
103 | 0.97415 | -0.19558 | 0.00046641 | 0.00011689
104 | 0.97477 | -0.1909 | 5.0687e-05 | 1.2703e-05
105 | 0.9741 | -0.196 | 0.00012049 | 3.0198e-05
106 | 0.97396 | -0.19706 | 0.00046352 | 0.00011617
107 | 0.97028 | -0.22465 | 0.00066781 | 0.00016737
108 | 0.97028 | -0.2247 | 0.00077211 | 0.00019351
109 | 0.97026 | -0.22478 | 0.00017234 | 4.3191e-05
110 | 0.97226 | -0.20994 | 8.2678e-05 | 2.0721e-05
111 | 0.97026 | -0.22481 | 0.0007242 | 0.0001815
112 | 0.97025 | -0.22487 | 0.00045273 | 0.00011346
113 | 0.97233 | -0.20945 | 0.00020898 | 5.2376e-05
114 | 0.9724 | -0.20892 | 0.0002211 | 5.5412e-05
115 | 0.9724 | -0.20891 | 6.0727e-05 | 1.522e-05
116 | 0.97375 | -0.19864 | 0 | 0
117 | 0.97369 | -0.19916 | 0 | 0
118 | 0.97366 | -0.19945 | 0.0001419 | 3.5563e-05
119 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.018026 | -0.0043488 | 0.018029 | 0.0043492 | 3.0397e-06 | 3.6799e-07 | 0.026781 | 0.026781 | 0.026781 | 0.9994 | -0.0044529 | 0.99958 | -0.0031439 | 3.3063
1 | 0.017438 | 0.0042014 | -0.017428 | -0.0042003 | 1.027e-05 | 1.0596e-06 | 0.025905 | 0.025906 | 0.025906 | 0.9994 | -0.0044529 | 0.9988 | -0.0090353 | 3.1983
2 | -0.019112 | -0.0046206 | 0.019113 | 0.0046207 | 8.3765e-07 | 1.2572e-07 | 0.028393 | 0.028393 | 0.028393 | 0.99958 | -0.0031439 | 0.99962 | -0.002805 | 3.5053
3 | 0.017251 | 0.0041562 | -0.017249 | -0.0041559 | 2.4644e-06 | 2.4054e-07 | 0.025644 | 0.025644 | 0.025644 | 0.9988 | -0.0090353 | 0.99865 | -0.010147 | 3.1659
4 | -0.021901 | -0.0053173 | 0.021909 | 0.0053189 | 8.0064e-06 | 1.6493e-06 | 0.032542 | 0.032542 | 0.032542 | 0.99962 | -0.002805 | 1 | 0 | 4.0175
5 | 0.0025115 | 0.00062722 | -0.0025101 | -0.00062872 | 1.3388e-06 | -1.4968e-06 | 0.0037378 | 0.0037385 | 0.0037385 | 0.99962 | -0.002805 | 0.99907 | -0.0066725 | 1.3846
6 | 0.017079 | 0.0041134 | -0.017072 | -0.0041127 | 7.0446e-06 | 6.4838e-07 | 0.025391 | 0.025392 | 0.025392 | 0.99865 | -0.010147 | 0.99822 | -0.013358 | 3.1348
7 | 0.015983 | 0.003859 | -0.015958 | -0.0038575 | 2.4279e-05 | 1.4717e-06 | 0.023938 | 0.023941 | 0.023941 | 0.99139 | -0.06498 | 0.98983 | -0.076751 | 2.9557
8 | -0.016613 | -0.004016 | 0.016641 | 0.0040183 | 2.768e-05 | 2.3178e-06 | 0.024884 | 0.024882 | 0.024884 | 0.99139 | -0.06498 | 0.99309 | -0.052091 | 3.0722
9 | 0.00045085 | 0.00011193 | -0.00045084 | -0.00011259 | 1.4727e-08 | -6.5938e-07 | 0.00067633 | 0.00067656 | 0.00067656 | 0.99139 | -0.06498 | 0.99135 | -0.065219 | 0.25058
10 | 0.015958 | 0.0038575 | -0.01591 | -0.0038546 | 4.7963e-05 | 2.985e-06 | 0.023941 | 0.023946 | 0.023946 | 0.98983 | -0.076751 | 0.98676 | -0.099987 | 2.9563
11 | -0.016641 | -0.0040183 | 0.016647 | 0.0040188 | 5.395e-06 | 4.4819e-07 | 0.024882 | 0.024881 | 0.024882 | 0.99309 | -0.052091 | 0.99343 | -0.049579 | 3.0718
12 | 0.00034338 | 8.5655e-05 | -0.00034337 | -8.5755e-05 | 1.2921e-09 | -1.0005e-07 | 0.00051526 | 0.0005153 | 0.0005153 | 0.99135 | -0.065219 | 0.99135 | -0.065246 | 0.19085
13 | 0.0026481 | 0.00066095 | -0.0026476 | -0.00066148 | 5.4873e-07 | -5.321e-07 | 0.0039395 | 0.0039398 | 0.0039398 | 1 | 0 | 0.99979 | -0.0015077 | 1.4592
14 | 0.19824 | 0.050132 | -0.19813 | -0.050088 | 0.00011538 | 4.4127e-05 | 0.29515 | 0.29515 | 0.29515 | 1 | 0 | 0.9994 | -0.0041314 | 36.438
15 | 0.0018052 | 0.00045204 | -0.0018051 | -0.00045239 | 1.3898e-07 | -3.4999e-07 | 0.0026885 | 0.0026887 | 0.0026887 | 0.99907 | -0.0066725 | 0.99899 | -0.0072291 | 0.99581
16 | 0.017072 | 0.0041127 | -0.017018 | -0.0041076 | 5.4664e-05 | 5.0947e-06 | 0.025392 | 0.025397 | 0.025397 | 0.99822 | -0.013358 | 0.99492 | -0.038273 | 3.1354
17 | 0.0015251 | 0.00038017 | -0.001525 | -0.00038066 | 1.3272e-07 | -4.9054e-07 | 0.0022692 | 0.0022694 | 0.0022694 | 0.99979 | -0.0015077 | 0.9997 | -0.0021423 | 0.84051
18 | 0.19781 | 0.050009 | -0.19754 | -0.049905 | 0.00027102 | 0.00010365 | 0.29468 | 0.29468 | 0.29468 | 0.9994 | -0.0041314 | 0.99799 | -0.01387 | 36.38
19 | 0.0001196 | 2.9798e-05 | -0.00011959 | -2.9973e-05 | 2.6923e-10 | -1.7509e-07 | 0.00017881 | 0.00017887 | 0.00017887 | 0.99492 | -0.038273 | 0.99492 | -0.038289 | 0.066247
20 | 0.016898 | 0.0040778 | -0.016877 | -0.0040759 | 2.1241e-05 | 1.9223e-06 | 0.025218 | 0.02522 | 0.02522 | 0.99492 | -0.038273 | 0.99363 | -0.048024 | 3.1136
21 | 0.001206 | 0.0003007 | -0.0012059 | -0.00030098 | 4.4887e-08 | -2.7558e-07 | 0.0017945 | 0.0017946 | 0.0017946 | 0.9997 | -0.0021423 | 0.99966 | -0.0024136 | 0.66468
22 | 0.19724 | 0.04983 | -0.19683 | -0.049671 | 0.00041749 | 0.00015967 | 0.29423 | 0.29423 | 0.29423 | 0.99799 | -0.01387 | 0.99581 | -0.028949 | 36.3253
23 | -0.05295 | -0.013277 | 0.053029 | 0.013307 | 7.9094e-05 | 3.0172e-05 | 0.080309 | 0.080309 | 0.080309 | 0.98112 | -0.13226 | 0.98264 | -0.1215 | 29.744
24 | 0.025918 | 0.0065019 | -0.025886 | -0.00649 | 3.2049e-05 | 1.1907e-05 | 0.039311 | 0.039311 | 0.039311 | 0.98112 | -0.13226 | 0.97987 | -0.14119 | 14.5597
25 | 0.071447 | 0.017912 | -0.071415 | -0.0179 | 3.1351e-05 | 1.2004e-05 | 0.10819 | 0.10819 | 0.10819 | 0.98264 | -0.1215 | 0.98219 | -0.12467 | 40.072
26 | -0.12448 | -0.031219 | 0.12498 | 0.03141 | 0.00050073 | 0.00019144 | 0.1885 | 0.1885 | 0.1885 | 0.98264 | -0.1215 | 0.98671 | -0.092602 | 34.908
27 | 0.025886 | 0.00649 | -0.025882 | -0.0064884 | 4.431e-06 | 1.6464e-06 | 0.039311 | 0.039311 | 0.039311 | 0.97987 | -0.14119 | 0.9797 | -0.14243 | 14.5597
28 | 0.026329 | 0.006601 | -0.026309 | -0.0065937 | 1.9596e-05 | 7.2873e-06 | 0.039889 | 0.039889 | 0.039889 | 0.98219 | -0.12467 | 0.98144 | -0.13005 | 14.7737
29 | 0.039396 | 0.0098728 | -0.039322 | -0.009845 | 7.3295e-05 | 2.7774e-05 | 0.059684 | 0.059684 | 0.059684 | 0.98219 | -0.12467 | 0.98031 | -0.13814 | 22.1053
30 | 0.0056905 | 0.0014261 | -0.0056898 | -0.001426 | 7.0321e-07 | 7.8591e-08 | 0.0086211 | 0.0086212 | 0.0086212 | 0.98219 | -0.12467 | 0.98207 | -0.12556 | 3.193
31 | -0.18099 | -0.045476 | 0.18129 | 0.045591 | 0.00030087 | 0.00011498 | 0.27298 | 0.27298 | 0.27298 | 0.98671 | -0.092602 | 0.98841 | -0.080676 | 33.7009
32 | 0.056009 | 0.014066 | -0.055938 | -0.014039 | 7.0852e-05 | 2.7048e-05 | 0.084475 | 0.084475 | 0.084475 | 0.98671 | -0.092602 | 0.98543 | -0.10171 | 31.287
33 | 0.025882 | 0.0064884 | -0.025867 | -0.0064828 | 1.4881e-05 | 5.5294e-06 | 0.039311 | 0.039311 | 0.039311 | 0.9797 | -0.14243 | 0.97912 | -0.14658 | 14.5598
34 | 0.035334 | 0.0088455 | -0.035316 | -0.0088386 | 1.8281e-05 | 6.9027e-06 | 0.053631 | 0.053631 | 0.053631 | 0.98031 | -0.13814 | 0.97978 | -0.14188 | 19.8632
35 | -0.19257 | -0.04842 | 0.19329 | 0.048692 | 0.00071253 | 0.00027248 | 0.28997 | 0.28997 | 0.28997 | 0.98841 | -0.080676 | 0.99218 | -0.054221 | 35.7986
36 | 0.048167 | 0.012092 | -0.048028 | -0.012039 | 0.00013927 | 5.303e-05 | 0.072741 | 0.072741 | 0.072741 | 0.98543 | -0.10171 | 0.98249 | -0.12259 | 26.9411
37 | 0.013314 | 0.0033368 | -0.013311 | -0.0033358 | 2.9647e-06 | 9.9434e-07 | 0.020234 | 0.020234 | 0.020234 | 0.97912 | -0.14658 | 0.97889 | -0.14819 | 7.4942
38 | 0.027839 | 0.006979 | -0.027823 | -0.006973 | 1.6213e-05 | 6.0527e-06 | 0.04228 | 0.04228 | 0.04228 | 0.97978 | -0.14188 | 0.97919 | -0.14609 | 15.6593
39 | 0.0074773 | 0.0018595 | -0.0074763 | -0.0018593 | 9.3208e-07 | 2.125e-07 | 0.011351 | 0.011351 | 0.011351 | 0.97978 | -0.14188 | 0.97966 | -0.1428 | 4.204
40 | -0.19382 | -0.048827 | 0.19451 | 0.04909 | 0.00068764 | 0.00026296 | 0.29078 | 0.29077 | 0.29078 | 0.99218 | -0.054221 | 0.99581 | -0.028949 | 35.8982
41 | 0.033428 | 0.0083796 | -0.033416 | -0.0083748 | 1.2662e-05 | 4.7698e-06 | 0.050629 | 0.050629 | 0.050629 | 0.98249 | -0.12259 | 0.9821 | -0.12533 | 18.7516
42 | -0.00028524 | -7.1489e-05 | 0.00028525 | 7.0895e-05 | 5.118e-09 | -5.9454e-07 | 0.00042464 | 0.00042443 | 0.00042464 | 0.99955 | -0.00317 | 0.99957 | -0.0030393 | 0.15727
43 | -0.0012058 | -0.00030162 | 0.0012058 | 0.00030156 | 9.3722e-09 | -5.7508e-08 | 0.0017949 | 0.0017949 | 0.0017949 | 0.99957 | -0.0030393 | 0.99958 | -0.0029829 | 0.66477
44 | -0.0012058 | -0.00030156 | 0.0012059 | 0.00030098 | 9.4449e-08 | -5.7968e-07 | 0.0017949 | 0.0017946 | 0.0017949 | 0.99958 | -0.0029829 | 0.99966 | -0.0024136 | 0.66476
45 | 0.0033517 | 0.00083974 | -0.0033513 | -0.00083991 | 4.4141e-07 | -1.7276e-07 | 0.0050949 | 0.005095 | 0.005095 | 0.97889 | -0.14819 | 0.97876 | -0.14914 | 1.887
46 | 0.016689 | 0.0040288 | -0.016686 | -0.0040286 | 3.346e-06 | 2.8211e-07 | 0.024939 | 0.024939 | 0.024939 | 0.99363 | -0.048024 | 0.99343 | -0.049579 | 3.0789
47 | -0.0011792 | -0.00029554 | 0.0011794 | 0.00029042 | 2.1454e-07 | -5.118e-06 | 0.0018084 | 0.0018065 | 0.0018084 | 0.9703 | -0.22463 | 0.97048 | -0.22329 | 0.33489
48 | -0.0011794 | -0.00029042 | 0.0011796 | 0.00027909 | 2.0847e-07 | -1.1331e-05 | 0.0018065 | 0.0018026 | 0.0018065 | 0.97048 | -0.22329 | 0.97066 | -0.22192 | 0.22303
49 | -0.0064285 | -0.0015888 | 0.0064332 | 0.001582 | 4.667e-06 | -6.795e-06 | 0.0098469 | 0.0098439 | 0.0098469 | 0.97066 | -0.22192 | 0.97139 | -0.21651 | 1.2157
50 | 0.0052489 | 0.0013097 | -0.0052471 | -0.0013141 | 1.8268e-06 | -4.3272e-06 | 0.0080445 | 0.0080463 | 0.0080463 | 0.97066 | -0.22192 | 0.97031 | -0.22445 | 0.99337
51 | -0.0064332 | -0.001582 | 0.0064357 | 0.0015784 | 2.5085e-06 | -3.6598e-06 | 0.0098439 | 0.0098422 | 0.0098439 | 0.97139 | -0.21651 | 0.97178 | -0.21358 | 1.2153
52 | 0.0042309 | 0.0010594 | -0.0042308 | -0.0010598 | 1.0973e-07 | -4.2219e-07 | 0.0064879 | 0.0064881 | 0.0064881 | 0.97031 | -0.22445 | 0.97028 | -0.22464 | 0.801
53 | -0.0065799 | -0.0016145 | 0.0065831 | 0.0016101 | 3.175e-06 | -4.3853e-06 | 0.010063 | 0.010061 | 0.010063 | 0.97178 | -0.21358 | 0.97226 | -0.20994 | 1.2424
54 | 0.0027892 | 0.00069851 | -0.0027892 | -0.00069856 | 5.4761e-09 | -5.1213e-08 | 0.0042773 | 0.0042773 | 0.0042773 | 0.97028 | -0.22464 | 0.97028 | -0.22465 | 0.52807
55 | 0.0022548 | 0.00055132 | -0.0022542 | -0.00055207 | 5.6067e-07 | -7.4898e-07 | 0.003422 | 0.0034223 | 0.0034223 | 0.97907 | -0.14708 | 0.97882 | -0.14896 | 1.2675
56 | -0.0049397 | -0.0012242 | 0.0049405 | 0.0012243 | 8.0307e-07 | 2.1291e-08 | 0.0075026 | 0.0075025 | 0.0075026 | 0.97907 | -0.14708 | 0.97924 | -0.14588 | 2.7787
57 | 0.0010461 | 0.00024929 | -0.0010461 | -0.00024937 | 9.2892e-09 | -7.083e-08 | 0.0015858 | 0.0015859 | 0.0015859 | 0.97882 | -0.14896 | 0.97881 | -0.14903 | 0.58735
58 | -0.0049405 | -0.0012243 | 0.0049426 | 0.0012243 | 2.0607e-06 | 5.4155e-08 | 0.0075025 | 0.0075022 | 0.0075025 | 0.97924 | -0.14588 | 0.97966 | -0.1428 | 2.7787
59 | 0.00066453 | 0.00015373 | -0.00066427 | -0.00015875 | 2.5737e-07 | -5.0147e-06 | 0.0010058 | 0.0010075 | 0.0010075 | 0.97881 | -0.14903 | 0.97842 | -0.15217 | 0.37316
60 | 0.00066427 | 0.00015875 | -0.00066389 | -0.00016617 | 3.8317e-07 | -7.4254e-06 | 0.0010075 | 0.0010102 | 0.0010102 | 0.97842 | -0.15217 | 0.97784 | -0.15654 | 0.37415
61 | 0.00066389 | 0.00016617 | -0.00066388 | -0.00016638 | 1.1022e-08 | -2.1286e-07 | 0.0010102 | 0.0010103 | 0.0010103 | 0.97784 | -0.15654 | 0.97782 | -0.15666 | 0.37417
62 | 0.00028837 | 7.1968e-05 | -0.00028836 | -7.2271e-05 | 2.7494e-09 | -3.0224e-07 | 0.00043273 | 0.00043284 | 0.00043284 | 0.99135 | -0.065246 | 0.99134 | -0.065316 | 0.16031
63 | 0.01591 | 0.0038546 | -0.015846 | -0.0038504 | 6.4798e-05 | 4.1958e-06 | 0.023946 | 0.023953 | 0.023953 | 0.98676 | -0.099987 | 0.98261 | -0.13134 | 2.9572
64 | 0.00068418 | 0.00016991 | -0.00068412 | -0.00017105 | 6.1583e-08 | -1.1415e-06 | 0.0010355 | 0.001036 | 0.001036 | 0.98261 | -0.13134 | 0.98252 | -0.132 | 0.38369
65 | 0.015161 | 0.0036805 | -0.01516 | -0.0036804 | 1.7217e-06 | 6.3381e-08 | 0.022918 | 0.022918 | 0.022918 | 0.98261 | -0.13134 | 0.9825 | -0.13221 | 2.8294
66 | 0.00057487 | 0.00014367 | -0.00057487 | -0.00014378 | 4.145e-09 | -1.0942e-07 | 0.0008705 | 0.00087054 | 0.00087054 | 0.98252 | -0.132 | 0.98251 | -0.13205 | 0.32242
67 | 0.015061 | 0.0036556 | -0.015059 | -0.0036555 | 1.578e-06 | 5.098e-08 | 0.022768 | 0.022768 | 0.022768 | 0.9825 | -0.13221 | 0.98239 | -0.13302 | 2.8109
68 | 0.00013177 | 3.2728e-05 | -0.00013177 | -3.3025e-05 | 5.8357e-10 | -2.973e-07 | 0.00019946 | 0.00019957 | 0.00019957 | 0.98251 | -0.13205 | 0.98251 | -0.13208 | 0.073915
69 | 0.014924 | 0.0036216 | -0.014918 | -0.0036215 | 5.6644e-06 | 1.4765e-07 | 0.022563 | 0.022564 | 0.022564 | 0.98239 | -0.13302 | 0.982 | -0.13593 | 2.7857
70 | -0.00052788 | -0.00013172 | 0.00052791 | 0.00013093 | 2.5182e-08 | -7.8557e-07 | 0.00080055 | 0.00080027 | 0.00080055 | 0.98094 | -0.14384 | 0.98099 | -0.14349 | 0.2965
71 | 4.2682e-05 | 1.0117e-05 | -4.2681e-05 | -1.0697e-05 | 1.1975e-10 | -5.7971e-07 | 6.4543e-05 | 6.4745e-05 | 6.4745e-05 | 0.98094 | -0.14384 | 0.98094 | -0.14386 | 0.02398
72 | -0.001024 | -0.00025528 | 0.001024 | 0.00025523 | 5.8884e-09 | -4.7145e-08 | 0.0015528 | 0.0015528 | 0.0015528 | 0.98099 | -0.14349 | 0.981 | -0.14345 | 0.57512
73 | -0.0011999 | -0.0002993 | 0.0012 | 0.00029889 | 7.2039e-08 | -4.1262e-07 | 0.0018195 | 0.0018194 | 0.0018195 | 0.981 | -0.14345 | 0.98106 | -0.14301 | 0.6739
74 | -0.0012 | -0.00029889 | 0.0012003 | 0.00029685 | 3.5496e-07 | -2.035e-06 | 0.0018194 | 0.0018186 | 0.0018194 | 0.98106 | -0.14301 | 0.98136 | -0.14083 | 0.67385
75 | 0.013496 | 0.0032711 | -0.013494 | -0.0032712 | 1.7319e-06 | -9.033e-08 | 0.020425 | 0.020425 | 0.020425 | 0.98136 | -0.14083 | 0.98123 | -0.14182 | 2.5216
76 | -0.014696 | -0.003568 | 0.014697 | 0.003568 | 7.0315e-07 | 1.1442e-08 | 0.022243 | 0.022243 | 0.022243 | 0.98136 | -0.14083 | 0.98141 | -0.14046 | 2.7461
77 | -0.00080193 | -0.00020027 | 0.00080194 | 0.00020018 | 6.3551e-09 | -8.3053e-08 | 0.0012212 | 0.0012212 | 0.0012212 | 0.9769 | -0.17468 | 0.97691 | -0.17462 | 0.45231
78 | 0.00070508 | 0.00017599 | -0.00070506 | -0.00017634 | 2.0466e-08 | -3.4826e-07 | 0.0010737 | 0.0010739 | 0.0010739 | 0.9769 | -0.17468 | 0.97687 | -0.17489 | 0.39772
79 | -0.00097302 | -0.00024306 | 0.00097304 | 0.00024296 | 1.2026e-08 | -1.0527e-07 | 0.0014818 | 0.0014818 | 0.0014818 | 0.97691 | -0.17462 | 0.97692 | -0.17453 | 0.54882
80 | 0.00053682 | 0.00013418 | -0.00053681 | -0.00013454 | 1.2139e-08 | -3.5963e-07 | 0.00081758 | 0.00081771 | 0.00081771 | 0.97687 | -0.17489 | 0.97685 | -0.17505 | 0.30286
81 | -0.0010794 | -0.00026962 | 0.0010795 | 0.00026923 | 5.5518e-08 | -3.9096e-07 | 0.0016438 | 0.0016437 | 0.0016438 | 0.97692 | -0.17453 | 0.97697 | -0.17415 | 0.60882
82 | 0.010495 | 0.0025423 | -0.010493 | -0.002543 | 2.3359e-06 | -7.586e-07 | 0.015954 | 0.015955 | 0.015955 | 0.97697 | -0.17415 | 0.97675 | -0.17587 | 1.9697
83 | -0.011575 | -0.0028115 | 0.011593 | 0.0028079 | 1.8131e-05 | -3.6198e-06 | 0.017598 | 0.017594 | 0.017598 | 0.97697 | -0.17415 | 0.97855 | -0.16212 | 2.1726
84 | 0.010148 | 0.0024606 | -0.010134 | -0.002466 | 1.4292e-05 | -5.3204e-06 | 0.015431 | 0.015434 | 0.015434 | 0.97675 | -0.17587 | 0.97533 | -0.18667 | 1.9055
85 | 0.00034497 | 8.2393e-05 | -0.00034492 | -8.6132e-05 | 5.1611e-08 | -3.7388e-06 | 0.00052412 | 0.00052543 | 0.00052543 | 0.97675 | -0.17587 | 0.9766 | -0.177 | 0.19461
86 | -0.011797 | -0.0028589 | 0.011798 | 0.0028586 | 1.5624e-06 | -2.8239e-07 | 0.017904 | 0.017903 | 0.017904 | 0.97855 | -0.16212 | 0.97869 | -0.1611 | 2.2103
87 | -0.00121 | -0.00030325 | 0.0012101 | 0.0003025 | 1.3494e-07 | -7.5083e-07 | 0.0018399 | 0.0018396 | 0.0018399 | 0.97857 | -0.16191 | 0.97869 | -0.1611 | 0.68145
88 | -0.013008 | -0.0031611 | 0.013012 | 0.0031609 | 3.4338e-06 | -2.7642e-07 | 0.019743 | 0.019742 | 0.019743 | 0.97869 | -0.1611 | 0.97895 | -0.15908 | 2.4374
89 | -0.013012 | -0.0031609 | 0.013022 | 0.0031601 | 9.9119e-06 | -8.0332e-07 | 0.019742 | 0.019741 | 0.019742 | 0.97895 | -0.15908 | 0.97972 | -0.15324 | 2.4373
90 | -0.013156 | -0.0031937 | 0.013159 | 0.0031934 | 3.8726e-06 | -2.7935e-07 | 0.019944 | 0.019944 | 0.019944 | 0.97972 | -0.15324 | 0.98002 | -0.15098 | 2.4623
91 | -0.00018329 | -4.5937e-05 | 0.00018329 | 4.5702e-05 | 9.0251e-10 | -2.3501e-07 | 0.00027831 | 0.00027822 | 0.00027831 | 0.98 | -0.15115 | 0.98 | -0.15111 | 0.10308
92 | -0.00018329 | -4.5702e-05 | 0.0001833 | 4.4843e-05 | 3.2945e-09 | -8.5908e-07 | 0.00027822 | 0.00027792 | 0.00027822 | 0.98 | -0.15111 | 0.98002 | -0.15098 | 0.10305
93 | -0.013343 | -0.0032382 | 0.013359 | 0.0032373 | 1.59e-05 | -9.6058e-07 | 0.020222 | 0.020219 | 0.020222 | 0.98002 | -0.15098 | 0.98123 | -0.14182 | 2.4965
94 | -0.014782 | -0.0035892 | 0.014783 | 0.0035893 | 1.8436e-06 | 3.7636e-08 | 0.022371 | 0.022371 | 0.022371 | 0.98141 | -0.14046 | 0.98153 | -0.13951 | 2.7619
95 | -0.014835 | -0.0036023 | 0.014835 | 0.0036023 | 1.3345e-07 | 3.0573e-09 | 0.02245 | 0.02245 | 0.02245 | 0.98153 | -0.13951 | 0.98154 | -0.13944 | 2.7716
96 | -0.014911 | -0.0036213 | 0.014918 | 0.0036215 | 6.8168e-06 | 1.7997e-07 | 0.022565 | 0.022564 | 0.022565 | 0.98154 | -0.13944 | 0.982 | -0.13593 | 2.7858
97 | 0.00021329 | 5.3148e-05 | -0.00021329 | -5.3455e-05 | 1.6265e-09 | -3.0668e-07 | 0.00032529 | 0.0003254 | 0.0003254 | 0.97533 | -0.18667 | 0.97532 | -0.18673 | 0.12052
98 | 0.0099204 | 0.0024128 | -0.009915 | -0.002415 | 5.3704e-06 | -2.1661e-06 | 0.015109 | 0.015111 | 0.015111 | 0.97533 | -0.18667 | 0.97478 | -0.19081 | 1.8655
99 | 0.00025799 | 6.4346e-05 | -0.00025799 | -6.4659e-05 | 2.4186e-09 | -3.1301e-07 | 0.00039299 | 0.0003931 | 0.0003931 | 0.9766 | -0.177 | 0.97659 | -0.17707 | 0.14559
100 | 5.0687e-05 | 1.0919e-05 | -5.0687e-05 | -1.2703e-05 | 5.3044e-10 | -1.7841e-06 | 7.6775e-05 | 7.7375e-05 | 7.7375e-05 | 0.97478 | -0.19081 | 0.97477 | -0.1909 | 0.028657
101 | 0.0098644 | 0.0024041 | -0.0098606 | -0.0024056 | 3.7754e-06 | -1.5499e-06 | 0.015034 | 0.015035 | 0.015035 | 0.97478 | -0.19081 | 0.9744 | -0.19372 | 1.8562
102 | -0.0089723 | -0.0021835 | 0.0089729 | 0.0021832 | 6.6197e-07 | -3.8088e-07 | 0.01368 | 0.013679 | 0.01368 | 0.97432 | -0.19429 | 0.9744 | -0.19372 | 1.6888
103 | 0.0086821 | 0.0021108 | -0.0086808 | -0.0021117 | 1.3221e-06 | -8.4673e-07 | 0.013236 | 0.013237 | 0.013237 | 0.97432 | -0.19429 | 0.97417 | -0.19545 | 1.6342
104 | 0.0083627 | 0.0020319 | -0.0083625 | -0.002032 | 1.3706e-07 | -9.8654e-08 | 0.012751 | 0.012751 | 0.012751 | 0.97417 | -0.19545 | 0.97415 | -0.19558 | 1.5742
105 | 0.0078961 | 0.0019151 | -0.0078957 | -0.0019155 | 4.3199e-07 | -3.6904e-07 | 0.012039 | 0.012039 | 0.012039 | 0.97415 | -0.19558 | 0.9741 | -0.196 | 1.4863
106 | 0.0077752 | 0.0018853 | -0.0077741 | -0.0018863 | 1.0738e-06 | -9.5863e-07 | 0.011855 | 0.011855 | 0.011855 | 0.9741 | -0.196 | 0.97396 | -0.19706 | 1.4636
107 | 0.0073106 | 0.0017701 | -0.0073091 | -0.0017717 | 1.5021e-06 | -1.5915e-06 | 0.011147 | 0.011148 | 0.011148 | 0.97396 | -0.19706 | 0.97375 | -0.19864 | 1.3763
108 | 0.0021214 | 0.00053119 | -0.0021214 | -0.00053142 | 1.4013e-08 | -2.3047e-07 | 0.0032532 | 0.0032533 | 0.0032533 | 0.97028 | -0.22465 | 0.97028 | -0.2247 | 0.40164
109 | 0.0013493 | 0.00033791 | -0.0013493 | -0.00033798 | 1.5118e-08 | -6.4073e-08 | 0.0020692 | 0.0020692 | 0.0020692 | 0.97028 | -0.2247 | 0.97026 | -0.22478 | 0.76637
110 | 0.0011769 | 0.00029478 | -0.0011769 | -0.00029482 | 5.8258e-09 | -3.3155e-08 | 0.0018049 | 0.0018049 | 0.0018049 | 0.97026 | -0.22478 | 0.97026 | -0.22481 | 0.66849
111 | -0.0066658 | -0.0016308 | 0.0066662 | 0.0016303 | 4.3422e-07 | -5.8141e-07 | 0.010188 | 0.010187 | 0.010188 | 0.97226 | -0.20994 | 0.97233 | -0.20945 | 1.2577
112 | 0.00045273 | 0.00011332 | -0.00045273 | -0.00011346 | 3.6154e-09 | -1.4705e-07 | 0.00069427 | 0.00069432 | 0.00069432 | 0.97026 | -0.22481 | 0.97025 | -0.22487 | 0.25716
113 | -0.0068752 | -0.0016826 | 0.0068757 | 0.001682 | 4.7978e-07 | -5.9298e-07 | 0.010507 | 0.010507 | 0.010507 | 0.97233 | -0.20945 | 0.9724 | -0.20892 | 1.2972
114 | -0.0070968 | -0.0017375 | 0.0070968 | 0.0017374 | 1.0726e-08 | -1.2191e-08 | 0.010845 | 0.010845 | 0.010845 | 0.9724 | -0.20892 | 0.9724 | -0.20891 | 1.3389
115 | -0.0071575 | -0.0017527 | 0.0071672 | 0.0017419 | 9.6624e-06 | -1.076e-05 | 0.010938 | 0.010933 | 0.010938 | 0.9724 | -0.20891 | 0.97375 | -0.19864 | 1.3504
116 | 0.00014191 | 2.9781e-05 | -0.0001419 | -3.3301e-05 | 8.2069e-09 | -3.52e-06 | 0.00021494 | 0.00021607 | 0.00021607 | 0.97375 | -0.19864 | 0.97369 | -0.19916 | 0.080025
117 | 0.0001419 | 3.3301e-05 | -0.0001419 | -3.5563e-05 | 5.322e-09 | -2.262e-06 | 0.00021607 | 0.00021686 | 0.00021686 | 0.97369 | -0.19916 | 0.97366 | -0.19945 | 0.080318

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2236 | 0.056112

## res_load
| p_mw | q_mvar
0 | 0.00058826 | 0.00014743
1 | 0.0010829 | 0.00027139
2 | 0.00017632 | 4.4191e-05
3 | 0.0002766 | 6.9323e-05
4 | 0.00016969 | 4.2529e-05
5 | 0.00017991 | 4.5089e-05
6 | 0.00010746 | 2.6932e-05
7 | 0.00070494 | 0.00017667
8 | 0.0011224 | 0.00028131
9 | 0.0003155 | 7.9073e-05
10 | 0.0018051 | 0.00045239
11 | 0.00031902 | 7.9954e-05
12 | 0.00029764 | 7.4596e-05
13 | 0.027032 | 0.0067748
14 | 0.026309 | 0.0065937
15 | 0.0039881 | 0.00099951
16 | 0.0056898 | 0.001426
17 | 0.011286 | 0.0028286
18 | 0.0077708 | 0.0019475
19 | 0.012553 | 0.003146
20 | 0.00053852 | 0.00013497
21 | 0.0146 | 0.003659
22 | 0.00028524 | 7.1489e-05
23 | 0.00092059 | 0.00023072
24 | 0.0099596 | 0.0024961
25 | 0.0023156 | 0.00058033
26 | 0.033416 | 0.0083748
27 | 0.00011959 | 2.9973e-05
28 | 0.00018785 | 4.708e-05
29 | 3.8974e-05 | 9.7679e-06
30 | 0.0011792 | 0.00029554
31 | 0.0010162 | 0.00025468
32 | 0.00014422 | 3.6145e-05
33 | 0.0014416 | 0.00036129
34 | 0.002685 | 0.00067292
35 | 0.0012081 | 0.00030277
36 | 0.00038159 | 9.5635e-05
37 | 0.0025338 | 0.00063502
38 | 0.027823 | 0.006973
39 | 0.00066388 | 0.00016638
40 | 0.0033513 | 0.00083991
41 | 5.5009e-05 | 1.3787e-05
42 | 0.00028836 | 7.2271e-05
43 | 0.00010925 | 2.738e-05
44 | 9.8917e-05 | 2.4791e-05
45 | 0.0004431 | 0.00011105
46 | 0.0001354 | 3.3936e-05
47 | 0.00013177 | 3.3025e-05
48 | 0.0004852 | 0.0001216
49 | 0.00049613 | 0.00012434
50 | 4.2681e-05 | 1.0697e-05
51 | 0.00017584 | 4.4071e-05
52 | 9.6851e-05 | 2.4273e-05
53 | 0.00017108 | 4.2878e-05
54 | 0.00016824 | 4.2165e-05
55 | 0.00010639 | 2.6665e-05
56 | 0.00053681 | 0.00013454
57 | 0.00020358 | 5.1022e-05
58 | 0.00121 | 0.00030325
59 | 0.00013409 | 3.3606e-05
60 | 0.00018329 | 4.5937e-05
61 | 8.4619e-05 | 2.1207e-05
62 | 5.189e-05 | 1.3005e-05
63 | 7.589e-05 | 1.902e-05
64 | 0.00013555 | 3.3971e-05
65 | 8.6926e-05 | 2.1786e-05
66 | 0.00021329 | 5.3455e-05
67 | 0.00025799 | 6.4659e-05
68 | 0.00029014 | 7.2716e-05
69 | 0.00088765 | 0.00022247
70 | 0.00031813 | 7.9732e-05
71 | 0.00046641 | 0.00011689
72 | 5.0687e-05 | 1.2703e-05
73 | 0.00012049 | 3.0198e-05
74 | 0.00046352 | 0.00011617
75 | 0.00066781 | 0.00016737
76 | 0.00077211 | 0.00019351
77 | 0.00017234 | 4.3191e-05
78 | 8.2678e-05 | 2.0721e-05
79 | 0.0007242 | 0.0001815
80 | 0.00045273 | 0.00011346
81 | 0.00020898 | 5.2376e-05
82 | 0.0002211 | 5.5412e-05
83 | 6.0727e-05 | 1.522e-05
84 | 0.0001419 | 3.5563e-05

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1