## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1150-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1150-6_0_3_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1150-6_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1150-6_0_3_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1150-6_0_3_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_1150-6_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1150-6_0_3_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1150-6_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1150-6_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1150-6_0_3_node_78 | 0.4 | n |  | TRUE
10 | bus_LV_1150-6_0_3_node_75 | 0.4 | n |  | TRUE
11 | bus_LV_1150-6_0_3_node_76 | 0.4 | n |  | TRUE
12 | bus_LV_1150-6_0_3_node_10 | 0.4 | n |  | TRUE
13 | bus_LV_1150-6_0_3_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1150-6_0_3_node_52 | 0.4 | n |  | TRUE
15 | bus_LV_1150-6_0_3_node_53 | 0.4 | n |  | TRUE
16 | bus_LV_1150-6_0_3_node_54 | 0.4 | n |  | TRUE
17 | bus_LV_1150-6_0_3_node_55 | 0.4 | n |  | TRUE
18 | bus_LV_1150-6_0_3_node_51 | 0.4 | n |  | TRUE
19 | bus_LV_1150-6_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1150-6_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1150-6_0_3_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1150-6_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1150-6_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1150-6_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1150-6_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_1150-6_0_3_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_1150-6_0_3_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_1150-6_0_3_node_63 | 0.4 | n |  | TRUE
29 | bus_LV_1150-6_0_3_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1150-6_0_3_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1150-6_0_3_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_1150-6_0_3_node_39 | 0.4 | n |  | TRUE
33 | bus_LV_1150-6_0_3_node_56 | 0.4 | n |  | TRUE
34 | bus_LV_1150-6_0_3_node_71 | 0.4 | n |  | TRUE
35 | bus_LV_1150-6_0_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_1150-6_0_3_node_58 | 0.4 | n |  | TRUE
37 | bus_LV_1150-6_0_3_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_1150-6_0_3_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_1150-6_0_3_node_32 | 0.4 | n |  | TRUE
40 | bus_LV_1150-6_0_3_node_50 | 0.4 | n |  | TRUE
41 | bus_LV_1150-6_0_3_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_1150-6_0_3_node_116 | 0.4 | n |  | TRUE
43 | bus_LV_1150-6_0_3_node_68 | 0.4 | n |  | TRUE
44 | bus_LV_1150-6_0_3_node_26 | 0.4 | n |  | TRUE
45 | bus_LV_1150-6_0_3_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_1150-6_0_3_node_28 | 0.4 | n |  | TRUE
47 | bus_LV_1150-6_0_3_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_1150-6_0_3_node_31 | 0.4 | n |  | TRUE
49 | bus_LV_1150-6_0_3_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_1150-6_0_3_node_35 | 0.4 | n |  | TRUE
51 | bus_LV_1150-6_0_3_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_1150-6_0_3_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_1150-6_0_3_node_57 | 0.4 | n |  | TRUE
54 | bus_LV_1150-6_0_3_node_42 | 0.4 | n |  | TRUE
55 | bus_LV_1150-6_0_3_node_48 | 0.4 | n |  | TRUE
56 | bus_LV_1150-6_0_3_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_1150-6_0_3_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_1150-6_0_3_node_47 | 0.4 | n |  | TRUE
59 | bus_LV_1150-6_0_3_node_80 | 0.4 | n |  | TRUE
60 | bus_LV_1150-6_0_3_node_88 | 0.4 | n |  | TRUE
61 | bus_LV_1150-6_0_3_node_81 | 0.4 | n |  | TRUE
62 | bus_LV_1150-6_0_3_node_91 | 0.4 | n |  | TRUE
63 | bus_LV_1150-6_0_3_node_108 | 0.4 | n |  | TRUE
64 | bus_LV_1150-6_0_3_node_59 | 0.4 | n |  | TRUE
65 | bus_LV_1150-6_0_3_node_60 | 0.4 | n |  | TRUE
66 | bus_LV_1150-6_0_3_node_61 | 0.4 | n |  | TRUE
67 | bus_LV_1150-6_0_3_node_62 | 0.4 | n |  | TRUE
68 | bus_LV_1150-6_0_3_node_125 | 0.4 | n |  | TRUE
69 | bus_LV_1150-6_0_3_node_65 | 0.4 | n |  | TRUE
70 | bus_LV_1150-6_0_3_node_66 | 0.4 | n |  | TRUE
71 | bus_LV_1150-6_0_3_node_72 | 0.4 | n |  | TRUE
72 | bus_LV_1150-6_0_3_node_89 | 0.4 | n |  | TRUE
73 | bus_LV_1150-6_0_3_node_87 | 0.4 | n |  | TRUE
74 | bus_LV_1150-6_0_3_node_73 | 0.4 | n |  | TRUE
75 | bus_LV_1150-6_0_3_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_1150-6_0_3_node_93 | 0.4 | n |  | TRUE
77 | bus_LV_1150-6_0_3_node_83 | 0.4 | n |  | TRUE
78 | bus_LV_1150-6_0_3_node_92 | 0.4 | n |  | TRUE
79 | bus_LV_1150-6_0_3_node_77 | 0.4 | n |  | TRUE
80 | bus_LV_1150-6_0_3_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_1150-6_0_3_node_82 | 0.4 | n |  | TRUE
82 | bus_LV_1150-6_0_3_node_84 | 0.4 | n |  | TRUE
83 | bus_LV_1150-6_0_3_node_86 | 0.4 | n |  | TRUE
84 | bus_LV_1150-6_0_3_node_90 | 0.4 | n |  | TRUE
85 | bus_LV_1150-6_0_3_node_110 | 0.4 | n |  | TRUE
86 | bus_LV_1150-6_0_3_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_1150-6_0_3_node_123 | 0.4 | n |  | TRUE
88 | bus_LV_1150-6_0_3_node_111 | 0.4 | n |  | TRUE
89 | bus_LV_1150-6_0_3_node_109 | 0.4 | n |  | TRUE
90 | bus_LV_1150-6_0_3_node_119 | 0.4 | n |  | TRUE
91 | bus_LV_1150-6_0_3_node_124 | 0.4 | n |  | TRUE
92 | bus_LV_1150-6_0_3_node_121 | 0.4 | n |  | TRUE
93 | bus_LV_1150-6_0_3_node_95 | 0.4 | n |  | TRUE
94 | bus_LV_1150-6_0_3_node_96 | 0.4 | n |  | TRUE
95 | bus_LV_1150-6_0_3_node_97 | 0.4 | n |  | TRUE
96 | bus_LV_1150-6_0_3_node_98 | 0.4 | n |  | TRUE
97 | bus_LV_1150-6_0_3_node_99 | 0.4 | n |  | TRUE
98 | bus_LV_1150-6_0_3_node_106 | 0.4 | n |  | TRUE
99 | bus_LV_1150-6_0_3_node_100 | 0.4 | n |  | TRUE
100 | bus_LV_1150-6_0_3_node_104 | 0.4 | n |  | TRUE
101 | bus_LV_1150-6_0_3_node_101 | 0.4 | n |  | TRUE
102 | bus_LV_1150-6_0_3_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_1150-6_0_3_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_1150-6_0_3_node_114 | 0.4 | n |  | TRUE
105 | bus_LV_1150-6_0_3_node_113 | 0.4 | n |  | TRUE
106 | bus_LV_1150-6_0_3_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_1150-6_0_3_node_107 | 0.4 | n |  | TRUE
108 | bus_LV_1150-6_0_3_node_112 | 0.4 | n |  | TRUE
109 | bus_LV_1150-6_0_3_node_117 | 0.4 | n |  | TRUE
110 | bus_LV_1150-6_0_3_node_118 | 0.4 | n |  | TRUE
111 | bus_LV_1150-6_0_3_node_115 | 0.4 | n |  | TRUE
112 | bus_LV_1150-6_0_3_node_122 | 0.4 | n |  | TRUE
113 | bus_MV_129_0_node_53 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1150-6_0_3_load_0 | 0 | 0.00011497 | 2.8814e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1150-6_0_3_load_4 | 3 | 0.00020247 | 5.0745e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1150-6_0_3_load_9 | 4 | 4.2391e-05 | 1.0624e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1150-6_0_3_load_6 | 5 | 0.00021337 | 5.3476e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1150-6_0_3_load_5 | 6 | 0.00010073 | 2.5245e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1150-6_0_3_load_8 | 8 | 0.00042817 | 0.00010731 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1150-6_0_3_load_76 | 11 | 0.00026275 | 6.5851e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1150-6_0_3_load_10 | 12 | 7.8496e-05 | 1.9673e-05 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1150-6_0_3_load_11 | 13 | 0.00057685 | 0.00014457 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1150-6_0_3_load_53 | 15 | 0.0040484 | 0.0010146 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1150-6_0_3_load_54 | 16 | 0.0010447 | 0.00026183 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1150-6_0_3_load_55 | 17 | 0.0010355 | 0.00025952 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1150-6_0_3_load_51 | 18 | 0.010837 | 0.002716 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1150-6_0_3_load_12 | 19 | 0.033112 | 0.0082987 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1150-6_0_3_load_15 | 22 | 0.014913 | 0.0037376 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1150-6_0_3_load_17 | 24 | 0.0011946 | 0.00029939 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1150-6_0_3_load_63 | 28 | 0.00051318 | 0.00012862 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1150-6_0_3_load_25 | 29 | 0.00016432 | 4.1182e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1150-6_0_3_load_39 | 32 | 0.0019509 | 0.00048895 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1150-6_0_3_load_71 | 34 | 0.00049113 | 0.00012309 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1150-6_0_3_load_22 | 35 | 0.0052362 | 0.0013123 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1150-6_0_3_load_58 | 36 | 0.00059676 | 0.00014956 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1150-6_0_3_load_36 | 38 | 0.0012877 | 0.00032273 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1150-6_0_3_load_32 | 39 | 0.00071482 | 0.00017915 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1150-6_0_3_load_50 | 40 | 0.0023743 | 0.00059507 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1150-6_0_3_load_38 | 41 | 0.0040651 | 0.0010188 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1150-6_0_3_load_116 | 42 | 0.00059354 | 0.00014876 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1150-6_0_3_load_26 | 44 | 0.040531 | 0.010158 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1150-6_0_3_load_27 | 45 | 0.012487 | 0.0031294 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1150-6_0_3_load_28 | 46 | 0.00088692 | 0.00022228 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1150-6_0_3_load_29 | 47 | 0.0021451 | 0.0005376 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1150-6_0_3_load_31 | 48 | 0.0030654 | 0.00076826 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1150-6_0_3_load_33 | 49 | 0.00044769 | 0.0001122 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1150-6_0_3_load_35 | 50 | 0.0013139 | 0.00032929 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1150-6_0_3_load_40 | 51 | 0.00055438 | 0.00013894 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1150-6_0_3_load_43 | 52 | 0.00088115 | 0.00022084 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1150-6_0_3_load_57 | 53 | 0.00059657 | 0.00014952 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1150-6_0_3_load_42 | 54 | 0.0006578 | 0.00016486 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1150-6_0_3_load_48 | 55 | 0.0064478 | 0.001616 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1150-6_0_3_load_45 | 57 | 0.00098047 | 0.00024573 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1150-6_0_3_load_47 | 58 | 0.0050955 | 0.0012771 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1150-6_0_3_load_80 | 59 | 0.0050151 | 0.0012569 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1150-6_0_3_load_81 | 61 | 0.00050096 | 0.00012555 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1150-6_0_3_load_91 | 62 | 0.0013416 | 0.00033624 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1150-6_0_3_load_60 | 65 | 0.00066468 | 0.00016659 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1150-6_0_3_load_62 | 67 | 0.00058155 | 0.00014575 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1150-6_0_3_load_125 | 68 | 0.0017874 | 0.00044795 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1150-6_0_3_load_65 | 69 | 0.00060656 | 0.00015202 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1150-6_0_3_load_66 | 70 | 0.00028172 | 7.0605e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1150-6_0_3_load_72 | 71 | 0.00087221 | 0.0002186 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1150-6_0_3_load_89 | 72 | 0.0031199 | 0.00078191 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1150-6_0_3_load_73 | 74 | 0.0015718 | 0.00039394 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1150-6_0_3_load_74 | 75 | 5.5778e-05 | 1.3979e-05 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1150-6_0_3_load_83 | 77 | 0.00017231 | 4.3185e-05 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1150-6_0_3_load_92 | 78 | 0.00066008 | 0.00016543 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1150-6_0_3_load_77 | 79 | 0.0001492 | 3.7394e-05 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1150-6_0_3_load_82 | 81 | 0.0001857 | 4.6542e-05 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1150-6_0_3_load_84 | 82 | 0.00030938 | 7.7537e-05 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1150-6_0_3_load_86 | 83 | 0.0010317 | 0.00025857 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1150-6_0_3_load_120 | 86 | 0.0017441 | 0.00043712 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1150-6_0_3_load_111 | 88 | 0.0017798 | 0.00044605 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1150-6_0_3_load_109 | 89 | 0.0017259 | 0.00043255 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1150-6_0_3_load_119 | 90 | 0.0017148 | 0.00042976 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1150-6_0_3_load_124 | 91 | 0.00048899 | 0.00012255 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1150-6_0_3_load_121 | 92 | 0.00063517 | 0.00015919 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1150-6_0_3_load_95 | 93 | 0.00040342 | 0.00010111 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1150-6_0_3_load_96 | 94 | 0.00055987 | 0.00014032 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1150-6_0_3_load_97 | 95 | 0.00046858 | 0.00011744 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1150-6_0_3_load_98 | 96 | 0.00069963 | 0.00017534 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1150-6_0_3_load_99 | 97 | 0.00067357 | 0.00016881 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1150-6_0_3_load_104 | 100 | 0.0024747 | 0.00062021 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1150-6_0_3_load_101 | 101 | 0.00052017 | 0.00013037 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1150-6_0_3_load_102 | 102 | 0.00052036 | 0.00013041 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1150-6_0_3_load_103 | 103 | 0.00091166 | 0.00022848 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1150-6_0_3_load_114 | 104 | 0.0005983 | 0.00014995 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1150-6_0_3_load_113 | 105 | 0.0005983 | 0.00014995 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1150-6_0_3_load_105 | 106 | 0.0016496 | 0.00041342 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1150-6_0_3_load_112 | 108 | 0.0017017 | 0.00042648 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1150-6_0_3_load_117 | 109 | 0.00073748 | 0.00018483 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1150-6_0_3_load_118 | 110 | 0.0037952 | 0.00095116 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1150-6_0_3_load_115 | 111 | 0.00083686 | 0.00020974 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1150-6_0_3_load_122 | 112 | 0.0052765 | 0.0013224 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 58 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1150-6_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01049 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1150-6_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.01383 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1150-6_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.024681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1150-6_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.033566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1150-6_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.015083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1150-6_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.025678 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1150-6_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.10064 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1150-6_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.068927 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1150-6_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.079495 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1150-6_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.14289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1150-6_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.015599 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1150-6_0_3_line_11 | NAYY 4x150 SE | 10 | 76 | 0.18181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1150-6_0_3_line_12 | NAYY 4x150 SE | 10 | 75 | 0.097267 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1150-6_0_3_line_13 | NAYY 4x150 SE | 11 | 79 | 0.052903 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1150-6_0_3_line_14 | NAYY 4x150 SE | 12 | 13 | 0.029384 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1150-6_0_3_line_15 | NAYY 4x150 SE | 13 | 14 | 0.068558 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1150-6_0_3_line_16 | NAYY 4x150 SE | 14 | 15 | 0.084175 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1150-6_0_3_line_17 | NAYY 4x150 SE | 14 | 16 | 0.048218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1150-6_0_3_line_18 | NAYY 4x150 SE | 14 | 17 | 0.11929 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1150-6_0_3_line_19 | NAYY 4x150 SE | 14 | 18 | 0.082755 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1150-6_0_3_line_20 | NAYY 4x150 SE | 16 | 59 | 0.02038 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1150-6_0_3_line_21 | NAYY 4x150 SE | 17 | 60 | 0.019083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1150-6_0_3_line_22 | NAYY 4x150 SE | 19 | 20 | 0.0096391 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1150-6_0_3_line_23 | NAYY 4x150 SE | 19 | 21 | 0.071882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1150-6_0_3_line_24 | NAYY 4x150 SE | 20 | 22 | 0.038862 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1150-6_0_3_line_25 | NAYY 4x150 SE | 20 | 23 | 0.049282 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1150-6_0_3_line_26 | NAYY 4x150 SE | 21 | 24 | 0.0086174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1150-6_0_3_line_27 | NAYY 4x150 SE | 21 | 25 | 0.066533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
28 | LV_1150-6_0_3_line_28 | NAYY 4x150 SE | 22 | 26 | 0.070086 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1150-6_0_3_line_29 | NAYY 4x150 SE | 23 | 27 | 0.023802 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1150-6_0_3_line_30 | NAYY 4x150 SE | 23 | 28 | 0.034039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1150-6_0_3_line_31 | NAYY 4x150 SE | 24 | 29 | 0.022892 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1150-6_0_3_line_32 | NAYY 4x150 SE | 25 | 33 | 0.011218 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
33 | LV_1150-6_0_3_line_33 | NAYY 4x150 SE | 25 | 34 | 0.020313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1150-6_0_3_line_34 | NAYY 4x150 SE | 26 | 35 | 0.16412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1150-6_0_3_line_35 | NAYY 4x150 SE | 27 | 36 | 0.01664 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1150-6_0_3_line_36 | NAYY 4x150 SE | 27 | 37 | 0.16433 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1150-6_0_3_line_37 | NAYY 4x150 SE | 30 | 31 | 0.005344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1150-6_0_3_line_38 | NAYY 4x150 SE | 30 | 32 | 0.021589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1150-6_0_3_line_39 | NAYY 4x150 SE | 31 | 33 | 0.01061 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1150-6_0_3_line_40 | NAYY 4x150 SE | 31 | 40 | 0.012461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1150-6_0_3_line_41 | NAYY 4x150 SE | 32 | 41 | 0.023183 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1150-6_0_3_line_42 | NAYY 4x150 SE | 33 | 42 | 0.02063 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
43 | LV_1150-6_0_3_line_43 | NAYY 4x150 SE | 34 | 43 | 0.024322 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1150-6_0_3_line_44 | NAYY 4x150 SE | 36 | 53 | 0.0083291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
45 | LV_1150-6_0_3_line_45 | NAYY 4x150 SE | 37 | 38 | 0.062882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
46 | LV_1150-6_0_3_line_46 | NAYY 4x150 SE | 37 | 39 | 0.063124 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
47 | LV_1150-6_0_3_line_47 | NAYY 4x150 SE | 39 | 48 | 0.040949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1150-6_0_3_line_48 | NAYY 4x150 SE | 40 | 55 | 0.030378 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1150-6_0_3_line_49 | NAYY 4x150 SE | 41 | 47 | 0.021101 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
50 | LV_1150-6_0_3_line_50 | NAYY 4x150 SE | 42 | 63 | 0.0055451 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1150-6_0_3_line_51 | NAYY 4x150 SE | 43 | 71 | 0.026568 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1150-6_0_3_line_52 | NAYY 4x150 SE | 43 | 70 | 0.013395 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1150-6_0_3_line_53 | NAYY 4x150 SE | 44 | 45 | 0.057164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1150-6_0_3_line_54 | NAYY 4x150 SE | 44 | 46 | 0.09277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1150-6_0_3_line_55 | NAYY 4x150 SE | 45 | 47 | 0.043305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1150-6_0_3_line_56 | NAYY 4x150 SE | 48 | 49 | 0.0081023 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1150-6_0_3_line_57 | NAYY 4x150 SE | 49 | 50 | 0.00043809 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
58 | LV_1150-6_0_3_line_58 | NAYY 4x150 SE | 50 | 51 | 0.018555 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
59 | LV_1150-6_0_3_line_59 | NAYY 4x150 SE | 51 | 52 | 0.017961 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
60 | LV_1150-6_0_3_line_60 | NAYY 4x150 SE | 52 | 54 | 0.018583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
61 | LV_1150-6_0_3_line_61 | NAYY 4x150 SE | 53 | 64 | 0.034309 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
62 | LV_1150-6_0_3_line_62 | NAYY 4x150 SE | 54 | 56 | 0.036876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
63 | LV_1150-6_0_3_line_63 | NAYY 4x150 SE | 55 | 58 | 0.048415 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
64 | LV_1150-6_0_3_line_64 | NAYY 4x150 SE | 56 | 57 | 0.017639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1150-6_0_3_line_65 | NAYY 4x150 SE | 59 | 61 | 0.014977 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
66 | LV_1150-6_0_3_line_66 | NAYY 4x150 SE | 60 | 62 | 0.014426 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1150-6_0_3_line_67 | NAYY 4x150 SE | 61 | 80 | 0.048481 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1150-6_0_3_line_68 | NAYY 4x150 SE | 62 | 87 | 0.014418 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1150-6_0_3_line_69 | NAYY 4x150 SE | 63 | 109 | 0.036847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
70 | LV_1150-6_0_3_line_70 | NAYY 4x150 SE | 63 | 98 | 0.010445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1150-6_0_3_line_71 | NAYY 4x150 SE | 64 | 65 | 0.017486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1150-6_0_3_line_72 | NAYY 4x150 SE | 64 | 66 | 0.030871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1150-6_0_3_line_73 | NAYY 4x150 SE | 65 | 67 | 0.0061779 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
74 | LV_1150-6_0_3_line_74 | NAYY 4x150 SE | 66 | 68 | 0.018342 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1150-6_0_3_line_75 | NAYY 4x150 SE | 69 | 70 | 0.0039772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
76 | LV_1150-6_0_3_line_76 | NAYY 4x150 SE | 72 | 73 | 0.0048271 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
77 | LV_1150-6_0_3_line_77 | NAYY 4x150 SE | 73 | 84 | 0.023756 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
78 | LV_1150-6_0_3_line_78 | NAYY 4x150 SE | 73 | 83 | 0.01283 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1150-6_0_3_line_79 | NAYY 4x150 SE | 74 | 75 | 0.0049883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1150-6_0_3_line_80 | NAYY 4x150 SE | 76 | 77 | 0.34119 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1150-6_0_3_line_81 | NAYY 4x150 SE | 76 | 78 | 0.26357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1150-6_0_3_line_82 | NAYY 4x150 SE | 77 | 81 | 0.010409 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1150-6_0_3_line_83 | NAYY 4x150 SE | 79 | 80 | 0.034506 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1150-6_0_3_line_84 | NAYY 4x150 SE | 81 | 82 | 0.0019653 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1150-6_0_3_line_85 | NAYY 4x150 SE | 84 | 85 | 0.012042 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1150-6_0_3_line_86 | NAYY 4x150 SE | 84 | 86 | 0.01403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1150-6_0_3_line_87 | NAYY 4x150 SE | 85 | 88 | 0.012864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1150-6_0_3_line_88 | NAYY 4x150 SE | 85 | 89 | 0.017951 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1150-6_0_3_line_89 | NAYY 4x150 SE | 86 | 90 | 6.7438e-05 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1150-6_0_3_line_90 | NAYY 4x150 SE | 87 | 91 | 0.0018749 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1150-6_0_3_line_91 | NAYY 4x150 SE | 87 | 92 | 0.013944 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1150-6_0_3_line_92 | NAYY 4x150 SE | 89 | 107 | 0.012177 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1150-6_0_3_line_93 | NAYY 4x150 SE | 91 | 102 | 0.022269 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1150-6_0_3_line_94 | NAYY 4x150 SE | 92 | 112 | 0.016972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1150-6_0_3_line_95 | NAYY 4x150 SE | 93 | 94 | 0.0103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1150-6_0_3_line_96 | NAYY 4x150 SE | 93 | 95 | 0.015932 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1150-6_0_3_line_97 | NAYY 4x150 SE | 94 | 96 | 0.041641 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1150-6_0_3_line_98 | NAYY 4x150 SE | 95 | 97 | 0.0022326 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1150-6_0_3_line_99 | NAYY 4x150 SE | 96 | 98 | 0.013799 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1150-6_0_3_line_100 | NAYY 4x150 SE | 97 | 99 | 0.011917 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1150-6_0_3_line_101 | NAYY 4x150 SE | 98 | 100 | 0.036013 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1150-6_0_3_line_102 | NAYY 4x150 SE | 99 | 101 | 0.021104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1150-6_0_3_line_103 | NAYY 4x150 SE | 99 | 102 | 0.013009 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1150-6_0_3_line_104 | NAYY 4x150 SE | 99 | 103 | 0.020864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1150-6_0_3_line_105 | NAYY 4x150 SE | 100 | 106 | 0.017771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1150-6_0_3_line_106 | NAYY 4x150 SE | 101 | 104 | 0.021659 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1150-6_0_3_line_107 | NAYY 4x150 SE | 104 | 105 | 0.0093136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1150-6_0_3_line_108 | NAYY 4x150 SE | 105 | 111 | 0.0036885 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1150-6_0_3_line_109 | NAYY 4x150 SE | 106 | 107 | 0.011907 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1150-6_0_3_line_110 | NAYY 4x150 SE | 107 | 108 | 0.023625 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1150-6_0_3_line_111 | NAYY 4x150 SE | 109 | 110 | 0.0086179 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1150-6_0_3_trafo_47 | 0.25 MVA 20/0.4 kV | 113 | 58 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2637536.5964 | 1220506.0547 | 2637542.0133 | 1220500.0519 | 2637543.8167 | 1220498.4611
1 | 2637531.4249 | 1220518.8853 | 2637536.5964 | 1220506.0547
2 | 2637536.5964 | 1220506.0547 | 2637527.7153 | 1220499.5727 | 2637514.7291 | 1220495.2532
3 | 2637531.4249 | 1220518.8853 | 2637505.4965 | 1220518.4108 | 2637497.9111 | 1220519.266
4 | 2637500.1664 | 1220491.4437 | 2637507.8189 | 1220492.9547 | 2637514.7291 | 1220495.2532
5 | 2637474.9743 | 1220486.4693 | 2637500.1664 | 1220491.4437
6 | 2637380.4639 | 1220454.8324 | 2637398.7052 | 1220466.5093 | 2637419.0596 | 1220473.9191 | 2637449.4884 | 1220481.4368 | 2637474.9743 | 1220486.4693
7 | 2637380.4639 | 1220454.8324 | 2637373.7333 | 1220457.4251 | 2637367.8298 | 1220457.5882 | 2637360.935 | 1220453.6982 | 2637353.6815 | 1220442.8908 | 2637346.0918 | 1220427.612 | 2637340.9349 | 1220410.5588
8 | 2637313.2406 | 1220336.7525 | 2637320.5008 | 1220346.5259 | 2637323.7072 | 1220355.4735 | 2637330.1096 | 1220381.0621 | 2637338.7184 | 1220403.2291 | 2637340.9349 | 1220410.5588
9 | 2637313.2406 | 1220336.7525 | 2637315.196 | 1220316.4749 | 2637312.9397 | 1220295.137 | 2637308.9292 | 1220277.6905 | 2637293.179 | 1220233.9549 | 2637287.3426 | 1220214.8627 | 2637284.159 | 1220203.4805 | 2637281.7654 | 1220199.2074
10 | 2637313.2406 | 1220336.7525 | 2637308.7067 | 1220351.6782
11 | 2637215.3887 | 1220045.6018 | 2637220.7142 | 1220045.7351 | 2637226.3633 | 1220048.7166 | 2637232.8286 | 1220055.8612 | 2637237.0494 | 1220065.2153 | 2637237.7776 | 1220078.6056 | 2637234.0682 | 1220110.0566 | 2637234.4386 | 1220124.8455 | 2637236.1365 | 1220137.2523 | 2637241.7468 | 1220151.2845 | 2637249.0111 | 1220161.6805 | 2637261.9477 | 1220174.947 | 2637273.6832 | 1220186.1714 | 2637279.1768 | 1220194.5774 | 2637281.7654 | 1220199.2074
12 | 2637281.7654 | 1220199.2074 | 2637220.3923 | 1220158.033 | 2637204.1501 | 1220151.639 | 2637198.7927 | 1220149.1516
13 | 2637308.7067 | 1220351.6782 | 2637307.2137 | 1220356.5932 | 2637302.0343 | 1220370.7581 | 2637291.3899 | 1220388.9245 | 2637284.2196 | 1220398.0796
14 | 2637330.2416 | 1220542.7752 | 2637359.307 | 1220538.4623
15 | 2637262.8054 | 1220554.6997 | 2637279.8805 | 1220550.2482 | 2637330.2416 | 1220542.7752
16 | 2637262.8054 | 1220554.6997 | 2637257.1746 | 1220551.3069 | 2637232.1939 | 1220523.0119 | 2637222.6803 | 1220515.6926 | 2637215.6672 | 1220513.7477 | 2637206.8981 | 1220512.3366 | 2637195.5091 | 1220514.9893
17 | 2637262.8054 | 1220554.6997 | 2637265.1474 | 1220548.9998 | 2637264.4733 | 1220542.7586 | 2637257.2981 | 1220525.4702 | 2637254.1602 | 1220509.2187 | 2637254.1163 | 1220508.7123
18 | 2637262.8054 | 1220554.6997 | 2637253.0688 | 1220556.3843 | 2637159.3013 | 1220580.1133 | 2637147.0046 | 1220583.2239
19 | 2637262.8054 | 1220554.6997 | 2637277.0232 | 1220581.3266 | 2637292.2729 | 1220620.0338 | 2637295.6282 | 1220630.4754
20 | 2637252.9752 | 1220488.4118 | 2637252.6457 | 1220491.7656 | 2637254.1163 | 1220508.7123
21 | 2637128.5041 | 1220587.9039 | 2637147.0046 | 1220583.2239
22 | 2637164.3299 | 1220818.7641 | 2637154.6979 | 1220818.3936
23 | 2637091.4018 | 1220799.354 | 2637095.2165 | 1220808.0941 | 2637101.0742 | 1220814.0118 | 2637107.3732 | 1220816.0856 | 2637121.6062 | 1220817.1303 | 2637154.3259 | 1220818.3793 | 2637154.6979 | 1220818.3936
24 | 2637164.3299 | 1220818.7641 | 2637162.2721 | 1220857.5718
25 | 2637164.3299 | 1220818.7641 | 2637208.396 | 1220820.451 | 2637213.5762 | 1220820.6501
26 | 2637091.4018 | 1220799.354 | 2637090.5109 | 1220807.9252
27 | 2637091.4018 | 1220799.354 | 2637090.0262 | 1220791.2295 | 2637090.6665 | 1220787.0755 | 2637091.9554 | 1220778.6674 | 2637093.1634 | 1220773.5163 | 2637094.3407 | 1220747.6861 | 2637095.0748 | 1220739.4413 | 2637095.6213 | 1220733.3077
28 | 2637158.5611 | 1220927.5594 | 2637162.2721 | 1220857.5718
29 | 2637213.5762 | 1220820.6501 | 2637227.7138 | 1220821.1831 | 2637237.3613 | 1220821.5547
30 | 2637213.5762 | 1220820.6501 | 2637224.1253 | 1220853.0127
31 | 2637088.1424 | 1220830.6944 | 2637089.4732 | 1220817.9086 | 2637090.5109 | 1220807.9252
32 | 2637106.836 | 1220734.2114 | 2637095.6213 | 1220733.3077
33 | 2637095.6213 | 1220733.3077 | 2637075.4806 | 1220730.6656
34 | 2637158.5611 | 1220927.5594 | 2637103.7416 | 1220941.215 | 2637089.8872 | 1220943.9749 | 2637077.4755 | 1220944.0978 | 2637065.0763 | 1220942.1974 | 2637053.7164 | 1220936.6457 | 2637044.8066 | 1220929.8974 | 2637012.5085 | 1220898.9585
35 | 2637237.3613 | 1220821.5547 | 2637252.4288 | 1220818.9695 | 2637253.7036 | 1220818.5174
36 | 2637237.3613 | 1220821.5547 | 2637227.7138 | 1220821.1831 | 2637229.2948 | 1220776.9779 | 2637244.3798 | 1220772.814 | 2637333.8377 | 1220741.4771
37 | 2637117.3561 | 1220735.8112 | 2637117.0497 | 1220741.1457
38 | 2637117.0497 | 1220741.1457 | 2637120.1999 | 1220740.8541 | 2637138.6244 | 1220741.024
39 | 2637117.3561 | 1220735.8112 | 2637106.836 | 1220734.2114
40 | 2637117.3561 | 1220735.8112 | 2637117.6625 | 1220730.4654 | 2637124.7572 | 1220730.8666
41 | 2637138.6244 | 1220741.024 | 2637138.7856 | 1220741.0255 | 2637161.8063 | 1220740.7977
42 | 2637106.836 | 1220734.2114 | 2637106.4976 | 1220727.6387 | 2637102.7907 | 1220714.0884
43 | 2637051.7214 | 1220725.5302 | 2637071.9557 | 1220730.2032 | 2637075.4806 | 1220730.6656
44 | 2637261.5535 | 1220815.7331 | 2637253.7036 | 1220818.5174
45 | 2637333.8377 | 1220741.4771 | 2637349.2721 | 1220784.4882 | 2637355.2513 | 1220800.6003
46 | 2637333.8377 | 1220741.4771 | 2637380.169 | 1220723.2009 | 2637393.2136 | 1220720.5126
47 | 2637433.8609 | 1220715.7782 | 2637399.0685 | 1220719.306 | 2637393.2136 | 1220720.5126
48 | 2637124.7572 | 1220730.8666 | 2637127.6048 | 1220731.0277 | 2637142.8232 | 1220732.2454 | 2637155.0808 | 1220732.0899
49 | 2637182.8653 | 1220739.5873 | 2637180.0098 | 1220739.8928 | 2637164.9832 | 1220740.7663 | 2637161.8063 | 1220740.7977
50 | 2637101.3275 | 1220708.7398 | 2637102.7907 | 1220714.0884
51 | 2637051.7214 | 1220725.5302 | 2637049.882 | 1220735.8471 | 2637047.0948 | 1220741.2108 | 2637042.3042 | 1220743.0043 | 2637037.5189 | 1220744.1831
52 | 2637051.7214 | 1220725.5302 | 2637038.543 | 1220723.1286
53 | 2637279.2661 | 1220713.7619 | 2637268.0457 | 1220718.8076 | 2637241.9471 | 1220728.7171 | 2637226.7985 | 1220733.3141 | 2637225.7069 | 1220733.5344
54 | 2637279.2661 | 1220713.7619 | 2637291.1128 | 1220708.4346 | 2637325.2967 | 1220694.0288 | 2637355.5667 | 1220683.1563 | 2637365.6795 | 1220680.2495
55 | 2637182.8653 | 1220739.5873 | 2637208.5842 | 1220736.8359 | 2637213.3308 | 1220736.0317 | 2637225.7069 | 1220733.5344
56 | 2637433.8609 | 1220715.7782 | 2637441.9218 | 1220714.9609
57 | 2637441.9218 | 1220714.9609 | 2637442.3577 | 1220714.9167
58 | 2637460.8184 | 1220713.0449 | 2637442.3577 | 1220714.9167
59 | 2637460.8184 | 1220713.0449 | 2637468.4531 | 1220712.2708 | 2637478.6931 | 1220713.2502
60 | 2637497.1916 | 1220715.0195 | 2637478.6931 | 1220713.2502
61 | 2637293.8891 | 1220804.2644 | 2637261.5535 | 1220815.7331
62 | 2637533.9002 | 1220718.5305 | 2637497.1916 | 1220715.0195
63 | 2637203.3 | 1220728.3192 | 2637200.3195 | 1220728.824 | 2637183.8905 | 1220730.7338 | 2637166.3279 | 1220731.9472 | 2637155.0808 | 1220732.0899
64 | 2637533.9002 | 1220718.5305 | 2637532.9466 | 1220700.9176
65 | 2637252.9752 | 1220488.4118 | 2637254.4394 | 1220473.5066
66 | 2637128.5041 | 1220587.9039 | 2637131.938 | 1220601.9155
67 | 2637264.0951 | 1220426.087 | 2637258.4199 | 1220446.7638 | 2637254.5984 | 1220471.8882 | 2637254.4394 | 1220473.5066
68 | 2637135.3699 | 1220615.9188 | 2637131.938 | 1220601.9155
69 | 2637101.3275 | 1220708.7398 | 2637098.9076 | 1220705.067 | 2637095.4561 | 1220703.7781 | 2637066.9827 | 1220699.7
70 | 2637101.3275 | 1220708.7398 | 2637100.8763 | 1220704.4567 | 2637099.1529 | 1220698.5647
71 | 2637293.8891 | 1220804.2644 | 2637299.6326 | 1220820.78
72 | 2637323.0627 | 1220793.9297 | 2637293.8891 | 1220804.2644
73 | 2637301.6618 | 1220826.6152 | 2637299.6326 | 1220820.78
74 | 2637323.0627 | 1220793.9297 | 2637329.3746 | 1220811.1518
75 | 2637034.6302 | 1220722.4155 | 2637038.543 | 1220723.1286
76 | 2637039.8134 | 1220610.3434 | 2637035.134 | 1220611.5283
77 | 2637046.454 | 1220633.1538 | 2637039.8134 | 1220610.3434
78 | 2637039.8134 | 1220610.3434 | 2637052.2512 | 1220607.1958
79 | 2637194.2683 | 1220147.051 | 2637198.7927 | 1220149.1516
80 | 2637215.3887 | 1220045.6018 | 2637349.3727 | 1219731.8165
81 | 2637215.3887 | 1220045.6018 | 2636997.2543 | 1219897.6654
82 | 2637344.2088 | 1219722.7784 | 2637349.3727 | 1219731.8165
83 | 2637264.0951 | 1220426.087 | 2637276.2087 | 1220408.3077 | 2637284.2196 | 1220398.0796
84 | 2637344.2088 | 1219722.7784 | 2637343.2338 | 1219721.072
85 | 2637046.454 | 1220633.1538 | 2637049.8265 | 1220644.7149
86 | 2637046.454 | 1220633.1538 | 2637032.9645 | 1220637.0115
87 | 2637053.4216 | 1220657.0668 | 2637049.8265 | 1220644.7149
88 | 2637049.8265 | 1220644.7149 | 2637067.057 | 1220639.6818
89 | 2637032.9645 | 1220637.0115 | 2637032.8996 | 1220637.0301
90 | 2637135.3699 | 1220615.9188 | 2637135.8157 | 1220617.74
91 | 2637135.3699 | 1220615.9188 | 2637128.7463 | 1220618.4346 | 2637122.0621 | 1220619.9704
92 | 2637078.7459 | 1220636.2674 | 2637067.057 | 1220639.6818
93 | 2637135.8157 | 1220617.74 | 2637141.1103 | 1220639.3704
94 | 2637105.5208 | 1220623.771 | 2637122.0621 | 1220619.9704
95 | 2637115.0624 | 1220659.4738 | 2637117.6181 | 1220669.4514
96 | 2637115.0624 | 1220659.4738 | 2637115.0624 | 1220659.4738 | 2637130.4962 | 1220655.5189
97 | 2637117.6181 | 1220669.4514 | 2637120.4247 | 1220680.4085 | 2637125.7106 | 1220694.1051 | 2637125.8103 | 1220696.3737 | 2637124.6042 | 1220697.5669 | 2637112.9471 | 1220698.3178
98 | 2637132.6589 | 1220654.9647 | 2637130.4962 | 1220655.5189
99 | 2637099.1529 | 1220698.5647 | 2637110.9126 | 1220698.4489 | 2637112.9471 | 1220698.3178
100 | 2637144.2034 | 1220652.0064 | 2637132.6589 | 1220654.9647
101 | 2637099.1529 | 1220698.5647 | 2637094.4953 | 1220682.6373 | 2637091.1495 | 1220676.5685 | 2637087.4759 | 1220664.6324
102 | 2637144.2034 | 1220652.0064 | 2637164.6523 | 1220646.7885
103 | 2637144.2034 | 1220652.0064 | 2637141.1103 | 1220639.3704
104 | 2637149.1676 | 1220672.2715 | 2637144.2034 | 1220652.0064
105 | 2637087.4759 | 1220664.6324 | 2637082.2483 | 1220647.6474
106 | 2637164.6523 | 1220646.7885 | 2637171.9764 | 1220644.9197 | 2637175.3564 | 1220658.6084
107 | 2637177.5891 | 1220667.6504 | 2637175.3564 | 1220658.6084
108 | 2637178.4733 | 1220671.2313 | 2637177.5891 | 1220667.6504
109 | 2637078.7459 | 1220636.2674 | 2637082.2483 | 1220647.6474
110 | 2637078.7459 | 1220636.2674 | 2637071.2735 | 1220613.8553
111 | 2637058.4519 | 1220698.4782 | 2637066.9827 | 1220699.7

## bus_geodata
| x | y | coords
0 | 2637543.8167 | 1220498.4611
1 | 2637536.5964 | 1220506.0547
2 | 2637531.4249 | 1220518.8853
3 | 2637514.7291 | 1220495.2532
4 | 2637497.9111 | 1220519.266
5 | 2637500.1664 | 1220491.4437
6 | 2637474.9743 | 1220486.4693
7 | 2637380.4639 | 1220454.8324
8 | 2637340.9349 | 1220410.5588
9 | 2637313.2406 | 1220336.7525
10 | 2637281.7654 | 1220199.2074
11 | 2637308.7067 | 1220351.6782
12 | 2637359.307 | 1220538.4623
13 | 2637330.2416 | 1220542.7752
14 | 2637262.8054 | 1220554.6997
15 | 2637195.5091 | 1220514.9893
16 | 2637254.1163 | 1220508.7123
17 | 2637147.0046 | 1220583.2239
18 | 2637295.6282 | 1220630.4754
19 | 2637154.6979 | 1220818.3936
20 | 2637164.3299 | 1220818.7641
21 | 2637091.4018 | 1220799.354
22 | 2637162.2721 | 1220857.5718
23 | 2637213.5762 | 1220820.6501
24 | 2637090.5109 | 1220807.9252
25 | 2637095.6213 | 1220733.3077
26 | 2637158.5611 | 1220927.5594
27 | 2637237.3613 | 1220821.5547
28 | 2637224.1253 | 1220853.0127
29 | 2637088.1424 | 1220830.6944
30 | 2637117.0497 | 1220741.1457
31 | 2637117.3561 | 1220735.8112
32 | 2637138.6244 | 1220741.024
33 | 2637106.836 | 1220734.2114
34 | 2637075.4806 | 1220730.6656
35 | 2637012.5085 | 1220898.9585
36 | 2637253.7036 | 1220818.5174
37 | 2637333.8377 | 1220741.4771
38 | 2637355.2513 | 1220800.6003
39 | 2637393.2136 | 1220720.5126
40 | 2637124.7572 | 1220730.8666
41 | 2637161.8063 | 1220740.7977
42 | 2637102.7907 | 1220714.0884
43 | 2637051.7214 | 1220725.5302
44 | 2637279.2661 | 1220713.7619
45 | 2637225.7069 | 1220733.5344
46 | 2637365.6795 | 1220680.2495
47 | 2637182.8653 | 1220739.5873
48 | 2637433.8609 | 1220715.7782
49 | 2637441.9218 | 1220714.9609
50 | 2637442.3577 | 1220714.9167
51 | 2637460.8184 | 1220713.0449
52 | 2637478.6931 | 1220713.2502
53 | 2637261.5535 | 1220815.7331
54 | 2637497.1916 | 1220715.0195
55 | 2637155.0808 | 1220732.0899
56 | 2637533.9002 | 1220718.5305
57 | 2637532.9466 | 1220700.9176
58 | 2637203.3 | 1220728.3192
59 | 2637252.9752 | 1220488.4118
60 | 2637128.5041 | 1220587.9039
61 | 2637254.4394 | 1220473.5066
62 | 2637131.938 | 1220601.9155
63 | 2637101.3275 | 1220708.7398
64 | 2637293.8891 | 1220804.2644
65 | 2637299.6326 | 1220820.78
66 | 2637323.0627 | 1220793.9297
67 | 2637301.6618 | 1220826.6152
68 | 2637329.3746 | 1220811.1518
69 | 2637034.6302 | 1220722.4155
70 | 2637038.543 | 1220723.1286
71 | 2637037.5189 | 1220744.1831
72 | 2637035.134 | 1220611.5283
73 | 2637039.8134 | 1220610.3434
74 | 2637194.2683 | 1220147.051
75 | 2637198.7927 | 1220149.1516
76 | 2637215.3887 | 1220045.6018
77 | 2637349.3727 | 1219731.8165
78 | 2636997.2543 | 1219897.6654
79 | 2637284.2196 | 1220398.0796
80 | 2637264.0951 | 1220426.087
81 | 2637344.2088 | 1219722.7784
82 | 2637343.2338 | 1219721.072
83 | 2637052.2512 | 1220607.1958
84 | 2637046.454 | 1220633.1538
85 | 2637049.8265 | 1220644.7149
86 | 2637032.9645 | 1220637.0115
87 | 2637135.3699 | 1220615.9188
88 | 2637053.4216 | 1220657.0668
89 | 2637067.057 | 1220639.6818
90 | 2637032.8996 | 1220637.0301
91 | 2637135.8157 | 1220617.74
92 | 2637122.0621 | 1220619.9704
93 | 2637115.0624 | 1220659.4738
94 | 2637117.6181 | 1220669.4514
95 | 2637130.4962 | 1220655.5189
96 | 2637112.9471 | 1220698.3178
97 | 2637132.6589 | 1220654.9647
98 | 2637099.1529 | 1220698.5647
99 | 2637144.2034 | 1220652.0064
100 | 2637087.4759 | 1220664.6324
101 | 2637164.6523 | 1220646.7885
102 | 2637141.1103 | 1220639.3704
103 | 2637149.1676 | 1220672.2715
104 | 2637175.3564 | 1220658.6084
105 | 2637177.589 | 1220667.6504
106 | 2637082.2483 | 1220647.6474
107 | 2637078.7459 | 1220636.2674
108 | 2637071.2734 | 1220613.8553
109 | 2637066.9827 | 1220699.7
110 | 2637058.4519 | 1220698.4782
111 | 2637178.4733 | 1220671.2313
112 | 2637105.5208 | 1220623.771
113 | 2637117.3561 | 1220735.8112

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97115 | -0.20425 | 0.00011497 | 2.8814e-05
1 | 0.97115 | -0.20424 | 0 | 0
2 | 0.97115 | -0.20425 | 0 | 0
3 | 0.97116 | -0.2042 | 0.00020247 | 5.0745e-05
4 | 0.97115 | -0.20426 | 4.2391e-05 | 1.0624e-05
5 | 0.97117 | -0.20414 | 0.00021337 | 5.3476e-05
6 | 0.97119 | -0.20398 | 0.00010073 | 2.5245e-05
7 | 0.97129 | -0.20324 | 0 | 0
8 | 0.97135 | -0.20274 | 0.00042817 | 0.00010731
9 | 0.97148 | -0.20178 | 0 | 0
10 | 0.97086 | -0.20639 | 0 | 0
11 | 0.97158 | -0.20109 | 0.00026275 | 6.5851e-05
12 | 0.97357 | -0.1864 | 7.8496e-05 | 1.9673e-05
13 | 0.97358 | -0.18637 | 0.00057685 | 0.00014457
14 | 0.97364 | -0.1859 | 0 | 0
15 | 0.97314 | -0.18949 | 0.0040484 | 0.0010146
16 | 0.97286 | -0.19158 | 0.0010447 | 0.00026183
17 | 0.97829 | -0.15246 | 0.0010355 | 0.00025952
18 | 0.97233 | -0.19535 | 0.010837 | 0.002716
19 | 0.97944 | -0.14408 | 0.033112 | 0.0082987
20 | 0.97895 | -0.14758 | 0 | 0
21 | 0.98656 | -0.093596 | 0 | 0
22 | 0.97781 | -0.15576 | 0.014913 | 0.0037376
23 | 0.9779 | -0.15514 | 0 | 0
24 | 0.98654 | -0.093717 | 0.0011946 | 0.00029939
25 | 0.98991 | -0.070013 | 0 | 0
26 | 0.97727 | -0.1596 | 0 | 0
27 | 0.9774 | -0.15866 | 0 | 0
28 | 0.97787 | -0.15532 | 0.00051318 | 0.00012862
29 | 0.98653 | -0.093756 | 0.00016432 | 4.1182e-05
30 | 0.99052 | -0.065765 | 0 | 0
31 | 0.991 | -0.062391 | 0 | 0
32 | 0.98857 | -0.079427 | 0.0019509 | 0.00048895
33 | 0.9903 | -0.067286 | 0 | 0
34 | 0.98985 | -0.07048 | 0.00049113 | 0.00012309
35 | 0.97602 | -0.16861 | 0.0052362 | 0.0013123
36 | 0.9773 | -0.1594 | 0.00059676 | 0.00014956
37 | 0.97502 | -0.17576 | 0 | 0
38 | 0.9749 | -0.17662 | 0.0012877 | 0.00032273
39 | 0.97423 | -0.18149 | 0.00071482 | 0.00017915
40 | 0.9922 | -0.054036 | 0.0023743 | 0.00059507
41 | 0.98654 | -0.093694 | 0.0040651 | 0.0010188
42 | 0.98934 | -0.074058 | 0.00059354 | 0.00014876
43 | 0.98979 | -0.070918 | 0 | 0
44 | 0.97797 | -0.15458 | 0.040531 | 0.010158
45 | 0.98142 | -0.12996 | 0.012487 | 0.0031294
46 | 0.97785 | -0.15545 | 0.00088692 | 0.00022228
47 | 0.98482 | -0.10585 | 0.0021451 | 0.0005376
48 | 0.97375 | -0.1849 | 0.0030654 | 0.00076826
49 | 0.9737 | -0.18531 | 0.00044769 | 0.0001122
50 | 0.97369 | -0.18533 | 0.0013139 | 0.00032929
51 | 0.97361 | -0.18593 | 0.00055438 | 0.00013894
52 | 0.97354 | -0.18641 | 0.00088115 | 0.00022084
53 | 0.97726 | -0.15972 | 0.00059657 | 0.00014952
54 | 0.9735 | -0.18673 | 0.0006578 | 0.00016486
55 | 0.99515 | -0.033507 | 0.0064478 | 0.001616
56 | 0.97345 | -0.18712 | 0 | 0
57 | 0.97342 | -0.1873 | 0.00098047 | 0.00024573
58 | 1 | 0 | -0.21154 | -0.053314
59 | 0.97256 | -0.19375 | 0.0050151 | 0.0012569
60 | 0.97906 | -0.14693 | 0 | 0
61 | 0.97245 | -0.19456 | 0.00050096 | 0.00012555
62 | 0.97964 | -0.14276 | 0.0013416 | 0.00033624
63 | 0.98883 | -0.07767 | 0 | 0
64 | 0.97711 | -0.16081 | 0 | 0
65 | 0.97707 | -0.16104 | 0.00066468 | 0.00016659
66 | 0.97703 | -0.16139 | 0 | 0
67 | 0.97707 | -0.16107 | 0.00058155 | 0.00014575
68 | 0.97698 | -0.16173 | 0.0017874 | 0.00044795
69 | 0.98977 | -0.071064 | 0.00060656 | 0.00015202
70 | 0.98977 | -0.071039 | 0.00028172 | 7.0605e-05
71 | 0.98975 | -0.071154 | 0.00087221 | 0.0002186
72 | 0.98572 | -0.099686 | 0.0031199 | 0.00078191
73 | 0.98574 | -0.099531 | 0 | 0
74 | 0.97062 | -0.20815 | 0.0015718 | 0.00039394
75 | 0.97063 | -0.20807 | 5.5778e-05 | 1.3979e-05
76 | 0.97051 | -0.20907 | 0 | 0
77 | 0.97018 | -0.21154 | 0.00017231 | 4.3185e-05
78 | 0.97025 | -0.21095 | 0.00066008 | 0.00016543
79 | 0.97191 | -0.1986 | 0.0001492 | 3.7394e-05
80 | 0.97214 | -0.19692 | 0 | 0
81 | 0.97017 | -0.2116 | 0.0001857 | 4.6542e-05
82 | 0.97017 | -0.2116 | 0.00030938 | 7.7537e-05
83 | 0.98572 | -0.099667 | 0.0010317 | 0.00025857
84 | 0.98588 | -0.098518 | 0 | 0
85 | 0.98601 | -0.097576 | 0 | 0
86 | 0.98581 | -0.099016 | 0.0017441 | 0.00043712
87 | 0.98025 | -0.13839 | 0 | 0
88 | 0.98598 | -0.097811 | 0.0017798 | 0.00044605
89 | 0.98626 | -0.095844 | 0.0017259 | 0.00043255
90 | 0.98581 | -0.099017 | 0.0017148 | 0.00042976
91 | 0.98035 | -0.13771 | 0.00048899 | 0.00012255
92 | 0.98013 | -0.13925 | 0.00063517 | 0.00015919
93 | 0.98394 | -0.11215 | 0.00040342 | 0.00010111
94 | 0.98456 | -0.10779 | 0.00055987 | 0.00014032
95 | 0.983 | -0.11884 | 0.00046858 | 0.00011744
96 | 0.98708 | -0.089981 | 0.00069963 | 0.00017534
97 | 0.98287 | -0.11977 | 0.00067357 | 0.00016881
98 | 0.98793 | -0.084 | 0 | 0
99 | 0.98218 | -0.12464 | 0 | 0
100 | 0.98705 | -0.090251 | 0.0024747 | 0.00062021
101 | 0.9821 | -0.1252 | 0.00052017 | 0.00013037
102 | 0.9815 | -0.1295 | 0.00052036 | 0.00013041
103 | 0.98216 | -0.12484 | 0.00091166 | 0.00022848
104 | 0.98204 | -0.12566 | 0.0005983 | 0.00014995
105 | 0.98202 | -0.12579 | 0.0005983 | 0.00014995
106 | 0.98667 | -0.092888 | 0.0016496 | 0.00041342
107 | 0.98645 | -0.094455 | 0 | 0
108 | 0.9864 | -0.094867 | 0.0017017 | 0.00042648
109 | 0.98859 | -0.079376 | 0.00073748 | 0.00018483
110 | 0.98854 | -0.07971 | 0.0037952 | 0.00095116
111 | 0.98202 | -0.12583 | 0.00083686 | 0.00020974
112 | 0.98 | -0.14018 | 0.0052765 | 0.0013224
113 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00011497 | -2.8814e-05 | 0.00011497 | 2.8684e-05 | 2.0308e-10 | -1.2972e-07 | 0.00017616 | 0.00017611 | 0.00017616 | 0.97115 | -0.20425 | 0.97115 | -0.20424 | 0.065244
1 | 4.2391e-05 | 1.0038e-05 | -4.2391e-05 | -1.0209e-05 | 3.621e-11 | -1.7111e-07 | 6.4746e-05 | 6.4805e-05 | 6.4805e-05 | 0.97115 | -0.20424 | 0.97115 | -0.20425 | 0.024002
2 | -0.00015736 | -3.8722e-05 | 0.00015736 | 3.8417e-05 | 8.9302e-10 | -3.0504e-07 | 0.00024085 | 0.00024075 | 0.00024085 | 0.97115 | -0.20424 | 0.97116 | -0.2042 | 0.089206
3 | 4.2391e-05 | 1.0209e-05 | -4.2391e-05 | -1.0624e-05 | 8.816e-11 | -4.1529e-07 | 6.4805e-05 | 6.4953e-05 | 6.4953e-05 | 0.97115 | -0.20425 | 0.97115 | -0.20426 | 0.024056
4 | -0.00035984 | -8.9162e-05 | 0.00035984 | 8.8976e-05 | 2.8568e-09 | -1.8553e-07 | 0.00055098 | 0.00055091 | 0.00055098 | 0.97116 | -0.2042 | 0.97117 | -0.20414 | 0.20407
5 | -0.00057321 | -0.00014245 | 0.00057322 | 0.00014214 | 1.2346e-08 | -3.1299e-07 | 0.00087784 | 0.00087773 | 0.00087784 | 0.97117 | -0.20414 | 0.97119 | -0.20398 | 0.32513
6 | -0.00067395 | -0.00016739 | 0.00067402 | 0.00016617 | 6.6863e-08 | -1.2198e-06 | 0.0010321 | 0.0010316 | 0.0010321 | 0.97119 | -0.20398 | 0.97129 | -0.20324 | 0.38224
7 | -0.00067402 | -0.00016617 | 0.00067407 | 0.00016533 | 4.5759e-08 | -8.3555e-07 | 0.0010316 | 0.0010313 | 0.0010316 | 0.97129 | -0.20324 | 0.97135 | -0.20274 | 0.38208
8 | -0.0011022 | -0.00027264 | 0.0011024 | 0.00027171 | 1.4118e-07 | -9.2985e-07 | 0.0016872 | 0.0016869 | 0.0016872 | 0.97135 | -0.20274 | 0.97148 | -0.20178 | 0.6249
9 | 0.0029582 | 0.0007289 | -0.0029563 | -0.00072996 | 1.8271e-06 | -1.0653e-06 | 0.0045265 | 0.0045272 | 0.0045272 | 0.97148 | -0.20178 | 0.97086 | -0.20639 | 1.6767
10 | -0.0040605 | -0.0010006 | 0.0040609 | 0.0010006 | 3.7578e-07 | -4.863e-08 | 0.0062134 | 0.0062133 | 0.0062134 | 0.97148 | -0.20178 | 0.97158 | -0.20109 | 2.3013
11 | 0.0013283 | 0.00032316 | -0.0013279 | -0.00032522 | 4.6881e-07 | -2.0671e-06 | 0.0020324 | 0.0020332 | 0.0020332 | 0.97086 | -0.20639 | 0.97051 | -0.20907 | 0.75305
12 | 0.001628 | 0.0004068 | -0.0016276 | -0.00040786 | 3.7782e-07 | -1.0572e-06 | 0.0024947 | 0.0024952 | 0.0024952 | 0.97086 | -0.20639 | 0.97063 | -0.20807 | 0.92414
13 | -0.0043237 | -0.0010664 | 0.0043251 | 0.0010663 | 1.4448e-06 | -9.969e-08 | 0.0066157 | 0.0066155 | 0.0066157 | 0.97158 | -0.20109 | 0.97191 | -0.1986 | 2.4503
14 | -7.8496e-05 | -1.9673e-05 | 7.8497e-05 | 1.9308e-05 | 2.6363e-10 | -3.6529e-07 | 0.00011997 | 0.00011984 | 0.00011997 | 0.97357 | -0.1864 | 0.97358 | -0.18637 | 0.044435
15 | -0.00065535 | -0.00016388 | 0.00065539 | 0.00016304 | 4.2896e-08 | -8.3609e-07 | 0.0010015 | 0.0010012 | 0.0010015 | 0.97358 | -0.18637 | 0.97364 | -0.1859 | 0.37093
16 | 0.0040504 | 0.0010144 | -0.0040484 | -0.0010146 | 2.0127e-06 | -2.7223e-07 | 0.00619 | 0.0061904 | 0.0061904 | 0.97364 | -0.1859 | 0.97314 | -0.18949 | 2.2927
17 | 0.01105 | 0.0027515 | -0.011041 | -0.0027488 | 8.5739e-06 | 2.6985e-06 | 0.016881 | 0.016881 | 0.016881 | 0.97364 | -0.1859 | 0.97286 | -0.19158 | 6.2522
18 | -0.026606 | -0.0066493 | 0.026729 | 0.0066951 | 0.00012303 | 4.583e-05 | 0.040656 | 0.040655 | 0.040656 | 0.97364 | -0.1859 | 0.97829 | -0.15246 | 15.0577
19 | 0.010851 | 0.0027204 | -0.010837 | -0.002716 | 1.4202e-05 | 4.4347e-06 | 0.016584 | 0.016584 | 0.016584 | 0.97364 | -0.1859 | 0.97233 | -0.19535 | 6.1423
20 | 0.0099963 | 0.002487 | -0.0099933 | -0.0024861 | 2.9704e-06 | 8.8948e-07 | 0.015283 | 0.015283 | 0.015283 | 0.97286 | -0.19158 | 0.97256 | -0.19375 | 5.6604
21 | -0.027765 | -0.0069546 | 0.027786 | 0.0069626 | 2.1237e-05 | 7.9281e-06 | 0.04223 | 0.04223 | 0.04223 | 0.97829 | -0.15246 | 0.97906 | -0.14693 | 15.6408
22 | 0.034901 | 0.0087492 | -0.034884 | -0.0087428 | 1.6911e-05 | 6.3828e-06 | 0.053024 | 0.053024 | 0.053024 | 0.97944 | -0.14408 | 0.97895 | -0.14758 | 19.6384
23 | -0.068013 | -0.017048 | 0.068492 | 0.017231 | 0.0004789 | 0.00018328 | 0.10333 | 0.10333 | 0.10333 | 0.97944 | -0.14408 | 0.98656 | -0.093596 | 38.27
24 | 0.020182 | 0.0050589 | -0.020159 | -0.0050506 | 2.2821e-05 | 8.2892e-06 | 0.030677 | 0.030677 | 0.030677 | 0.97895 | -0.14758 | 0.97781 | -0.15576 | 11.3618
25 | 0.014702 | 0.0036839 | -0.014687 | -0.0036786 | 1.5357e-05 | 5.2877e-06 | 0.022347 | 0.022347 | 0.022347 | 0.97895 | -0.14758 | 0.9779 | -0.15514 | 8.2767
26 | 0.0013589 | 0.00034018 | -0.0013589 | -0.00034028 | 2.2588e-08 | -1.0134e-07 | 0.0020495 | 0.0020496 | 0.0020496 | 0.98656 | -0.093596 | 0.98654 | -0.093717 | 0.7591
27 | -0.06985 | -0.017571 | 0.070081 | 0.017658 | 0.00023051 | 8.6953e-05 | 0.10538 | 0.10538 | 0.10538 | 0.98656 | -0.093596 | 0.98991 | -0.070013 | 19.5145
28 | 0.0052455 | 0.001313 | -0.0052427 | -0.0013128 | 2.7864e-06 | 1.9306e-07 | 0.0079819 | 0.0079822 | 0.0079822 | 0.97781 | -0.15576 | 0.97727 | -0.1596 | 2.9564
29 | 0.014173 | 0.0035504 | -0.014167 | -0.0035481 | 6.9082e-06 | 2.3585e-06 | 0.021566 | 0.021567 | 0.021567 | 0.9779 | -0.15514 | 0.9774 | -0.15866 | 7.9876
30 | 0.00051319 | 0.00012819 | -0.00051318 | -0.00012862 | 1.295e-08 | -4.2205e-07 | 0.00078075 | 0.0007809 | 0.0007809 | 0.9779 | -0.15514 | 0.97787 | -0.15532 | 0.28922
31 | 0.00016432 | 4.089e-05 | -0.00016432 | -4.1182e-05 | 8.771e-10 | -2.9196e-07 | 0.00024774 | 0.00024785 | 0.00024785 | 0.98654 | -0.093717 | 0.98653 | -0.093756 | 0.091795
32 | -0.072333 | -0.018222 | 0.072361 | 0.018232 | 2.7602e-05 | 1.0183e-05 | 0.10876 | 0.10876 | 0.10876 | 0.98991 | -0.070013 | 0.9903 | -0.067286 | 13.4274
33 | 0.0022519 | 0.00056329 | -0.0022518 | -0.00056349 | 1.4521e-07 | -2.0528e-07 | 0.0033846 | 0.0033847 | 0.0033847 | 0.98991 | -0.070013 | 0.98985 | -0.07048 | 1.2536
34 | 0.0052427 | 0.0013128 | -0.0052362 | -0.0013123 | 6.526e-06 | 4.562e-07 | 0.0079822 | 0.007983 | 0.007983 | 0.97727 | -0.1596 | 0.97602 | -0.16861 | 2.9567
35 | 0.0042282 | 0.0010582 | -0.0042278 | -0.0010583 | 4.3019e-07 | -4.3073e-08 | 0.0064366 | 0.0064367 | 0.0064367 | 0.9774 | -0.15866 | 0.9773 | -0.1594 | 2.384
36 | 0.0099383 | 0.0024899 | -0.0099148 | -0.0024829 | 2.3474e-05 | 6.9739e-06 | 0.01513 | 0.015131 | 0.015131 | 0.9774 | -0.15866 | 0.97502 | -0.17576 | 5.6039
37 | -0.062725 | -0.015805 | 0.062754 | 0.015817 | 2.9627e-05 | 1.1326e-05 | 0.094259 | 0.094259 | 0.094259 | 0.99052 | -0.065765 | 0.991 | -0.062391 | 34.9106
38 | 0.062725 | 0.015805 | -0.062605 | -0.01576 | 0.00011969 | 4.5757e-05 | 0.094259 | 0.094259 | 0.094259 | 0.99052 | -0.065765 | 0.98857 | -0.079427 | 34.9107
39 | 0.13736 | 0.034594 | -0.13726 | -0.034558 | 9.3928e-05 | 3.5716e-05 | 0.2063 | 0.2063 | 0.2063 | 0.991 | -0.062391 | 0.9903 | -0.067286 | 25.4696
40 | -0.20011 | -0.05041 | 0.20034 | 0.0505 | 0.00023414 | 8.957e-05 | 0.30056 | 0.30056 | 0.30056 | 0.991 | -0.062391 | 0.9922 | -0.054036 | 37.1065
41 | 0.060654 | 0.015271 | -0.060533 | -0.015224 | 0.00012064 | 4.6105e-05 | 0.091322 | 0.091322 | 0.091322 | 0.98857 | -0.079427 | 0.98654 | -0.093694 | 33.8231
42 | 0.064902 | 0.016326 | -0.064841 | -0.016303 | 6.1239e-05 | 2.3023e-05 | 0.097542 | 0.097542 | 0.097542 | 0.9903 | -0.067286 | 0.98934 | -0.074058 | 18.0634
43 | 0.0017606 | 0.0004404 | -0.0017605 | -0.00044067 | 1.063e-07 | -2.7174e-07 | 0.0026464 | 0.0026465 | 0.0026465 | 0.98985 | -0.07048 | 0.98979 | -0.070918 | 0.9802
44 | 0.0036311 | 0.0009087 | -0.0036309 | -0.00090874 | 1.5883e-07 | -4.3274e-08 | 0.0055281 | 0.0055281 | 0.0055281 | 0.9773 | -0.1594 | 0.97726 | -0.15972 | 2.0474
45 | 0.0012879 | 0.000322 | -0.0012877 | -0.00032273 | 1.5156e-07 | -7.2589e-07 | 0.0019652 | 0.0019654 | 0.0019654 | 0.97502 | -0.17576 | 0.9749 | -0.17662 | 0.72794
46 | 0.008627 | 0.0021609 | -0.0086202 | -0.0021591 | 6.8276e-06 | 1.8393e-06 | 0.013165 | 0.013166 | 0.013166 | 0.97502 | -0.17576 | 0.97423 | -0.18149 | 4.8762
47 | 0.0079053 | 0.0019799 | -0.0079016 | -0.001979 | 3.7251e-06 | 9.2308e-07 | 0.012074 | 0.012074 | 0.012074 | 0.97423 | -0.18149 | 0.97375 | -0.1849 | 4.4719
48 | -0.20272 | -0.051095 | 0.2033 | 0.051319 | 0.00058441 | 0.00022359 | 0.30412 | 0.30412 | 0.30412 | 0.9922 | -0.054036 | 0.99515 | -0.033507 | 37.5461
49 | 0.056468 | 0.014206 | -0.056373 | -0.014169 | 9.5559e-05 | 3.6484e-05 | 0.085191 | 0.085191 | 0.085191 | 0.98654 | -0.093694 | 0.98482 | -0.10585 | 31.5522
50 | 0.064247 | 0.016155 | -0.064215 | -0.016142 | 3.2322e-05 | 1.236e-05 | 0.096649 | 0.096649 | 0.096649 | 0.98934 | -0.074058 | 0.98883 | -0.07767 | 35.7961
51 | 0.00087224 | 0.00021827 | -0.00087221 | -0.0002186 | 2.8504e-08 | -3.3049e-07 | 0.0013112 | 0.0013113 | 0.0013113 | 0.98979 | -0.070918 | 0.98975 | -0.071154 | 0.48567
52 | 0.00088829 | 0.00022241 | -0.00088828 | -0.00022257 | 1.4906e-08 | -1.6643e-07 | 0.0013354 | 0.0013354 | 0.0013354 | 0.98979 | -0.070918 | 0.98977 | -0.071039 | 0.4946
53 | -0.041418 | -0.010379 | 0.04156 | 0.010433 | 0.00014166 | 5.3764e-05 | 0.063018 | 0.063018 | 0.063018 | 0.97797 | -0.15458 | 0.98142 | -0.12996 | 23.3401
54 | 0.00088702 | 0.00022116 | -0.00088692 | -0.00022228 | 1.0541e-07 | -1.1234e-06 | 0.0013492 | 0.0013496 | 0.0013496 | 0.97797 | -0.15458 | 0.97785 | -0.15545 | 0.49987
55 | -0.054046 | -0.013562 | 0.054228 | 0.013632 | 0.00018148 | 6.925e-05 | 0.08195 | 0.08195 | 0.08195 | 0.98142 | -0.12996 | 0.98482 | -0.10585 | 30.3519
56 | 0.0048362 | 0.0012107 | -0.004836 | -0.0012107 | 2.761e-07 | 5.4094e-09 | 0.0073899 | 0.0073899 | 0.0073899 | 0.97375 | -0.1849 | 0.9737 | -0.18531 | 2.737
57 | 0.0043883 | 0.0010985 | -0.0043883 | -0.0010985 | 1.2293e-08 | -7.2103e-10 | 0.0067058 | 0.0067058 | 0.0067058 | 0.9737 | -0.18531 | 0.97369 | -0.18533 | 2.4836
58 | 0.0030744 | 0.00076922 | -0.0030741 | -0.00076936 | 2.5554e-07 | -1.3249e-07 | 0.0046978 | 0.0046979 | 0.0046979 | 0.97369 | -0.18533 | 0.97361 | -0.18593 | 1.74
59 | 0.0025197 | 0.00063042 | -0.0025196 | -0.00063057 | 1.6618e-07 | -1.5943e-07 | 0.0038506 | 0.0038507 | 0.0038507 | 0.97361 | -0.18593 | 0.97354 | -0.18641 | 1.4262
60 | 0.0016384 | 0.00040974 | -0.0016383 | -0.00040994 | 7.2703e-08 | -2.0309e-07 | 0.0025039 | 0.002504 | 0.002504 | 0.97354 | -0.18641 | 0.9735 | -0.18673 | 0.92741
61 | 0.0030343 | 0.00075923 | -0.0030339 | -0.00075948 | 4.5693e-07 | -2.5406e-07 | 0.0046197 | 0.0046199 | 0.0046199 | 0.97726 | -0.15972 | 0.97711 | -0.16081 | 1.7111
62 | 0.00098055 | 0.00024508 | -0.0009805 | -0.00024552 | 5.168e-08 | -4.3858e-07 | 0.0014986 | 0.0014987 | 0.0014987 | 0.9735 | -0.18673 | 0.97345 | -0.18712 | 0.55508
63 | -0.20975 | -0.052935 | 0.21074 | 0.053314 | 0.0009914 | 0.00037941 | 0.31376 | 0.31376 | 0.31376 | 0.99515 | -0.033507 | 1 | 0 | 38.7363
64 | 0.0009805 | 0.00024552 | -0.00098047 | -0.00024573 | 2.4724e-08 | -2.0977e-07 | 0.0014987 | 0.0014988 | 0.0014988 | 0.97345 | -0.18712 | 0.97342 | -0.1873 | 0.55511
65 | 0.0049782 | 0.0012292 | -0.0049777 | -0.0012292 | 5.4123e-07 | 2.2335e-08 | 0.00761 | 0.0076101 | 0.0076101 | 0.97256 | -0.19375 | 0.97245 | -0.19456 | 2.8186
66 | -0.027786 | -0.0069626 | 0.027802 | 0.0069686 | 1.6054e-05 | 5.9931e-06 | 0.04223 | 0.04223 | 0.04223 | 0.97906 | -0.14693 | 0.97964 | -0.14276 | 15.6408
67 | 0.0044767 | 0.0011036 | -0.0044753 | -0.0011037 | 1.4169e-06 | -5.6326e-08 | 0.0068436 | 0.0068438 | 0.0068438 | 0.97245 | -0.19456 | 0.97214 | -0.19692 | 2.5347
68 | -0.029144 | -0.0073048 | 0.029161 | 0.0073114 | 1.763e-05 | 6.5992e-06 | 0.044268 | 0.044268 | 0.044268 | 0.97964 | -0.14276 | 0.98025 | -0.13839 | 16.3955
69 | 0.0045339 | 0.0011359 | -0.0045328 | -0.0011359 | 1.0703e-06 | -6.0901e-08 | 0.0068226 | 0.0068228 | 0.0068228 | 0.98883 | -0.07767 | 0.98859 | -0.079376 | 2.527
70 | 0.059681 | 0.015006 | -0.059628 | -0.014986 | 5.259e-05 | 2.0093e-05 | 0.089827 | 0.089827 | 0.089827 | 0.98883 | -0.07767 | 0.98793 | -0.084 | 33.2692
71 | 0.0012463 | 0.00031206 | -0.0012462 | -0.00031226 | 3.9301e-08 | -2.039e-07 | 0.0018978 | 0.0018979 | 0.0018979 | 0.97711 | -0.16081 | 0.97707 | -0.16104 | 0.70293
72 | 0.0017876 | 0.00044743 | -0.0017874 | -0.00044776 | 1.4274e-07 | -3.3174e-07 | 0.0027221 | 0.0027222 | 0.0027222 | 0.97711 | -0.16081 | 0.97703 | -0.16139 | 1.0082
73 | 0.00058155 | 0.00014567 | -0.00058155 | -0.00014575 | 3.0238e-09 | -7.6212e-08 | 0.00088564 | 0.00088566 | 0.00088566 | 0.97707 | -0.16104 | 0.97707 | -0.16107 | 0.32802
74 | 0.0017874 | 0.00044776 | -0.0017874 | -0.00044795 | 8.482e-08 | -1.9707e-07 | 0.0027222 | 0.0027223 | 0.0027223 | 0.97703 | -0.16139 | 0.97698 | -0.16173 | 1.0083
75 | -0.00060656 | -0.00015202 | 0.00060656 | 0.00015197 | 2.0637e-09 | -5.0322e-08 | 0.0009119 | 0.00091188 | 0.0009119 | 0.98977 | -0.071064 | 0.98977 | -0.071039 | 0.33774
76 | -0.0031199 | -0.00078191 | 0.0031199 | 0.00078188 | 6.6811e-08 | -3.5836e-08 | 0.0047097 | 0.0047097 | 0.0047097 | 0.98572 | -0.099686 | 0.98574 | -0.099531 | 1.7443
77 | -0.0041517 | -0.0010403 | 0.0041522 | 0.0010402 | 5.822e-07 | -7.8956e-08 | 0.006267 | 0.0062669 | 0.006267 | 0.98574 | -0.099531 | 0.98588 | -0.098518 | 2.3211
78 | 0.0010317 | 0.00025841 | -0.0010317 | -0.00025857 | 1.9418e-08 | -1.5608e-07 | 0.0015574 | 0.0015574 | 0.0015574 | 0.98574 | -0.099531 | 0.98572 | -0.099667 | 0.57683
79 | -0.0015718 | -0.00039394 | 0.0015718 | 0.00039388 | 1.8074e-08 | -5.4703e-08 | 0.0024097 | 0.0024097 | 0.0024097 | 0.97062 | -0.20815 | 0.97063 | -0.20807 | 0.89248
80 | 0.00066762 | 0.00016298 | -0.00066739 | -0.00016711 | 2.2273e-07 | -4.129e-06 | 0.0010221 | 0.0010236 | 0.0010236 | 0.97051 | -0.20907 | 0.97018 | -0.21154 | 0.3791
81 | 0.00066025 | 0.00016224 | -0.00066008 | -0.00016543 | 1.6835e-07 | -3.1913e-06 | 0.0010112 | 0.0010123 | 0.0010123 | 0.97051 | -0.20907 | 0.97025 | -0.21095 | 0.37494
82 | 0.00049508 | 0.00012393 | -0.00049508 | -0.00012405 | 3.7449e-09 | -1.271e-07 | 0.00075928 | 0.00075933 | 0.00075933 | 0.97018 | -0.21154 | 0.97017 | -0.2116 | 0.28123
83 | -0.0044743 | -0.0011037 | 0.0044753 | 0.0011037 | 1.0085e-06 | -3.9829e-08 | 0.0068439 | 0.0068438 | 0.0068439 | 0.97191 | -0.1986 | 0.97214 | -0.19692 | 2.5348
84 | 0.00030938 | 7.7513e-05 | -0.00030938 | -7.7537e-05 | 2.7611e-10 | -2.4162e-08 | 0.0004745 | 0.00047451 | 0.00047451 | 0.97017 | -0.2116 | 0.97017 | -0.2116 | 0.17575
85 | -0.0076114 | -0.001907 | 0.0076124 | 0.0019072 | 9.9164e-07 | 2.2783e-07 | 0.011488 | 0.011488 | 0.011488 | 0.98588 | -0.098518 | 0.98601 | -0.097576 | 4.2547
86 | 0.0034591 | 0.00086679 | -0.0034589 | -0.00086688 | 2.3864e-07 | -8.7109e-08 | 0.0052209 | 0.005221 | 0.005221 | 0.98588 | -0.098518 | 0.98581 | -0.099016 | 1.9337
87 | 0.0017798 | 0.00044591 | -0.0017798 | -0.00044605 | 5.791e-08 | -1.418e-07 | 0.0026859 | 0.002686 | 0.002686 | 0.98601 | -0.097576 | 0.98598 | -0.097811 | 0.9948
88 | -0.0093922 | -0.0023531 | 0.0093944 | 0.0023538 | 2.2502e-06 | 6.3645e-07 | 0.014174 | 0.014174 | 0.014174 | 0.98601 | -0.097576 | 0.98626 | -0.095844 | 5.2495
89 | 0.0017148 | 0.00042976 | -0.0017148 | -0.00042976 | 2.8223e-10 | -7.5185e-10 | 0.0025883 | 0.0025883 | 0.0025883 | 0.98581 | -0.099016 | 0.98581 | -0.099017 | 0.95864
90 | -0.035074 | -0.0087931 | 0.035078 | 0.0087944 | 3.3167e-06 | 1.252e-06 | 0.053244 | 0.053244 | 0.053244 | 0.98025 | -0.13839 | 0.98035 | -0.13771 | 19.7199
91 | 0.0059131 | 0.0014817 | -0.0059124 | -0.0014817 | 7.01e-07 | 9.386e-08 | 0.0089759 | 0.008976 | 0.008976 | 0.98025 | -0.13839 | 0.98013 | -0.13925 | 3.3244
92 | -0.01112 | -0.0027863 | 0.011122 | 0.002787 | 2.1389e-06 | 6.6723e-07 | 0.016778 | 0.016777 | 0.016778 | 0.98626 | -0.095844 | 0.98645 | -0.094455 | 6.2139
93 | -0.035567 | -0.0089169 | 0.035607 | 0.0089322 | 4.0499e-05 | 1.5295e-05 | 0.053986 | 0.053986 | 0.053986 | 0.98035 | -0.13771 | 0.9815 | -0.1295 | 19.9948
94 | 0.0052772 | 0.0013225 | -0.0052765 | -0.0013224 | 6.7979e-07 | 4.758e-08 | 0.0080116 | 0.0080117 | 0.0080117 | 0.98013 | -0.13925 | 0.98 | -0.14018 | 2.9673
95 | -0.041233 | -0.010353 | 0.041258 | 0.010363 | 2.4996e-05 | 9.483e-06 | 0.062364 | 0.062364 | 0.062364 | 0.98394 | -0.11215 | 0.98456 | -0.10779 | 23.0977
96 | 0.04083 | 0.010252 | -0.040792 | -0.010238 | 3.7914e-05 | 1.438e-05 | 0.061754 | 0.061754 | 0.061754 | 0.98394 | -0.11215 | 0.983 | -0.11884 | 22.8718
97 | -0.041818 | -0.010503 | 0.041922 | 0.010543 | 0.00010382 | 3.9399e-05 | 0.06321 | 0.06321 | 0.06321 | 0.98456 | -0.10779 | 0.98708 | -0.089981 | 23.4111
98 | 0.040323 | 0.01012 | -0.040318 | -0.010118 | 5.1915e-06 | 1.9684e-06 | 0.061045 | 0.061045 | 0.061045 | 0.983 | -0.11884 | 0.98287 | -0.11977 | 22.6091
99 | -0.042621 | -0.010718 | 0.042657 | 0.010731 | 3.5561e-05 | 1.3501e-05 | 0.064265 | 0.064264 | 0.064265 | 0.98708 | -0.089981 | 0.98793 | -0.084 | 23.8017
100 | 0.039644 | 0.0099497 | -0.039618 | -0.0099395 | 2.6794e-05 | 1.0154e-05 | 0.060025 | 0.060025 | 0.060025 | 0.98287 | -0.11977 | 0.98218 | -0.12464 | 22.2314
101 | 0.016971 | 0.0042547 | -0.016957 | -0.0042496 | 1.4684e-05 | 5.1871e-06 | 0.025563 | 0.025563 | 0.025563 | 0.98793 | -0.084 | 0.98705 | -0.090251 | 9.4677
102 | 0.002554 | 0.00063943 | -0.0025538 | -0.00063962 | 1.9714e-07 | -1.9125e-07 | 0.0038691 | 0.0038692 | 0.0038692 | 0.98218 | -0.12464 | 0.9821 | -0.1252 | 1.433
103 | 0.036152 | 0.0090719 | -0.036128 | -0.0090627 | 2.4355e-05 | 9.2028e-06 | 0.054775 | 0.054775 | 0.054775 | 0.98218 | -0.12464 | 0.9815 | -0.1295 | 20.2869
104 | 0.00091169 | 0.00022823 | -0.00091166 | -0.00022848 | 2.4836e-08 | -2.5449e-07 | 0.0013811 | 0.0013812 | 0.0013812 | 0.98218 | -0.12464 | 0.98216 | -0.12484 | 0.51156
105 | 0.014482 | 0.0036293 | -0.014477 | -0.0036275 | 5.2856e-06 | 1.8058e-06 | 0.021832 | 0.021832 | 0.021832 | 0.98705 | -0.090251 | 0.98667 | -0.092888 | 8.086
106 | 0.0020336 | 0.00050926 | -0.0020335 | -0.00050948 | 1.283e-07 | -2.247e-07 | 0.0030811 | 0.0030811 | 0.0030811 | 0.9821 | -0.1252 | 0.98204 | -0.12566 | 1.1412
107 | 0.0014352 | 0.00035953 | -0.0014352 | -0.00035964 | 2.7483e-08 | -1.0727e-07 | 0.0021746 | 0.0021746 | 0.0021746 | 0.98204 | -0.12566 | 0.98202 | -0.12579 | 0.80542
108 | 0.00083686 | 0.00020969 | -0.00083686 | -0.00020974 | 3.7009e-09 | -4.5243e-08 | 0.001268 | 0.0012681 | 0.0012681 | 0.98202 | -0.12579 | 0.98202 | -0.12583 | 0.46965
109 | 0.012827 | 0.0032141 | -0.012824 | -0.0032132 | 2.7803e-06 | 9.1729e-07 | 0.019344 | 0.019344 | 0.019344 | 0.98667 | -0.092888 | 0.98645 | -0.094455 | 7.1646
110 | 0.0017018 | 0.00042621 | -0.0017017 | -0.00042648 | 9.7139e-08 | -2.6422e-07 | 0.0025669 | 0.002567 | 0.002567 | 0.98645 | -0.094455 | 0.9864 | -0.094867 | 0.95075
111 | 0.0037954 | 0.00095112 | -0.0037952 | -0.00095116 | 1.755e-07 | -4.2989e-08 | 0.0057127 | 0.0057128 | 0.0057128 | 0.98859 | -0.079376 | 0.98854 | -0.07971 | 2.1158

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.21664 | 0.054591

## res_load
| p_mw | q_mvar
0 | 0.00011497 | 2.8814e-05
1 | 0.00020247 | 5.0745e-05
2 | 4.2391e-05 | 1.0624e-05
3 | 0.00021337 | 5.3476e-05
4 | 0.00010073 | 2.5245e-05
5 | 0.00042817 | 0.00010731
6 | 0.00026275 | 6.5851e-05
7 | 7.8496e-05 | 1.9673e-05
8 | 0.00057685 | 0.00014457
9 | 0.0040484 | 0.0010146
10 | 0.0010447 | 0.00026183
11 | 0.0010355 | 0.00025952
12 | 0.010837 | 0.002716
13 | 0.033112 | 0.0082987
14 | 0.014913 | 0.0037376
15 | 0.0011946 | 0.00029939
16 | 0.00051318 | 0.00012862
17 | 0.00016432 | 4.1182e-05
18 | 0.0019509 | 0.00048895
19 | 0.00049113 | 0.00012309
20 | 0.0052362 | 0.0013123
21 | 0.00059676 | 0.00014956
22 | 0.0012877 | 0.00032273
23 | 0.00071482 | 0.00017915
24 | 0.0023743 | 0.00059507
25 | 0.0040651 | 0.0010188
26 | 0.00059354 | 0.00014876
27 | 0.040531 | 0.010158
28 | 0.012487 | 0.0031294
29 | 0.00088692 | 0.00022228
30 | 0.0021451 | 0.0005376
31 | 0.0030654 | 0.00076826
32 | 0.00044769 | 0.0001122
33 | 0.0013139 | 0.00032929
34 | 0.00055438 | 0.00013894
35 | 0.00088115 | 0.00022084
36 | 0.00059657 | 0.00014952
37 | 0.0006578 | 0.00016486
38 | 0.0064478 | 0.001616
39 | 0.00098047 | 0.00024573
40 | 0.0050955 | 0.0012771
41 | 0.0050151 | 0.0012569
42 | 0.00050096 | 0.00012555
43 | 0.0013416 | 0.00033624
44 | 0.00066468 | 0.00016659
45 | 0.00058155 | 0.00014575
46 | 0.0017874 | 0.00044795
47 | 0.00060656 | 0.00015202
48 | 0.00028172 | 7.0605e-05
49 | 0.00087221 | 0.0002186
50 | 0.0031199 | 0.00078191
51 | 0.0015718 | 0.00039394
52 | 5.5778e-05 | 1.3979e-05
53 | 0.00017231 | 4.3185e-05
54 | 0.00066008 | 0.00016543
55 | 0.0001492 | 3.7394e-05
56 | 0.0001857 | 4.6542e-05
57 | 0.00030938 | 7.7537e-05
58 | 0.0010317 | 0.00025857
59 | 0.0017441 | 0.00043712
60 | 0.0017798 | 0.00044605
61 | 0.0017259 | 0.00043255
62 | 0.0017148 | 0.00042976
63 | 0.00048899 | 0.00012255
64 | 0.00063517 | 0.00015919
65 | 0.00040342 | 0.00010111
66 | 0.00055987 | 0.00014032
67 | 0.00046858 | 0.00011744
68 | 0.00069963 | 0.00017534
69 | 0.00067357 | 0.00016881
70 | 0.0024747 | 0.00062021
71 | 0.00052017 | 0.00013037
72 | 0.00052036 | 0.00013041
73 | 0.00091166 | 0.00022848
74 | 0.0005983 | 0.00014995
75 | 0.0005983 | 0.00014995
76 | 0.0016496 | 0.00041342
77 | 0.0017017 | 0.00042648
78 | 0.00073748 | 0.00018483
79 | 0.0037952 | 0.00095116
80 | 0.00083686 | 0.00020974
81 | 0.0052765 | 0.0013224

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1