## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1150-7_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1150-7_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1150-7_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1150-7_0_3_node_15 | 0.4 | n |  | TRUE
4 | bus_LV_1150-7_0_3_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1150-7_0_3_node_55 | 0.4 | n |  | TRUE
6 | bus_LV_1150-7_0_3_node_49 | 0.4 | n |  | TRUE
7 | bus_LV_1150-7_0_3_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_1150-7_0_3_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_1150-7_0_3_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1150-7_0_3_node_14 | 0.4 | n |  | TRUE
11 | bus_LV_1150-7_0_3_node_57 | 0.4 | n |  | TRUE
12 | bus_LV_1150-7_0_3_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_1150-7_0_3_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_1150-7_0_3_node_54 | 0.4 | n |  | TRUE
15 | bus_LV_1150-7_0_3_node_4 | 0.4 | n |  | TRUE
16 | bus_LV_1150-7_0_3_node_5 | 0.4 | n |  | TRUE
17 | bus_LV_1150-7_0_3_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_1150-7_0_3_node_8 | 0.4 | n |  | TRUE
19 | bus_LV_1150-7_0_3_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1150-7_0_3_node_13 | 0.4 | n |  | TRUE
21 | bus_LV_1150-7_0_3_node_6 | 0.4 | n |  | TRUE
22 | bus_LV_1150-7_0_3_node_7 | 0.4 | n |  | TRUE
23 | bus_LV_1150-7_0_3_node_10 | 0.4 | n |  | TRUE
24 | bus_LV_1150-7_0_3_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_1150-7_0_3_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1150-7_0_3_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1150-7_0_3_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1150-7_0_3_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1150-7_0_3_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_1150-7_0_3_node_56 | 0.4 | n |  | TRUE
31 | bus_LV_1150-7_0_3_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1150-7_0_3_node_46 | 0.4 | n |  | TRUE
33 | bus_LV_1150-7_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1150-7_0_3_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_1150-7_0_3_node_150 | 0.4 | n |  | TRUE
36 | bus_LV_1150-7_0_3_node_52 | 0.4 | n |  | TRUE
37 | bus_LV_1150-7_0_3_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_1150-7_0_3_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1150-7_0_3_node_47 | 0.4 | n |  | TRUE
40 | bus_LV_1150-7_0_3_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1150-7_0_3_node_41 | 0.4 | n |  | TRUE
42 | bus_LV_1150-7_0_3_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_1150-7_0_3_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_1150-7_0_3_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_1150-7_0_3_node_44 | 0.4 | n |  | TRUE
46 | bus_LV_1150-7_0_3_node_45 | 0.4 | n |  | TRUE
47 | bus_LV_1150-7_0_3_node_53 | 0.4 | n |  | TRUE
48 | bus_LV_1150-7_0_3_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_1150-7_0_3_node_33 | 0.4 | n |  | TRUE
50 | bus_LV_1150-7_0_3_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_1150-7_0_3_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_1150-7_0_3_node_35 | 0.4 | n |  | TRUE
53 | bus_LV_1150-7_0_3_node_38 | 0.4 | n |  | TRUE
54 | bus_LV_1150-7_0_3_node_40 | 0.4 | n |  | TRUE
55 | bus_LV_1150-7_0_3_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_1150-7_0_3_node_51 | 0.4 | n |  | TRUE
57 | bus_LV_1150-7_0_3_node_62 | 0.4 | n |  | TRUE
58 | bus_LV_1150-7_0_3_node_60 | 0.4 | n |  | TRUE
59 | bus_LV_1150-7_0_3_node_130 | 0.4 | n |  | TRUE
60 | bus_LV_1150-7_0_3_node_105 | 0.4 | n |  | TRUE
61 | bus_LV_1150-7_0_3_node_59 | 0.4 | n |  | TRUE
62 | bus_LV_1150-7_0_3_node_61 | 0.4 | n |  | TRUE
63 | bus_LV_1150-7_0_3_node_63 | 0.4 | n |  | TRUE
64 | bus_LV_1150-7_0_3_node_64 | 0.4 | n |  | TRUE
65 | bus_LV_1150-7_0_3_node_68 | 0.4 | n |  | TRUE
66 | bus_LV_1150-7_0_3_node_65 | 0.4 | n |  | TRUE
67 | bus_LV_1150-7_0_3_node_142 | 0.4 | n |  | TRUE
68 | bus_LV_1150-7_0_3_node_129 | 0.4 | n |  | TRUE
69 | bus_LV_1150-7_0_3_node_119 | 0.4 | n |  | TRUE
70 | bus_LV_1150-7_0_3_node_66 | 0.4 | n |  | TRUE
71 | bus_LV_1150-7_0_3_node_143 | 0.4 | n |  | TRUE
72 | bus_LV_1150-7_0_3_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_1150-7_0_3_node_98 | 0.4 | n |  | TRUE
74 | bus_LV_1150-7_0_3_node_97 | 0.4 | n |  | TRUE
75 | bus_LV_1150-7_0_3_node_135 | 0.4 | n |  | TRUE
76 | bus_LV_1150-7_0_3_node_118 | 0.4 | n |  | TRUE
77 | bus_LV_1150-7_0_3_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_1150-7_0_3_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_1150-7_0_3_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_1150-7_0_3_node_72 | 0.4 | n |  | TRUE
81 | bus_LV_1150-7_0_3_node_73 | 0.4 | n |  | TRUE
82 | bus_LV_1150-7_0_3_node_74 | 0.4 | n |  | TRUE
83 | bus_LV_1150-7_0_3_node_75 | 0.4 | n |  | TRUE
84 | bus_LV_1150-7_0_3_node_91 | 0.4 | n |  | TRUE
85 | bus_LV_1150-7_0_3_node_110 | 0.4 | n |  | TRUE
86 | bus_LV_1150-7_0_3_node_92 | 0.4 | n |  | TRUE
87 | bus_LV_1150-7_0_3_node_108 | 0.4 | n |  | TRUE
88 | bus_LV_1150-7_0_3_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_1150-7_0_3_node_113 | 0.4 | n |  | TRUE
90 | bus_LV_1150-7_0_3_node_94 | 0.4 | n |  | TRUE
91 | bus_LV_1150-7_0_3_node_81 | 0.4 | n |  | TRUE
92 | bus_LV_1150-7_0_3_node_76 | 0.4 | n |  | TRUE
93 | bus_LV_1150-7_0_3_node_77 | 0.4 | n |  | TRUE
94 | bus_LV_1150-7_0_3_node_78 | 0.4 | n |  | TRUE
95 | bus_LV_1150-7_0_3_node_79 | 0.4 | n |  | TRUE
96 | bus_LV_1150-7_0_3_node_82 | 0.4 | n |  | TRUE
97 | bus_LV_1150-7_0_3_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_1150-7_0_3_node_133 | 0.4 | n |  | TRUE
99 | bus_LV_1150-7_0_3_node_89 | 0.4 | n |  | TRUE
100 | bus_LV_1150-7_0_3_node_90 | 0.4 | n |  | TRUE
101 | bus_LV_1150-7_0_3_node_131 | 0.4 | n |  | TRUE
102 | bus_LV_1150-7_0_3_node_93 | 0.4 | n |  | TRUE
103 | bus_LV_1150-7_0_3_node_84 | 0.4 | n |  | TRUE
104 | bus_LV_1150-7_0_3_node_85 | 0.4 | n |  | TRUE
105 | bus_LV_1150-7_0_3_node_86 | 0.4 | n |  | TRUE
106 | bus_LV_1150-7_0_3_node_87 | 0.4 | n |  | TRUE
107 | bus_LV_1150-7_0_3_node_126 | 0.4 | n |  | TRUE
108 | bus_LV_1150-7_0_3_node_147 | 0.4 | n |  | TRUE
109 | bus_LV_1150-7_0_3_node_125 | 0.4 | n |  | TRUE
110 | bus_LV_1150-7_0_3_node_146 | 0.4 | n |  | TRUE
111 | bus_LV_1150-7_0_3_node_132 | 0.4 | n |  | TRUE
112 | bus_LV_1150-7_0_3_node_95 | 0.4 | n |  | TRUE
113 | bus_LV_1150-7_0_3_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_1150-7_0_3_node_99 | 0.4 | n |  | TRUE
115 | bus_LV_1150-7_0_3_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_1150-7_0_3_node_103 | 0.4 | n |  | TRUE
117 | bus_LV_1150-7_0_3_node_141 | 0.4 | n |  | TRUE
118 | bus_LV_1150-7_0_3_node_101 | 0.4 | n |  | TRUE
119 | bus_LV_1150-7_0_3_node_124 | 0.4 | n |  | TRUE
120 | bus_LV_1150-7_0_3_node_102 | 0.4 | n |  | TRUE
121 | bus_LV_1150-7_0_3_node_104 | 0.4 | n |  | TRUE
122 | bus_LV_1150-7_0_3_node_106 | 0.4 | n |  | TRUE
123 | bus_LV_1150-7_0_3_node_148 | 0.4 | n |  | TRUE
124 | bus_LV_1150-7_0_3_node_107 | 0.4 | n |  | TRUE
125 | bus_LV_1150-7_0_3_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_1150-7_0_3_node_111 | 0.4 | n |  | TRUE
127 | bus_LV_1150-7_0_3_node_112 | 0.4 | n |  | TRUE
128 | bus_LV_1150-7_0_3_node_137 | 0.4 | n |  | TRUE
129 | bus_LV_1150-7_0_3_node_114 | 0.4 | n |  | TRUE
130 | bus_LV_1150-7_0_3_node_115 | 0.4 | n |  | TRUE
131 | bus_LV_1150-7_0_3_node_116 | 0.4 | n |  | TRUE
132 | bus_LV_1150-7_0_3_node_117 | 0.4 | n |  | TRUE
133 | bus_LV_1150-7_0_3_node_138 | 0.4 | n |  | TRUE
134 | bus_LV_1150-7_0_3_node_139 | 0.4 | n |  | TRUE
135 | bus_LV_1150-7_0_3_node_120 | 0.4 | n |  | TRUE
136 | bus_LV_1150-7_0_3_node_121 | 0.4 | n |  | TRUE
137 | bus_LV_1150-7_0_3_node_122 | 0.4 | n |  | TRUE
138 | bus_LV_1150-7_0_3_node_123 | 0.4 | n |  | TRUE
139 | bus_LV_1150-7_0_3_node_128 | 0.4 | n |  | TRUE
140 | bus_LV_1150-7_0_3_node_127 | 0.4 | n |  | TRUE
141 | bus_LV_1150-7_0_3_node_140 | 0.4 | n |  | TRUE
142 | bus_LV_1150-7_0_3_node_149 | 0.4 | n |  | TRUE
143 | bus_LV_1150-7_0_3_node_153 | 0.4 | n |  | TRUE
144 | bus_LV_1150-7_0_3_node_152 | 0.4 | n |  | TRUE
145 | bus_LV_1150-7_0_3_node_144 | 0.4 | n |  | TRUE
146 | bus_LV_1150-7_0_3_node_145 | 0.4 | n |  | TRUE
147 | bus_LV_1150-7_0_3_node_151 | 0.4 | n |  | TRUE
148 | bus_MV_129_0_node_230 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1150-7_0_3_load_0 | 0 | 0.0011285 | 0.00028284 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1150-7_0_3_load_1 | 1 | 0.000421 | 0.00010551 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1150-7_0_3_load_2 | 2 | 0.00020259 | 5.0773e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1150-7_0_3_load_3 | 4 | 0.00017457 | 4.3751e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1150-7_0_3_load_55 | 5 | 0.00013447 | 3.3701e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1150-7_0_3_load_49 | 6 | 0.00013955 | 3.4974e-05 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1150-7_0_3_load_50 | 7 | 0.00061088 | 0.0001531 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1150-7_0_3_load_28 | 8 | 0.00048456 | 0.00012144 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1150-7_0_3_load_14 | 10 | 0.00019149 | 4.7992e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1150-7_0_3_load_57 | 11 | 0.0011386 | 0.00028536 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1150-7_0_3_load_21 | 12 | 0.00022586 | 5.6605e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1150-7_0_3_load_29 | 13 | 0.0013426 | 0.0003365 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1150-7_0_3_load_4 | 15 | 0.0019102 | 0.00047875 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1150-7_0_3_load_5 | 16 | 0.00015873 | 3.9782e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1150-7_0_3_load_12 | 19 | 0.00044489 | 0.0001115 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1150-7_0_3_load_13 | 20 | 0.00041821 | 0.00010481 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1150-7_0_3_load_6 | 21 | 0.00043547 | 0.00010914 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1150-7_0_3_load_7 | 22 | 0.00014875 | 3.7279e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1150-7_0_3_load_10 | 23 | 0.00025983 | 6.512e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1150-7_0_3_load_17 | 24 | 9.2745e-05 | 2.3244e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1150-7_0_3_load_20 | 27 | 0.00067596 | 0.00016941 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1150-7_0_3_load_22 | 28 | 0.0020397 | 0.00051121 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1150-7_0_3_load_58 | 29 | 0.0025427 | 0.00063727 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1150-7_0_3_load_56 | 30 | 0.0055437 | 0.0013894 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1150-7_0_3_load_27 | 31 | 0.00059641 | 0.00014947 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1150-7_0_3_load_46 | 32 | 0.0019569 | 0.00049046 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1150-7_0_3_load_23 | 33 | 0.0007906 | 0.00019814 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1150-7_0_3_load_150 | 35 | 0.0026295 | 0.00065901 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1150-7_0_3_load_48 | 37 | 0.0017835 | 0.000447 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1150-7_0_3_load_25 | 38 | 6.0176e-05 | 1.5081e-05 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1150-7_0_3_load_47 | 39 | 0.0014549 | 0.00036463 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1150-7_0_3_load_24 | 40 | 0.00026677 | 6.6859e-05 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1150-7_0_3_load_41 | 41 | 0.00078764 | 0.0001974 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1150-7_0_3_load_42 | 42 | 0.00032312 | 8.098e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1150-7_0_3_load_45 | 46 | 0.00065411 | 0.00016394 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1150-7_0_3_load_53 | 47 | 0.00024882 | 6.236e-05 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1150-7_0_3_load_33 | 49 | 0.0015795 | 0.00039586 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1150-7_0_3_load_34 | 50 | 0.0019613 | 0.00049154 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1150-7_0_3_load_38 | 53 | 0.0018287 | 0.00045831 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1150-7_0_3_load_40 | 54 | 0.0015838 | 0.00039694 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1150-7_0_3_load_39 | 55 | 0.0006999 | 0.00017541 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1150-7_0_3_load_51 | 56 | 0.001181 | 0.00029598 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1150-7_0_3_load_62 | 57 | 0.0041026 | 0.0010282 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1150-7_0_3_load_60 | 58 | 0.0023473 | 0.0005883 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1150-7_0_3_load_130 | 59 | 0.0070177 | 0.0017588 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1150-7_0_3_load_105 | 60 | 0.0068934 | 0.0017276 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1150-7_0_3_load_59 | 61 | 0.0018395 | 0.00046102 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1150-7_0_3_load_61 | 62 | 0.0032247 | 0.00080818 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1150-7_0_3_load_64 | 64 | 0.0016445 | 0.00041215 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1150-7_0_3_load_65 | 66 | 0.0021071 | 0.00052808 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1150-7_0_3_load_142 | 67 | 0.002292 | 0.00057442 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1150-7_0_3_load_129 | 68 | 0.0026503 | 0.00066423 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1150-7_0_3_load_119 | 69 | 0.0030982 | 0.00077647 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1150-7_0_3_load_66 | 70 | 0.0027643 | 0.0006928 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1150-7_0_3_load_143 | 71 | 0.0039723 | 0.00099555 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1150-7_0_3_load_67 | 72 | 0.0011115 | 0.00027856 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1150-7_0_3_load_98 | 73 | 0.0017166 | 0.00043021 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1150-7_0_3_load_97 | 74 | 0.0018394 | 0.000461 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1150-7_0_3_load_135 | 75 | 0.0015951 | 0.00039976 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1150-7_0_3_load_118 | 76 | 0.0024579 | 0.00061602 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1150-7_0_3_load_69 | 77 | 0.0020382 | 0.00051082 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1150-7_0_3_load_70 | 78 | 0.0013723 | 0.00034393 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1150-7_0_3_load_72 | 80 | 0.0013693 | 0.00034319 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1150-7_0_3_load_73 | 81 | 0.0017641 | 0.00044212 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1150-7_0_3_load_74 | 82 | 0.002649 | 0.0006639 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1150-7_0_3_load_75 | 83 | 0.0017652 | 0.00044241 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1150-7_0_3_load_91 | 84 | 0.0030639 | 0.00076789 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1150-7_0_3_load_110 | 85 | 0.0019535 | 0.00048958 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1150-7_0_3_load_92 | 86 | 0.001487 | 0.00037268 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1150-7_0_3_load_108 | 87 | 0.0024603 | 0.00061661 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1150-7_0_3_load_113 | 89 | 0.0049985 | 0.0012527 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1150-7_0_3_load_94 | 90 | 0.0050007 | 0.0012533 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1150-7_0_3_load_76 | 92 | 0.0029205 | 0.00073194 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1150-7_0_3_load_77 | 93 | 0.0033138 | 0.00083051 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1150-7_0_3_load_78 | 94 | 0.0024933 | 0.00062488 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1150-7_0_3_load_79 | 95 | 0.0032683 | 0.00081912 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1150-7_0_3_load_82 | 96 | 0.0016492 | 0.00041332 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1150-7_0_3_load_88 | 97 | 0.0023263 | 0.00058303 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1150-7_0_3_load_133 | 98 | 0.0025765 | 0.00064573 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1150-7_0_3_load_89 | 99 | 0.0016576 | 0.00041542 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1150-7_0_3_load_90 | 100 | 0.0014546 | 0.00036457 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1150-7_0_3_load_131 | 101 | 0.0031553 | 0.0007908 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1150-7_0_3_load_93 | 102 | 0.0017024 | 0.00042665 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1150-7_0_3_load_84 | 103 | 0.0014735 | 0.00036928 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1150-7_0_3_load_87 | 106 | 0.0022937 | 0.00057485 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1150-7_0_3_load_126 | 107 | 0.001906 | 0.00047768 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1150-7_0_3_load_147 | 108 | 0.001587 | 0.00039774 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1150-7_0_3_load_125 | 109 | 0.0024444 | 0.00061262 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1150-7_0_3_load_146 | 110 | 0.0021081 | 0.00052834 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1150-7_0_3_load_132 | 111 | 0.0025776 | 0.000646 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1150-7_0_3_load_95 | 112 | 0.0016041 | 0.00040203 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1150-7_0_3_load_96 | 113 | 0.0020946 | 0.00052496 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1150-7_0_3_load_103 | 116 | 0.0019627 | 0.00049189 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1150-7_0_3_load_141 | 117 | 0.0018727 | 0.00046935 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1150-7_0_3_load_101 | 118 | 0.0020878 | 0.00052326 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1150-7_0_3_load_102 | 120 | 0.002012 | 0.00050426 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1150-7_0_3_load_106 | 122 | 0.0053236 | 0.0013342 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1150-7_0_3_load_148 | 123 | 0.0031543 | 0.00079054 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1150-7_0_3_load_107 | 124 | 0.0025396 | 0.00063649 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1150-7_0_3_load_111 | 126 | 0.001436 | 0.0003599 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1150-7_0_3_load_112 | 127 | 0.0032569 | 0.00081625 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1150-7_0_3_load_137 | 128 | 0.0035608 | 0.00089242 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1150-7_0_3_load_114 | 129 | 0.0025004 | 0.00062667 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1150-7_0_3_load_115 | 130 | 0.0035206 | 0.00088234 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1150-7_0_3_load_116 | 131 | 0.0059461 | 0.0014902 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1150-7_0_3_load_117 | 132 | 0.0019009 | 0.00047641 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1150-7_0_3_load_138 | 133 | 0.00083702 | 0.00020978 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1150-7_0_3_load_139 | 134 | 0.00064351 | 0.00016128 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1150-7_0_3_load_120 | 135 | 0.00025274 | 6.3343e-05 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1150-7_0_3_load_121 | 136 | 0.0014148 | 0.00035457 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1150-7_0_3_load_122 | 137 | 0.00283 | 0.00070927 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1150-7_0_3_load_123 | 138 | 0.00037478 | 9.3928e-05 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1150-7_0_3_load_128 | 139 | 0.0012309 | 0.00030849 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1150-7_0_3_load_127 | 140 | 0.0013874 | 0.00034771 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1150-7_0_3_load_153 | 143 | 0.0026499 | 0.00066413 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1150-7_0_3_load_144 | 145 | 0.0018856 | 0.00047257 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1150-7_0_3_load_145 | 146 | 0.0022119 | 0.00055435 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1150-7_0_3_load_151 | 147 | 0.0014483 | 0.00036298 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 57 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1150-7_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.033557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
1 | LV_1150-7_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.03882 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
2 | LV_1150-7_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.13634 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
3 | LV_1150-7_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0070952 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1150-7_0_3_line_4 | NAYY 4x150 SE | 2 | 5 | 0.14684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1150-7_0_3_line_5 | NAYY 4x150 SE | 3 | 10 | 0.026943 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1150-7_0_3_line_6 | NAYY 4x150 SE | 5 | 14 | 0.0032461 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
7 | LV_1150-7_0_3_line_7 | NAYY 4x150 SE | 6 | 7 | 0.011513 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1150-7_0_3_line_8 | NAYY 4x150 SE | 7 | 44 | 0.022048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1150-7_0_3_line_9 | NAYY 4x150 SE | 8 | 9 | 0.0092376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1150-7_0_3_line_10 | NAYY 4x150 SE | 9 | 40 | 0.029081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1150-7_0_3_line_11 | NAYY 4x150 SE | 9 | 33 | 0.035844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1150-7_0_3_line_12 | NAYY 4x150 SE | 10 | 18 | 0.46639 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
13 | LV_1150-7_0_3_line_13 | NAYY 4x150 SE | 10 | 15 | 0.13087 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1150-7_0_3_line_14 | NAYY 4x150 SE | 11 | 12 | 0.018338 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
15 | LV_1150-7_0_3_line_15 | NAYY 4x150 SE | 11 | 13 | 0.45831 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1150-7_0_3_line_16 | NAYY 4x150 SE | 12 | 25 | 0.022854 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
17 | LV_1150-7_0_3_line_17 | NAYY 4x150 SE | 13 | 48 | 0.044851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1150-7_0_3_line_18 | NAYY 4x150 SE | 14 | 47 | 0.009459 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
19 | LV_1150-7_0_3_line_19 | NAYY 4x150 SE | 15 | 16 | 0.0022469 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1150-7_0_3_line_20 | NAYY 4x150 SE | 16 | 17 | 0.019455 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1150-7_0_3_line_21 | NAYY 4x150 SE | 17 | 19 | 0.018582 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1150-7_0_3_line_22 | NAYY 4x150 SE | 17 | 20 | 0.05908 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1150-7_0_3_line_23 | NAYY 4x150 SE | 18 | 23 | 0.043889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1150-7_0_3_line_24 | NAYY 4x150 SE | 18 | 21 | 0.010816 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1150-7_0_3_line_25 | NAYY 4x150 SE | 21 | 22 | 0.02376 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1150-7_0_3_line_26 | NAYY 4x150 SE | 24 | 25 | 0.028448 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
27 | LV_1150-7_0_3_line_27 | NAYY 4x150 SE | 24 | 26 | 0.1039 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
28 | LV_1150-7_0_3_line_28 | NAYY 4x150 SE | 25 | 27 | 0.024702 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1150-7_0_3_line_29 | NAYY 4x150 SE | 26 | 28 | 0.057705 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
30 | LV_1150-7_0_3_line_30 | NAYY 4x150 SE | 27 | 31 | 0.020921 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1150-7_0_3_line_31 | NAYY 4x150 SE | 28 | 32 | 0.030984 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
32 | LV_1150-7_0_3_line_32 | NAYY 4x150 SE | 29 | 30 | 0.0051003 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1150-7_0_3_line_33 | NAYY 4x150 SE | 30 | 52 | 0.015097 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1150-7_0_3_line_34 | NAYY 4x150 SE | 31 | 38 | 0.013947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1150-7_0_3_line_35 | NAYY 4x150 SE | 32 | 39 | 0.044396 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1150-7_0_3_line_36 | NAYY 4x150 SE | 34 | 35 | 0.021346 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1150-7_0_3_line_37 | NAYY 4x150 SE | 34 | 36 | 0.093099 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1150-7_0_3_line_38 | NAYY 4x150 SE | 34 | 37 | 0.22557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1150-7_0_3_line_39 | NAYY 4x150 SE | 36 | 59 | 0.068878 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1150-7_0_3_line_40 | NAYY 4x150 SE | 36 | 56 | 0.067174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1150-7_0_3_line_41 | NAYY 4x150 SE | 37 | 39 | 0.025732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1150-7_0_3_line_42 | NAYY 4x150 SE | 38 | 40 | 0.032974 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1150-7_0_3_line_43 | NAYY 4x150 SE | 41 | 42 | 0.014654 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
44 | LV_1150-7_0_3_line_44 | NAYY 4x150 SE | 41 | 43 | 0.028864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
45 | LV_1150-7_0_3_line_45 | NAYY 4x150 SE | 42 | 44 | 0.03681 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
46 | LV_1150-7_0_3_line_46 | NAYY 4x150 SE | 43 | 45 | 0.005348 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
47 | LV_1150-7_0_3_line_47 | NAYY 4x150 SE | 43 | 46 | 0.014453 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
48 | LV_1150-7_0_3_line_48 | NAYY 4x150 SE | 44 | 48 | 0.026304 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
49 | LV_1150-7_0_3_line_49 | NAYY 4x150 SE | 45 | 47 | 0.006527 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
50 | LV_1150-7_0_3_line_50 | NAYY 4x150 SE | 49 | 50 | 0.037616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
51 | LV_1150-7_0_3_line_51 | NAYY 4x150 SE | 49 | 51 | 0.18626 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
52 | LV_1150-7_0_3_line_52 | NAYY 4x150 SE | 50 | 52 | 0.0073547 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
53 | LV_1150-7_0_3_line_53 | NAYY 4x150 SE | 51 | 53 | 0.04616 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
54 | LV_1150-7_0_3_line_54 | NAYY 4x150 SE | 52 | 54 | 0.035084 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
55 | LV_1150-7_0_3_line_55 | NAYY 4x150 SE | 53 | 56 | 0.026976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
56 | LV_1150-7_0_3_line_56 | NAYY 4x150 SE | 54 | 55 | 0.0012559 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
57 | LV_1150-7_0_3_line_57 | NAYY 4x150 SE | 57 | 58 | 0.016956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
58 | LV_1150-7_0_3_line_58 | NAYY 4x150 SE | 58 | 61 | 0.027581 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
59 | LV_1150-7_0_3_line_59 | NAYY 4x150 SE | 59 | 60 | 0.043429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
60 | LV_1150-7_0_3_line_60 | NAYY 4x150 SE | 60 | 121 | 0.033024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
61 | LV_1150-7_0_3_line_61 | NAYY 4x150 SE | 61 | 62 | 0.018158 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
62 | LV_1150-7_0_3_line_62 | NAYY 4x150 SE | 62 | 63 | 0.019954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
63 | LV_1150-7_0_3_line_63 | NAYY 4x150 SE | 62 | 64 | 0.019142 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
64 | LV_1150-7_0_3_line_64 | NAYY 4x150 SE | 63 | 65 | 0.01629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
65 | LV_1150-7_0_3_line_65 | NAYY 4x150 SE | 63 | 66 | 0.0080479 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
66 | LV_1150-7_0_3_line_66 | NAYY 4x150 SE | 64 | 67 | 0.01133 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
67 | LV_1150-7_0_3_line_67 | NAYY 4x150 SE | 65 | 68 | 0.014252 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
68 | LV_1150-7_0_3_line_68 | NAYY 4x150 SE | 65 | 69 | 0.017104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
69 | LV_1150-7_0_3_line_69 | NAYY 4x150 SE | 66 | 70 | 0.052992 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
70 | LV_1150-7_0_3_line_70 | NAYY 4x150 SE | 67 | 71 | 0.016233 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
71 | LV_1150-7_0_3_line_71 | NAYY 4x150 SE | 68 | 75 | 0.058033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
72 | LV_1150-7_0_3_line_72 | NAYY 4x150 SE | 69 | 76 | 0.0084876 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
73 | LV_1150-7_0_3_line_73 | NAYY 4x150 SE | 70 | 72 | 0.0062781 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
74 | LV_1150-7_0_3_line_74 | NAYY 4x150 SE | 71 | 83 | 0.0014557 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
75 | LV_1150-7_0_3_line_75 | NAYY 4x150 SE | 72 | 73 | 0.0141 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
76 | LV_1150-7_0_3_line_76 | NAYY 4x150 SE | 73 | 74 | 0.017569 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
77 | LV_1150-7_0_3_line_77 | NAYY 4x150 SE | 74 | 114 | 0.020683 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
78 | LV_1150-7_0_3_line_78 | NAYY 4x150 SE | 76 | 131 | 0.015305 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
79 | LV_1150-7_0_3_line_79 | NAYY 4x150 SE | 77 | 78 | 0.011844 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
80 | LV_1150-7_0_3_line_80 | NAYY 4x150 SE | 77 | 79 | 0.027421 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
81 | LV_1150-7_0_3_line_81 | NAYY 4x150 SE | 78 | 80 | 0.0094205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
82 | LV_1150-7_0_3_line_82 | NAYY 4x150 SE | 79 | 81 | 0.013748 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
83 | LV_1150-7_0_3_line_83 | NAYY 4x150 SE | 79 | 82 | 0.019764 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
84 | LV_1150-7_0_3_line_84 | NAYY 4x150 SE | 79 | 83 | 0.019856 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
85 | LV_1150-7_0_3_line_85 | NAYY 4x150 SE | 80 | 84 | 0.0017638 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
86 | LV_1150-7_0_3_line_86 | NAYY 4x150 SE | 81 | 85 | 0.025871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
87 | LV_1150-7_0_3_line_87 | NAYY 4x150 SE | 84 | 86 | 0.0078094 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
88 | LV_1150-7_0_3_line_88 | NAYY 4x150 SE | 85 | 87 | 0.003502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
89 | LV_1150-7_0_3_line_89 | NAYY 4x150 SE | 86 | 100 | 0.0096976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
90 | LV_1150-7_0_3_line_90 | NAYY 4x150 SE | 87 | 124 | 0.0036536 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
91 | LV_1150-7_0_3_line_91 | NAYY 4x150 SE | 88 | 89 | 0.026214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
92 | LV_1150-7_0_3_line_92 | NAYY 4x150 SE | 88 | 90 | 0.019273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
93 | LV_1150-7_0_3_line_93 | NAYY 4x150 SE | 88 | 91 | 0.017712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
94 | LV_1150-7_0_3_line_94 | NAYY 4x150 SE | 89 | 101 | 0.024034 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
95 | LV_1150-7_0_3_line_95 | NAYY 4x150 SE | 90 | 102 | 0.03412 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
96 | LV_1150-7_0_3_line_96 | NAYY 4x150 SE | 91 | 96 | 0.015432 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
97 | LV_1150-7_0_3_line_97 | NAYY 4x150 SE | 91 | 95 | 0.045766 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
98 | LV_1150-7_0_3_line_98 | NAYY 4x150 SE | 92 | 93 | 0.028273 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
99 | LV_1150-7_0_3_line_99 | NAYY 4x150 SE | 92 | 94 | 0.024991 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
100 | LV_1150-7_0_3_line_100 | NAYY 4x150 SE | 93 | 95 | 0.03645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
101 | LV_1150-7_0_3_line_101 | NAYY 4x150 SE | 96 | 99 | 0.0075905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
102 | LV_1150-7_0_3_line_102 | NAYY 4x150 SE | 97 | 98 | 0.02413 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
103 | LV_1150-7_0_3_line_103 | NAYY 4x150 SE | 98 | 111 | 0.021093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
104 | LV_1150-7_0_3_line_104 | NAYY 4x150 SE | 99 | 100 | 0.0096486 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
105 | LV_1150-7_0_3_line_105 | NAYY 4x150 SE | 101 | 111 | 0.020092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
106 | LV_1150-7_0_3_line_106 | NAYY 4x150 SE | 102 | 112 | 0.025425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
107 | LV_1150-7_0_3_line_107 | NAYY 4x150 SE | 103 | 104 | 0.11566 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
108 | LV_1150-7_0_3_line_108 | NAYY 4x150 SE | 104 | 105 | 0.013419 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
109 | LV_1150-7_0_3_line_109 | NAYY 4x150 SE | 104 | 106 | 0.059691 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
110 | LV_1150-7_0_3_line_110 | NAYY 4x150 SE | 105 | 107 | 0.043545 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
111 | LV_1150-7_0_3_line_111 | NAYY 4x150 SE | 106 | 108 | 0.017883 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
112 | LV_1150-7_0_3_line_112 | NAYY 4x150 SE | 107 | 109 | 0.023137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
113 | LV_1150-7_0_3_line_113 | NAYY 4x150 SE | 108 | 110 | 0.0028107 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
114 | LV_1150-7_0_3_line_114 | NAYY 4x150 SE | 109 | 140 | 0.028874 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
115 | LV_1150-7_0_3_line_115 | NAYY 4x150 SE | 110 | 145 | 0.020407 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
116 | LV_1150-7_0_3_line_116 | NAYY 4x150 SE | 112 | 113 | 0.023689 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
117 | LV_1150-7_0_3_line_117 | NAYY 4x150 SE | 114 | 115 | 0.006239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
118 | LV_1150-7_0_3_line_118 | NAYY 4x150 SE | 115 | 116 | 0.020622 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
119 | LV_1150-7_0_3_line_119 | NAYY 4x150 SE | 115 | 117 | 0.032762 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
120 | LV_1150-7_0_3_line_120 | NAYY 4x150 SE | 116 | 118 | 0.0032192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
121 | LV_1150-7_0_3_line_121 | NAYY 4x150 SE | 117 | 119 | 0.0082155 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
122 | LV_1150-7_0_3_line_122 | NAYY 4x150 SE | 118 | 120 | 0.027808 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
123 | LV_1150-7_0_3_line_123 | NAYY 4x150 SE | 119 | 139 | 0.0097428 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
124 | LV_1150-7_0_3_line_124 | NAYY 4x150 SE | 119 | 137 | 0.012997 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
125 | LV_1150-7_0_3_line_125 | NAYY 4x150 SE | 120 | 121 | 0.013589 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
126 | LV_1150-7_0_3_line_126 | NAYY 4x150 SE | 121 | 122 | 0.020363 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
127 | LV_1150-7_0_3_line_127 | NAYY 4x150 SE | 122 | 123 | 0.028925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
128 | LV_1150-7_0_3_line_128 | NAYY 4x150 SE | 124 | 125 | 0.01813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
129 | LV_1150-7_0_3_line_129 | NAYY 4x150 SE | 125 | 126 | 0.01583 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
130 | LV_1150-7_0_3_line_130 | NAYY 4x150 SE | 125 | 127 | 0.016791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
131 | LV_1150-7_0_3_line_131 | NAYY 4x150 SE | 126 | 128 | 0.0037079 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
132 | LV_1150-7_0_3_line_132 | NAYY 4x150 SE | 129 | 130 | 0.015586 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
133 | LV_1150-7_0_3_line_133 | NAYY 4x150 SE | 129 | 131 | 0.0081731 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
134 | LV_1150-7_0_3_line_134 | NAYY 4x150 SE | 130 | 132 | 0.019366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
135 | LV_1150-7_0_3_line_135 | NAYY 4x150 SE | 132 | 133 | 0.01708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
136 | LV_1150-7_0_3_line_136 | NAYY 4x150 SE | 133 | 134 | 0.00082954 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
137 | LV_1150-7_0_3_line_137 | NAYY 4x150 SE | 134 | 141 | 0.051708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
138 | LV_1150-7_0_3_line_138 | NAYY 4x150 SE | 135 | 136 | 0.0073737 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
139 | LV_1150-7_0_3_line_139 | NAYY 4x150 SE | 135 | 137 | 0.025684 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
140 | LV_1150-7_0_3_line_140 | NAYY 4x150 SE | 136 | 138 | 0.023193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
141 | LV_1150-7_0_3_line_141 | NAYY 4x150 SE | 139 | 140 | 0.019665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
142 | LV_1150-7_0_3_line_142 | NAYY 4x150 SE | 141 | 142 | 0.083081 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
143 | LV_1150-7_0_3_line_143 | NAYY 4x150 SE | 142 | 143 | 0.02366 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
144 | LV_1150-7_0_3_line_144 | NAYY 4x150 SE | 142 | 144 | 0.030871 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
145 | LV_1150-7_0_3_line_145 | NAYY 4x150 SE | 144 | 147 | 0.039311 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
146 | LV_1150-7_0_3_line_146 | NAYY 4x150 SE | 145 | 146 | 0.00023468 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1150-7_0_3_trafo_62 | 0.25 MVA 20/0.4 kV | 148 | 57 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2637569.868 | 1222231.4493 | 2637572.7696 | 1222232.4325 | 2637602.8068 | 1222237.6874
1 | 2637569.868 | 1222231.4493 | 2637558.7605 | 1222227.6858 | 2637554.5111 | 1222224.4127 | 2637552.5067 | 1222218.7189 | 2637537.0459 | 1222221.4059
2 | 2637635.6637 | 1222370.0114 | 2637602.8068 | 1222237.6874
3 | 2637537.0459 | 1222221.4059 | 2637530.0555 | 1222222.6209
4 | 2637522.0685 | 1222075.3337 | 2637537.0459 | 1222221.4059
5 | 2637635.6637 | 1222370.0114 | 2637642.2327 | 1222377.0682 | 2637656.6337 | 1222386.6576
6 | 2637523.3936 | 1222072.3704 | 2637522.0685 | 1222075.3337
7 | 2637605.2588 | 1222087.4995 | 2637605.6654 | 1222086.7752 | 2637609.7552 | 1222076.9062
8 | 2637609.5224 | 1222054.9138 | 2637610.4234 | 1222067.1824 | 2637609.7552 | 1222076.9062 | 2637609.7552 | 1222076.9062
9 | 2637436.3024 | 1221577.9059 | 2637427.6451 | 1221581.1281
10 | 2637436.3024 | 1221577.9059 | 2637463.8039 | 1221568.4512
11 | 2637436.3024 | 1221577.9059 | 2637445.9707 | 1221543.3905
12 | 2637656.6337 | 1222386.6576 | 2637966.5786 | 1222735.1616
13 | 2637737.4553 | 1222283.7305 | 2637656.6337 | 1222386.6576
14 | 2637577.4644 | 1221558.1063 | 2637589.8297 | 1221558.7938 | 2637595.7097 | 1221559.7237
15 | 2637595.7097 | 1221559.7237 | 2637665.9769 | 1222012.6135
16 | 2637554.6457 | 1221556.8376 | 2637577.4644 | 1221558.1063
17 | 2637632.7566 | 1222042.5753 | 2637656.096 | 1222019.609 | 2637665.9769 | 1222012.6135
18 | 2637523.3936 | 1222072.3704 | 2637527.251 | 1222063.7337
19 | 2637739.5718 | 1222284.4848 | 2637737.4553 | 1222283.7305
20 | 2637758.3349 | 1222289.5836 | 2637742.5544 | 1222285.5479 | 2637739.5718 | 1222284.4848
21 | 2637758.3349 | 1222289.5836 | 2637774.2232 | 1222299.22
22 | 2637758.3349 | 1222289.5836 | 2637765.5027 | 1222282.3246 | 2637771.9116 | 1222267.9678 | 2637776.4451 | 1222271.8766 | 2637787.7627 | 1222280.0199 | 2637798.9352 | 1222287.1002
23 | 2637966.5786 | 1222735.1616 | 2637975.4314 | 1222731.2268 | 2637994.3501 | 1222730.5358 | 2638003.9428 | 1222725.9276 | 2638007.3998 | 1222722.851
24 | 2637966.5786 | 1222735.1616 | 2637975.5766 | 1222741.1632
25 | 2637995.3431 | 1222754.3472 | 2637975.5766 | 1222741.1632
26 | 2637554.6457 | 1221556.8376 | 2637555.1404 | 1221540.9423 | 2637551.9438 | 1221531.8057 | 2637550.1088 | 1221529.6044
27 | 2637479.3951 | 1221453.6693 | 2637484.4531 | 1221457.5367 | 2637531.5489 | 1221507.3404 | 2637550.1088 | 1221529.6044
28 | 2637554.6457 | 1221556.8376 | 2637534.2762 | 1221560.8784 | 2637530.3545 | 1221561.2067
29 | 2637479.3951 | 1221453.6693 | 2637474.5663 | 1221444.7225 | 2637464.6605 | 1221434.9211 | 2637455.5397 | 1221429.3605 | 2637438.2682 | 1221425.6053 | 2637433.0337 | 1221425.2587
30 | 2637509.4695 | 1221561.1951 | 2637523.5296 | 1221561.7779 | 2637530.3545 | 1221561.2067
31 | 2637402.6152 | 1221428.4182 | 2637407.9446 | 1221426.2487 | 2637421.3897 | 1221424.4876 | 2637433.0337 | 1221425.2587
32 | 2637583.1229 | 1221156.1007 | 2637585.1275 | 1221151.4108
33 | 2637591.0611 | 1221137.5286 | 2637585.1275 | 1221151.4108
34 | 2637509.4695 | 1221561.1951 | 2637495.5349 | 1221560.6174
35 | 2637402.6152 | 1221428.4182 | 2637387.3427 | 1221434.6356 | 2637376.1303 | 1221438.4231 | 2637365.1482 | 1221438.1318 | 2637360.357 | 1221436.4267
36 | 2637265.3074 | 1221208.8483 | 2637281.5897 | 1221208.3498 | 2637286.6686 | 1221207.7145
37 | 2637231.8474 | 1221133.3833 | 2637240.1286 | 1221149.5891 | 2637254.1768 | 1221174.0025 | 2637286.6686 | 1221207.7145
38 | 2637286.6686 | 1221207.7145 | 2637336.1148 | 1221427.7994
39 | 2637231.0931 | 1221064.5093 | 2637231.8474 | 1221133.3833
40 | 2637231.8474 | 1221133.3833 | 2637243.7349 | 1221136.9708 | 2637260.7569 | 1221148.0282 | 2637275.3654 | 1221154.4122 | 2637291.1824 | 1221164.039
41 | 2637336.1148 | 1221427.7994 | 2637360.357 | 1221436.4267
42 | 2637463.8039 | 1221568.4512 | 2637482.225 | 1221562.1183 | 2637490.3294 | 1221560.4016 | 2637495.5349 | 1221560.6174
43 | 2637559.8119 | 1222062.1944 | 2637574.4044 | 1222063.5393
44 | 2637532.4349 | 1222053.0491 | 2637559.8038 | 1222062.1936 | 2637559.8119 | 1222062.1944
45 | 2637609.5224 | 1222054.9138 | 2637596.021 | 1222060.999 | 2637586.8499 | 1222063.5871 | 2637578.7092 | 1222063.936 | 2637574.4044 | 1222063.5393
46 | 2637532.4349 | 1222053.0491 | 2637530.0459 | 1222057.8369
47 | 2637532.4349 | 1222053.0491 | 2637541.5518 | 1222041.8344
48 | 2637609.5224 | 1222054.9138 | 2637621.7308 | 1222049.3987 | 2637632.7566 | 1222042.5753
49 | 2637530.0459 | 1222057.8369 | 2637528.4788 | 1222060.9845 | 2637527.251 | 1222063.7337
50 | 2637547.0967 | 1221129.3869 | 2637559.7554 | 1221133.6845 | 2637567.512 | 1221135.5012 | 2637583.7335 | 1221136.8977
51 | 2637363.0512 | 1221158.0076 | 2637547.0967 | 1221129.3869
52 | 2637591.0611 | 1221137.5286 | 2637583.7335 | 1221136.8977
53 | 2637363.0512 | 1221158.0076 | 2637342.255 | 1221164.5701 | 2637330.4391 | 1221166.5195 | 2637318.1185 | 1221165.3372
54 | 2637591.0611 | 1221137.5286 | 2637625.0728 | 1221139.3108 | 2637626.0834 | 1221139.1369
55 | 2637291.1824 | 1221164.039 | 2637312.3424 | 1221164.783 | 2637318.1185 | 1221165.3372
56 | 2637627.3211 | 1221138.924 | 2637626.0834 | 1221139.1369
57 | 2637314.8549 | 1221021.5913 | 2637310.3691 | 1221023.1864 | 2637306.5016 | 1221022.9621 | 2637303.8821 | 1221019.6993 | 2637302.078 | 1221015.9762
58 | 2637290.0511 | 1220991.1555 | 2637302.078 | 1221015.9762
59 | 2637231.0931 | 1221064.5093 | 2637214.0441 | 1221068.8561 | 2637207.5091 | 1221073.0511 | 2637189.9088 | 1221077.1381
60 | 2637157.6001 | 1221081.6672 | 2637165.7331 | 1221082.7519 | 2637189.9088 | 1221077.1381
61 | 2637282.1329 | 1220974.8144 | 2637290.0511 | 1220991.1555
62 | 2637263.8601 | 1220982.9495 | 2637282.1329 | 1220974.8144
63 | 2637282.1329 | 1220974.8144 | 2637299.3651 | 1220966.4807
64 | 2637263.8601 | 1220982.9495 | 2637258.73 | 1220967.486
65 | 2637263.8601 | 1220982.9495 | 2637256.2836 | 1220985.6635
66 | 2637299.3651 | 1220966.4807 | 2637309.565 | 1220961.5479
67 | 2637258.73 | 1220967.486 | 2637246.2056 | 1220969.8536 | 2637244.7018 | 1220969.7682
68 | 2637258.73 | 1220967.486 | 2637258.1126 | 1220965.5254 | 2637253.9191 | 1220951.0735
69 | 2637256.2836 | 1220985.6635 | 2637235.8881 | 1220992.9696 | 2637223.1265 | 1220996.9033 | 2637205.6546 | 1221001.1194
70 | 2637324.1786 | 1220954.4806 | 2637309.565 | 1220961.5479
71 | 2637244.7018 | 1220969.7682 | 2637238.0685 | 1220969.3914 | 2637230.5109 | 1220967.2651 | 2637226.2966 | 1220964.2482 | 2637208.062 | 1220945.6233 | 2637199.7593 | 1220938.8786 | 2637198.4142 | 1220938.025
72 | 2637251.5539 | 1220942.922 | 2637253.9191 | 1220951.0735
73 | 2637199.5516 | 1221002.592 | 2637205.6546 | 1221001.1194
74 | 2637324.1786 | 1220954.4806 | 2637325.489 | 1220953.8468
75 | 2637199.5516 | 1221002.592 | 2637185.8445 | 1221005.8996
76 | 2637168.8171 | 1221010.2092 | 2637171.9722 | 1221009.2471 | 2637185.8445 | 1221005.8996
77 | 2637149.0337 | 1221016.2416 | 2637168.8171 | 1221010.2092
78 | 2637251.5539 | 1220942.922 | 2637247.2889 | 1220928.2236
79 | 2637366.4785 | 1220967.2212 | 2637361.221 | 1220969.573 | 2637358.0315 | 1220970.0978 | 2637355.2357 | 1220969.5355
80 | 2637343.3642 | 1220945.2022 | 2637345.878 | 1220952.022 | 2637353.43 | 1220968.3568 | 2637355.2357 | 1220969.5355
81 | 2637375.0779 | 1220963.3746 | 2637366.4785 | 1220967.2212
82 | 2637343.3642 | 1220945.2022 | 2637338.8416 | 1220932.2189
83 | 2637343.3642 | 1220945.2022 | 2637361.345 | 1220936.9972
84 | 2637343.3642 | 1220945.2022 | 2637325.489 | 1220953.8468
85 | 2637375.0779 | 1220963.3746 | 2637376.688 | 1220962.6544
86 | 2637338.8416 | 1220932.2189 | 2637330.3313 | 1220907.7881
87 | 2637383.8167 | 1220959.4656 | 2637376.688 | 1220962.6544
88 | 2637329.1794 | 1220904.481 | 2637330.3313 | 1220907.7881
89 | 2637383.8167 | 1220959.4656 | 2637388.2808 | 1220957.4687 | 2637392.6181 | 1220955.3955
90 | 2637327.9775 | 1220901.0307 | 2637329.1794 | 1220904.481
91 | 2637400.3479 | 1220919.1995 | 2637422.5941 | 1220905.3321
92 | 2637400.3479 | 1220919.1995 | 2637396.9289 | 1220911.5624 | 2637393.0049 | 1220901.3869
93 | 2637411.3974 | 1220933.0659 | 2637400.3479 | 1220919.1995
94 | 2637442.5621 | 1220891.9646 | 2637428.0169 | 1220901.9517 | 2637422.5941 | 1220905.3321
95 | 2637380.8259 | 1220869.5155 | 2637383.6789 | 1220877.2033 | 2637393.0049 | 1220901.3869
96 | 2637411.3974 | 1220933.0659 | 2637411.8543 | 1220937.6159 | 2637411.2447 | 1220941.6701 | 2637409.452 | 1220945.6723 | 2637407.7146 | 1220947.2898
97 | 2637411.3974 | 1220933.0659 | 2637415.5033 | 1220935.1929 | 2637426.4296 | 1220945.7233 | 2637429.7478 | 1220947.6564 | 2637433.818 | 1220948.2156 | 2637437.0612 | 1220947.6023 | 2637440.4131 | 1220945.3776 | 2637447.8371 | 1220937.6787
98 | 2637485.6111 | 1220885.5757 | 2637479.8476 | 1220895.6735 | 2637471.2059 | 1220909.9007
99 | 2637485.6111 | 1220885.5757 | 2637497.9994 | 1220863.8707
100 | 2637447.8371 | 1220937.6787 | 2637454.2876 | 1220930.9895 | 2637463.4731 | 1220921.5527 | 2637469.5144 | 1220912.6854 | 2637471.2059 | 1220909.9007
101 | 2637401.3232 | 1220951.2344 | 2637405.7511 | 1220949.1178 | 2637407.7146 | 1220947.2898
102 | 2637472.8064 | 1220864.1416 | 2637489.3861 | 1220846.6099
103 | 2637472.8064 | 1220864.1416 | 2637460.9101 | 1220876.7211 | 2637458.0413 | 1220879.1815
104 | 2637401.3232 | 1220951.2344 | 2637392.6181 | 1220955.3955
105 | 2637442.5621 | 1220891.9646 | 2637445.4418 | 1220889.9873 | 2637458.0413 | 1220879.1815
106 | 2637380.8259 | 1220869.5155 | 2637371.9802 | 1220845.6791
107 | 2636983.7289 | 1221065.7768 | 2636991.7285 | 1221088.362 | 2636997.3776 | 1221096.0906 | 2637004.268 | 1221100.6138 | 2637036.9336 | 1221115.1919 | 2637057.057 | 1221119.1971 | 2637074.1143 | 1221123.5335
108 | 2636980.8365 | 1221052.6733 | 2636983.7289 | 1221065.7768
109 | 2636983.7289 | 1221065.7768 | 2636988.3993 | 1221067.429 | 2637007.3105 | 1221069.9812 | 2637019.1 | 1221071.0661 | 2637042.9094 | 1221071.5825
110 | 2636980.8365 | 1221052.6733 | 2637023.2589 | 1221042.8488
111 | 2637042.9094 | 1221071.5825 | 2637060.7884 | 1221071.9702
112 | 2637045.7993 | 1221037.6288 | 2637023.2589 | 1221042.8488
113 | 2637060.7884 | 1221071.9702 | 2637063.5984 | 1221072.0311
114 | 2637073.9291 | 1221031.1143 | 2637045.7993 | 1221037.6288
115 | 2637084.0006 | 1221072.4736 | 2637063.5984 | 1221072.0311
116 | 2637363.7384 | 1220823.4701 | 2637371.9802 | 1220845.6791
117 | 2637143.0521 | 1221018.0721 | 2637149.0337 | 1221016.2416
118 | 2637143.0521 | 1221018.0721 | 2637147.6508 | 1221038.1749
119 | 2637143.0521 | 1221018.0721 | 2637110.6928 | 1221023.1949
120 | 2637147.6508 | 1221038.1749 | 2637148.3687 | 1221041.313
121 | 2637102.5784 | 1221024.4795 | 2637110.6928 | 1221023.1949
122 | 2637148.3687 | 1221041.313 | 2637154.5698 | 1221068.4205
123 | 2637102.5784 | 1221024.4795 | 2637093.0868 | 1221026.6776
124 | 2637102.5784 | 1221024.4795 | 2637099.4217 | 1221011.8713
125 | 2637157.6001 | 1221081.6672 | 2637154.5698 | 1221068.4205
126 | 2637157.6001 | 1221081.6672 | 2637137.8159 | 1221086.4862
127 | 2637109.7129 | 1221093.3315 | 2637137.8159 | 1221086.4862
128 | 2637322.0136 | 1220883.9099 | 2637327.9775 | 1220901.0307
129 | 2637322.0136 | 1220883.9099 | 2637306.1949 | 1220884.5044
130 | 2637333.8924 | 1220872.0105 | 2637322.0136 | 1220883.9099
131 | 2637302.4896 | 1220884.6437 | 2637306.1949 | 1220884.5044
132 | 2637245.0113 | 1220920.3743 | 2637240.6679 | 1220905.4056
133 | 2637245.0113 | 1220920.3743 | 2637247.2889 | 1220928.2236
134 | 2637240.6679 | 1220905.4056 | 2637238.8638 | 1220899.188 | 2637234.9903 | 1220886.8917
135 | 2637229.8584 | 1220870.6009 | 2637229.863 | 1220870.6148 | 2637234.9903 | 1220886.8917
136 | 2637229.8584 | 1220870.6009 | 2637229.6013 | 1220869.8122
137 | 2637213.5762 | 1220820.6501 | 2637229.6013 | 1220869.8122
138 | 2637088.0937 | 1220995.2503 | 2637080.9051 | 1220996.8919
139 | 2637088.0937 | 1220995.2503 | 2637094.8728 | 1220993.7022 | 2637099.4217 | 1221011.8713
140 | 2637080.9051 | 1220996.8919 | 2637062.8823 | 1221001.0076 | 2637058.2164 | 1221000.3918
141 | 2637093.0868 | 1221026.6776 | 2637073.9291 | 1221031.1143
142 | 2637213.5762 | 1220820.6501 | 2637227.7138 | 1220821.1831 | 2637237.3613 | 1220821.5547 | 2637252.4288 | 1220818.9695 | 2637293.8891 | 1220804.2644
143 | 2637301.6618 | 1220826.6152 | 2637293.8891 | 1220804.2644
144 | 2637323.0627 | 1220793.9297 | 2637293.8891 | 1220804.2644
145 | 2637336.5931 | 1220830.8474 | 2637323.0627 | 1220793.9297
146 | 2637084.2352 | 1221072.4787 | 2637084.0006 | 1221072.4736

## bus_geodata
| x | y | coords
0 | 2637569.868 | 1222231.4493
1 | 2637602.8068 | 1222237.6874
2 | 2637537.0459 | 1222221.4059
3 | 2637635.6637 | 1222370.0114
4 | 2637530.0555 | 1222222.6209
5 | 2637522.0685 | 1222075.3337
6 | 2637605.2588 | 1222087.4995
7 | 2637609.7552 | 1222076.9062
8 | 2637427.6451 | 1221581.1281
9 | 2637436.3024 | 1221577.9059
10 | 2637656.6337 | 1222386.6576
11 | 2637595.7097 | 1221559.7237
12 | 2637577.4644 | 1221558.1063
13 | 2637665.9769 | 1222012.6135
14 | 2637523.3936 | 1222072.3704
15 | 2637737.4553 | 1222283.7305
16 | 2637739.5718 | 1222284.4848
17 | 2637758.3349 | 1222289.5836
18 | 2637966.5786 | 1222735.1616
19 | 2637774.2232 | 1222299.22
20 | 2637798.9352 | 1222287.1002
21 | 2637975.5766 | 1222741.1632
22 | 2637995.3431 | 1222754.3472
23 | 2638007.3998 | 1222722.851
24 | 2637550.1088 | 1221529.6044
25 | 2637554.6457 | 1221556.8376
26 | 2637479.3951 | 1221453.6693
27 | 2637530.3545 | 1221561.2067
28 | 2637433.0337 | 1221425.2587
29 | 2637583.1229 | 1221156.1007
30 | 2637585.1275 | 1221151.4108
31 | 2637509.4695 | 1221561.1951
32 | 2637402.6152 | 1221428.4182
33 | 2637445.9707 | 1221543.3905
34 | 2637286.6686 | 1221207.7145
35 | 2637265.3074 | 1221208.8483
36 | 2637231.8474 | 1221133.3833
37 | 2637336.1148 | 1221427.7994
38 | 2637495.5349 | 1221560.6174
39 | 2637360.357 | 1221436.4267
40 | 2637463.8039 | 1221568.4512
41 | 2637559.8119 | 1222062.1944
42 | 2637574.4044 | 1222063.5393
43 | 2637532.4349 | 1222053.0491
44 | 2637609.5224 | 1222054.9138
45 | 2637530.0459 | 1222057.8369
46 | 2637541.5518 | 1222041.8344
47 | 2637527.251 | 1222063.7337
48 | 2637632.7566 | 1222042.5753
49 | 2637547.0967 | 1221129.3869
50 | 2637583.7335 | 1221136.8977
51 | 2637363.0512 | 1221158.0076
52 | 2637591.0611 | 1221137.5286
53 | 2637318.1185 | 1221165.3372
54 | 2637626.0834 | 1221139.1369
55 | 2637627.3211 | 1221138.924
56 | 2637291.1824 | 1221164.039
57 | 2637314.8549 | 1221021.5913
58 | 2637302.078 | 1221015.9762
59 | 2637231.0931 | 1221064.5093
60 | 2637189.9088 | 1221077.1381
61 | 2637290.0511 | 1220991.1555
62 | 2637282.1329 | 1220974.8144
63 | 2637263.8601 | 1220982.9495
64 | 2637299.3651 | 1220966.4807
65 | 2637258.73 | 1220967.486
66 | 2637256.2836 | 1220985.6635
67 | 2637309.565 | 1220961.5479
68 | 2637244.7018 | 1220969.7682
69 | 2637253.9191 | 1220951.0735
70 | 2637205.6546 | 1221001.1194
71 | 2637324.1786 | 1220954.4806
72 | 2637199.5516 | 1221002.592
73 | 2637185.8445 | 1221005.8996
74 | 2637168.8171 | 1221010.2092
75 | 2637198.4142 | 1220938.025
76 | 2637251.5539 | 1220942.922
77 | 2637355.2357 | 1220969.5355
78 | 2637366.4785 | 1220967.2212
79 | 2637343.3642 | 1220945.2022
80 | 2637375.0779 | 1220963.3746
81 | 2637338.8416 | 1220932.2189
82 | 2637361.345 | 1220936.9972
83 | 2637325.489 | 1220953.8468
84 | 2637376.688 | 1220962.6544
85 | 2637330.3313 | 1220907.7881
86 | 2637383.8167 | 1220959.4656
87 | 2637329.1794 | 1220904.481
88 | 2637400.3479 | 1220919.1995
89 | 2637422.5941 | 1220905.3321
90 | 2637393.0049 | 1220901.3869
91 | 2637411.3974 | 1220933.0659
92 | 2637485.6111 | 1220885.5757
93 | 2637471.2059 | 1220909.9007
94 | 2637497.9994 | 1220863.8707
95 | 2637447.8371 | 1220937.6787
96 | 2637407.7146 | 1220947.2898
97 | 2637489.3861 | 1220846.6099
98 | 2637472.8064 | 1220864.1416
99 | 2637401.3232 | 1220951.2343
100 | 2637392.6181 | 1220955.3955
101 | 2637442.5621 | 1220891.9646
102 | 2637380.8259 | 1220869.5155
103 | 2637074.1143 | 1221123.5335
104 | 2636983.7289 | 1221065.7768
105 | 2636980.8365 | 1221052.6733
106 | 2637042.9094 | 1221071.5825
107 | 2637023.2589 | 1221042.8488
108 | 2637060.7884 | 1221071.9702
109 | 2637045.7993 | 1221037.6288
110 | 2637063.5984 | 1221072.0311
111 | 2637458.0413 | 1220879.1815
112 | 2637371.9802 | 1220845.6791
113 | 2637363.7384 | 1220823.4701
114 | 2637149.0337 | 1221016.2416
115 | 2637143.0521 | 1221018.0721
116 | 2637147.6508 | 1221038.1749
117 | 2637110.6928 | 1221023.1949
118 | 2637148.3687 | 1221041.313
119 | 2637102.5784 | 1221024.4795
120 | 2637154.5698 | 1221068.4205
121 | 2637157.6001 | 1221081.6672
122 | 2637137.8159 | 1221086.4862
123 | 2637109.7129 | 1221093.3315
124 | 2637327.9775 | 1220901.0307
125 | 2637322.0136 | 1220883.9099
126 | 2637306.1949 | 1220884.5044
127 | 2637333.8924 | 1220872.0105
128 | 2637302.4896 | 1220884.6437
129 | 2637245.0113 | 1220920.3743
130 | 2637240.6679 | 1220905.4056
131 | 2637247.2889 | 1220928.2236
132 | 2637234.9903 | 1220886.8917
133 | 2637229.8584 | 1220870.6009
134 | 2637229.6013 | 1220869.8122
135 | 2637088.0937 | 1220995.2503
136 | 2637080.9051 | 1220996.8919
137 | 2637099.4217 | 1221011.8713
138 | 2637058.2164 | 1221000.3918
139 | 2637093.0868 | 1221026.6776
140 | 2637073.9291 | 1221031.1143
141 | 2637213.5762 | 1220820.6501
142 | 2637293.8891 | 1220804.2644
143 | 2637301.6618 | 1220826.6152
144 | 2637323.0627 | 1220793.9297
145 | 2637084.0006 | 1221072.4736
146 | 2637084.2352 | 1221072.4787
147 | 2637336.5931 | 1220830.8474
148 | 2637282.1329 | 1220974.8144

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97111 | -0.20681 | 0.0011285 | 0.00028284
1 | 0.97104 | -0.20735 | 0.000421 | 0.00010551
2 | 0.97121 | -0.20603 | 0.00020259 | 5.0773e-05
3 | 0.97077 | -0.20933 | 0 | 0
4 | 0.97121 | -0.20604 | 0.00017457 | 4.3751e-05
5 | 0.97164 | -0.20287 | 0.00013447 | 3.3701e-05
6 | 0.97198 | -0.20029 | 0.00013955 | 3.4974e-05
7 | 0.97198 | -0.20027 | 0.00061088 | 0.0001531
8 | 0.97447 | -0.1817 | 0.00048456 | 0.00012144
9 | 0.97448 | -0.18165 | 0 | 0
10 | 0.97072 | -0.20972 | 0.00019149 | 4.7992e-05
11 | 0.97458 | -0.18095 | 0.0011386 | 0.00028536
12 | 0.97468 | -0.1802 | 0.00022586 | 5.6605e-05
13 | 0.97231 | -0.19782 | 0.0013426 | 0.0003365
14 | 0.97165 | -0.2028 | 0 | 0
15 | 0.97044 | -0.21177 | 0.0019102 | 0.00047875
16 | 0.97043 | -0.21179 | 0.00015873 | 3.9782e-05
17 | 0.97041 | -0.21197 | 0 | 0
18 | 0.97043 | -0.21193 | 0 | 0
19 | 0.9704 | -0.21206 | 0.00044489 | 0.0001115
20 | 0.97037 | -0.21224 | 0.00041821 | 0.00010481
21 | 0.97042 | -0.212 | 0.00043547 | 0.00010914
22 | 0.97042 | -0.21204 | 0.00014875 | 3.7279e-05
23 | 0.97041 | -0.21205 | 0.00025983 | 6.512e-05
24 | 0.97501 | -0.17777 | 9.2745e-05 | 2.3244e-05
25 | 0.97481 | -0.17925 | 0 | 0
26 | 0.97574 | -0.17235 | 0 | 0
27 | 0.97471 | -0.18 | 0.00067596 | 0.00016941
28 | 0.97615 | -0.16933 | 0.0020397 | 0.00051121
29 | 0.97253 | -0.19456 | 0.0025427 | 0.00063727
30 | 0.97255 | -0.19442 | 0.0055437 | 0.0013894
31 | 0.97464 | -0.18048 | 0.00059641 | 0.00014947
32 | 0.9764 | -0.1675 | 0.0019569 | 0.00049046
33 | 0.97444 | -0.18195 | 0.0007906 | 0.00019814
34 | 0.97944 | -0.14527 | 0 | 0
35 | 0.97935 | -0.14586 | 0.0026295 | 0.00065901
36 | 0.98054 | -0.13723 | 0 | 0
37 | 0.97705 | -0.16272 | 0.0017835 | 0.000447
38 | 0.97461 | -0.18072 | 6.0176e-05 | 1.5081e-05
39 | 0.9768 | -0.16456 | 0.0014549 | 0.00036463
40 | 0.97453 | -0.18126 | 0.00026677 | 6.6859e-05
41 | 0.97181 | -0.20158 | 0.00078764 | 0.0001974
42 | 0.97186 | -0.20117 | 0.00032312 | 8.098e-05
43 | 0.97171 | -0.20231 | 0 | 0
44 | 0.97201 | -0.2001 | 0 | 0
45 | 0.97169 | -0.20244 | 0 | 0
46 | 0.9717 | -0.20241 | 0.00065411 | 0.00016394
47 | 0.97167 | -0.20259 | 0.00024882 | 6.236e-05
48 | 0.97212 | -0.19926 | 0 | 0
49 | 0.97352 | -0.18744 | 0.0015795 | 0.00039586
50 | 0.97284 | -0.19233 | 0.0019613 | 0.00049154
51 | 0.97731 | -0.16023 | 0 | 0
52 | 0.97273 | -0.19314 | 0 | 0
53 | 0.97825 | -0.15351 | 0.0018287 | 0.00045831
54 | 0.97261 | -0.19398 | 0.0015838 | 0.00039694
55 | 0.97261 | -0.19399 | 0.0006999 | 0.00017541
56 | 0.97888 | -0.14907 | 0.001181 | 0.00029598
57 | 1 | 0 | -0.22729 | -0.057163
58 | 0.99817 | -0.012632 | 0.0023473 | 0.0005883
59 | 0.98193 | -0.12725 | 0.0070177 | 0.0017588
60 | 0.98295 | -0.11993 | 0.0068934 | 0.0017276
61 | 0.99524 | -0.033059 | 0.0018395 | 0.00046102
62 | 0.99332 | -0.046461 | 0.0032247 | 0.00080818
63 | 0.99203 | -0.055529 | 0 | 0
64 | 0.99105 | -0.062273 | 0.0016445 | 0.00041215
65 | 0.99134 | -0.06037 | 0 | 0
66 | 0.99162 | -0.058395 | 0.0021071 | 0.00052808
67 | 0.98974 | -0.071476 | 0.002292 | 0.00057442
68 | 0.99125 | -0.060986 | 0.0026503 | 0.00066423
69 | 0.99072 | -0.064721 | 0.0030982 | 0.00077647
70 | 0.98899 | -0.076946 | 0.0027643 | 0.0006928
71 | 0.98791 | -0.084324 | 0.0039723 | 0.00099555
72 | 0.98868 | -0.079091 | 0.0011115 | 0.00027856
73 | 0.98801 | -0.08386 | 0.0017166 | 0.00043021
74 | 0.98718 | -0.089708 | 0.0018394 | 0.000461
75 | 0.99112 | -0.061928 | 0.0015951 | 0.00039976
76 | 0.99046 | -0.066615 | 0.0024579 | 0.00061602
77 | 0.9836 | -0.11476 | 0.0020382 | 0.00051082
78 | 0.98274 | -0.12089 | 0.0013723 | 0.00034393
79 | 0.98568 | -0.10003 | 0 | 0
80 | 0.98207 | -0.12564 | 0.0013693 | 0.00034319
81 | 0.98535 | -0.10243 | 0.0017641 | 0.00044212
82 | 0.98561 | -0.10057 | 0.002649 | 0.0006639
83 | 0.98776 | -0.085419 | 0.0017652 | 0.00044241
84 | 0.98195 | -0.1265 | 0.0030639 | 0.00076789
85 | 0.98478 | -0.10648 | 0.0019535 | 0.00048958
86 | 0.98144 | -0.13009 | 0.001487 | 0.00037268
87 | 0.98471 | -0.10696 | 0.0024603 | 0.00061661
88 | 0.97829 | -0.15259 | 0 | 0
89 | 0.97769 | -0.15687 | 0.0049985 | 0.0012527
90 | 0.978 | -0.15468 | 0.0050007 | 0.0012533
91 | 0.97896 | -0.14778 | 0 | 0
92 | 0.97748 | -0.15843 | 0.0029205 | 0.00073194
93 | 0.9777 | -0.15683 | 0.0033138 | 0.00083051
94 | 0.97739 | -0.15908 | 0.0024933 | 0.00062488
95 | 0.97816 | -0.15351 | 0.0032683 | 0.00081912
96 | 0.97982 | -0.14167 | 0.0016492 | 0.00041332
97 | 0.97687 | -0.16278 | 0.0023263 | 0.00058303
98 | 0.97695 | -0.1622 | 0.0025765 | 0.00064573
99 | 0.98026 | -0.13854 | 0.0016576 | 0.00041542
100 | 0.98084 | -0.13439 | 0.0014546 | 0.00036457
101 | 0.97732 | -0.15954 | 0.0031553 | 0.0007908
102 | 0.97773 | -0.15661 | 0.0017024 | 0.00042665
103 | 0.98138 | -0.13098 | 0.0014735 | 0.00036928
104 | 0.98163 | -0.12921 | 0 | 0
105 | 0.98186 | -0.1276 | 0 | 0
106 | 0.98076 | -0.13545 | 0.0022937 | 0.00057485
107 | 0.98259 | -0.12238 | 0.001906 | 0.00047768
108 | 0.98055 | -0.1369 | 0.001587 | 0.00039774
109 | 0.98304 | -0.11915 | 0.0024444 | 0.00061262
110 | 0.98053 | -0.13708 | 0.0021081 | 0.00052834
111 | 0.9771 | -0.16111 | 0.0025776 | 0.000646
112 | 0.97759 | -0.15759 | 0.0016041 | 0.00040203
113 | 0.97752 | -0.15811 | 0.0020946 | 0.00052496
114 | 0.98623 | -0.096475 | 0 | 0
115 | 0.98594 | -0.098518 | 0 | 0
116 | 0.98525 | -0.10349 | 0.0019627 | 0.00049189
117 | 0.98474 | -0.10704 | 0.0018727 | 0.00046935
118 | 0.98514 | -0.10425 | 0.0020878 | 0.00052326
119 | 0.98446 | -0.10903 | 0 | 0
120 | 0.98425 | -0.11058 | 0.002012 | 0.00050426
121 | 0.98383 | -0.11358 | 0 | 0
122 | 0.98358 | -0.11536 | 0.0053236 | 0.0013342
123 | 0.98345 | -0.11631 | 0.0031543 | 0.00079054
124 | 0.98465 | -0.10736 | 0.0025396 | 0.00063649
125 | 0.98444 | -0.10891 | 0 | 0
126 | 0.98432 | -0.10972 | 0.001436 | 0.0003599
127 | 0.98436 | -0.10947 | 0.0032569 | 0.00081625
128 | 0.9843 | -0.10986 | 0.0035608 | 0.00089242
129 | 0.98987 | -0.070774 | 0.0025004 | 0.00062667
130 | 0.98962 | -0.072525 | 0.0035206 | 0.00088234
131 | 0.99003 | -0.069648 | 0.0059461 | 0.0014902
132 | 0.98941 | -0.074007 | 0.0019009 | 0.00047641
133 | 0.98928 | -0.074982 | 0.00083702 | 0.00020978
134 | 0.98927 | -0.075023 | 0.00064351 | 0.00016128
135 | 0.9843 | -0.11022 | 0.00025274 | 6.3343e-05
136 | 0.98428 | -0.11036 | 0.0014148 | 0.00035457
137 | 0.98437 | -0.10968 | 0.00283 | 0.00070927
138 | 0.98426 | -0.11045 | 0.00037478 | 9.3928e-05
139 | 0.9842 | -0.11089 | 0.0012309 | 0.00030849
140 | 0.98371 | -0.1144 | 0.0013874 | 0.00034771
141 | 0.98896 | -0.077194 | 0 | 0
142 | 0.98847 | -0.080682 | 0 | 0
143 | 0.98838 | -0.081322 | 0.0026499 | 0.00066413
144 | 0.98841 | -0.08114 | 0 | 0
145 | 0.98041 | -0.13795 | 0.0018856 | 0.00047257
146 | 0.9804 | -0.13795 | 0.0022119 | 0.00055435
147 | 0.98833 | -0.081722 | 0.0014483 | 0.00036298
148 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0043913 | 0.0010767 | -0.004391 | -0.0010778 | 3.1524e-07 | -1.1242e-06 | 0.0067202 | 0.0067206 | 0.0067206 | 0.97111 | -0.20681 | 0.97104 | -0.20735 | 0.82971
1 | -0.0055198 | -0.0013595 | 0.0055204 | 0.0013583 | 5.7643e-07 | -1.2193e-06 | 0.0084494 | 0.0084489 | 0.0084494 | 0.97111 | -0.20681 | 0.97121 | -0.20603 | 1.0431
2 | 0.00397 | 0.00097227 | -0.0039689 | -0.00097693 | 1.0471e-06 | -4.6557e-06 | 0.0060755 | 0.0060773 | 0.0060773 | 0.97104 | -0.20735 | 0.97077 | -0.20933 | 0.75028
3 | 0.00017457 | 4.3663e-05 | -0.00017457 | -4.3751e-05 | 3.1668e-10 | -8.7681e-08 | 0.00026743 | 0.00026746 | 0.00026746 | 0.97121 | -0.20603 | 0.97121 | -0.20604 | 0.099059
4 | -0.0058976 | -0.0014527 | 0.0059001 | 0.0014482 | 2.4881e-06 | -4.4967e-06 | 0.0090267 | 0.0090248 | 0.0090267 | 0.97121 | -0.20603 | 0.97164 | -0.20287 | 1.1144
5 | 0.0039689 | 0.00097693 | -0.0039687 | -0.00097785 | 2.0699e-07 | -9.1966e-07 | 0.0060773 | 0.0060776 | 0.0060776 | 0.97077 | -0.20933 | 0.97072 | -0.20972 | 0.75033
6 | -0.0060345 | -0.0014819 | 0.0060346 | 0.0014818 | 5.7529e-08 | -9.8489e-08 | 0.0092307 | 0.0092307 | 0.0092307 | 0.97164 | -0.20287 | 0.97165 | -0.2028 | 1.1396
7 | -0.00013955 | -3.4974e-05 | 0.00013955 | 3.4832e-05 | 3.2782e-10 | -1.4258e-07 | 0.00021364 | 0.00021359 | 0.00021364 | 0.97198 | -0.20029 | 0.97198 | -0.20027 | 0.079125
8 | -0.00075043 | -0.00018793 | 0.00075045 | 0.00018767 | 1.8155e-08 | -2.663e-07 | 0.0011488 | 0.0011487 | 0.0011488 | 0.97198 | -0.20027 | 0.97201 | -0.2001 | 0.42548
9 | -0.00048456 | -0.00012144 | 0.00048457 | 0.00012133 | 3.1557e-09 | -1.1387e-07 | 0.00073993 | 0.00073989 | 0.00073993 | 0.97447 | -0.1817 | 0.97448 | -0.18165 | 0.27405
10 | -0.0012752 | -0.00031904 | 0.0012753 | 0.0003187 | 6.8787e-08 | -3.3586e-07 | 0.001947 | 0.0019469 | 0.001947 | 0.97448 | -0.18165 | 0.97453 | -0.18126 | 0.72111
11 | 0.00079063 | 0.00019771 | -0.0007906 | -0.00019814 | 3.2596e-08 | -4.3399e-07 | 0.0012071 | 0.0012073 | 0.0012073 | 0.97448 | -0.18165 | 0.97444 | -0.18195 | 0.44714
12 | 0.0008443 | 0.00019914 | -0.00084405 | -0.00021057 | 2.4284e-07 | -1.1434e-05 | 0.0012898 | 0.0012939 | 0.0012939 | 0.97072 | -0.20972 | 0.97043 | -0.21193 | 0.23961
13 | 0.0029329 | 0.00073072 | -0.0029321 | -0.00073364 | 8.2495e-07 | -2.9174e-06 | 0.0044943 | 0.0044955 | 0.0044955 | 0.97072 | -0.20972 | 0.97044 | -0.21177 | 0.8325
14 | -0.011308 | -0.0027832 | 0.011309 | 0.002783 | 1.1346e-06 | -2.4918e-07 | 0.017248 | 0.017247 | 0.017248 | 0.97458 | -0.18095 | 0.97468 | -0.1802 | 2.1293
15 | 0.01017 | 0.0024978 | -0.010147 | -0.0025061 | 2.2938e-05 | -8.2704e-06 | 0.015509 | 0.015515 | 0.015515 | 0.97458 | -0.18095 | 0.97231 | -0.19782 | 1.9155
16 | -0.011535 | -0.0028396 | 0.011537 | 0.0028393 | 1.4711e-06 | -2.8881e-07 | 0.017592 | 0.017592 | 0.017592 | 0.97468 | -0.1802 | 0.97481 | -0.17925 | 2.1719
17 | 0.0088041 | 0.0021696 | -0.0088024 | -0.0021706 | 1.6903e-06 | -1.0184e-06 | 0.01346 | 0.013461 | 0.013461 | 0.97231 | -0.19782 | 0.97212 | -0.19926 | 1.6619
18 | -0.0060346 | -0.0014818 | 0.0060347 | 0.0014815 | 1.6764e-07 | -2.8701e-07 | 0.0092307 | 0.0092305 | 0.0092307 | 0.97165 | -0.2028 | 0.97167 | -0.20259 | 1.1396
19 | 0.0010219 | 0.00025488 | -0.0010219 | -0.00025491 | 3.4404e-09 | -2.6438e-08 | 0.0015664 | 0.0015665 | 0.0015665 | 0.97044 | -0.21177 | 0.97043 | -0.21179 | 0.58017
20 | 0.00086314 | 0.00021513 | -0.00086312 | -0.00021536 | 2.1252e-08 | -2.3218e-07 | 0.0013231 | 0.0013231 | 0.0013231 | 0.97043 | -0.21179 | 0.97041 | -0.21197 | 0.49005
21 | 0.00044489 | 0.00011127 | -0.00044489 | -0.0001115 | 5.3957e-09 | -2.2749e-07 | 0.00068211 | 0.00068219 | 0.00068219 | 0.97041 | -0.21197 | 0.9704 | -0.21206 | 0.25266
22 | 0.00041822 | 0.00010409 | -0.00041821 | -0.00010481 | 1.5155e-08 | -7.2404e-07 | 0.00064104 | 0.0006413 | 0.0006413 | 0.97041 | -0.21197 | 0.97037 | -0.21224 | 0.23752
23 | 0.00025984 | 6.4579e-05 | -0.00025983 | -6.512e-05 | 4.3452e-09 | -5.4057e-07 | 0.00039823 | 0.00039842 | 0.00039842 | 0.97043 | -0.21193 | 0.97041 | -0.21205 | 0.14756
24 | 0.00058422 | 0.00014599 | -0.00058421 | -0.00014612 | 5.4144e-09 | -1.3154e-07 | 0.00089566 | 0.00089571 | 0.00089571 | 0.97043 | -0.21193 | 0.97042 | -0.212 | 0.33174
25 | 0.00014875 | 3.6986e-05 | -0.00014875 | -3.7279e-05 | 7.7093e-10 | -2.9325e-07 | 0.00022798 | 0.00022808 | 0.00022808 | 0.97042 | -0.212 | 0.97042 | -0.21204 | 0.084475
26 | 0.014415 | 0.0035579 | -0.014412 | -0.0035579 | 2.8587e-06 | 3.5304e-08 | 0.02198 | 0.02198 | 0.02198 | 0.97501 | -0.17777 | 0.97481 | -0.17925 | 2.7136
27 | -0.014507 | -0.0035812 | 0.014518 | 0.0035813 | 1.0574e-05 | 1.7677e-07 | 0.022121 | 0.02212 | 0.022121 | 0.97501 | -0.17777 | 0.97574 | -0.17235 | 2.731
28 | 0.0028752 | 0.00071861 | -0.0028749 | -0.0007188 | 2.9682e-07 | -1.9376e-07 | 0.0043882 | 0.0043883 | 0.0043883 | 0.97481 | -0.17925 | 0.97471 | -0.18 | 1.6253
29 | -0.014518 | -0.0035813 | 0.014524 | 0.0035814 | 5.8725e-06 | 9.5434e-08 | 0.02212 | 0.022119 | 0.02212 | 0.97574 | -0.17235 | 0.97615 | -0.16933 | 2.7308
30 | 0.0021989 | 0.00054939 | -0.0021988 | -0.0005496 | 1.4707e-07 | -2.0418e-07 | 0.0033563 | 0.0033564 | 0.0033564 | 0.97471 | -0.18 | 0.97464 | -0.18048 | 1.2431
31 | -0.016564 | -0.0040926 | 0.016568 | 0.0040931 | 4.1017e-06 | 4.153e-07 | 0.025228 | 0.025228 | 0.025228 | 0.97615 | -0.16933 | 0.9764 | -0.1675 | 3.1146
32 | -0.0025427 | -0.00063727 | 0.0025428 | 0.00063722 | 4.8172e-08 | -4.476e-08 | 0.0038905 | 0.0038905 | 0.0038905 | 0.97253 | -0.19456 | 0.97255 | -0.19442 | 1.4409
33 | -0.0080865 | -0.0020266 | 0.0080879 | 0.002027 | 1.4421e-06 | 3.6727e-07 | 0.012372 | 0.012372 | 0.012372 | 0.97255 | -0.19442 | 0.97273 | -0.19314 | 4.5824
34 | 0.0016024 | 0.00040012 | -0.0016023 | -0.00040028 | 5.2063e-08 | -1.5378e-07 | 0.0024459 | 0.0024459 | 0.0024459 | 0.97464 | -0.18048 | 0.97461 | -0.18072 | 0.9059
35 | -0.018525 | -0.0045835 | 0.018532 | 0.0045847 | 7.3487e-06 | 1.1599e-06 | 0.02821 | 0.02821 | 0.02821 | 0.9764 | -0.1675 | 0.9768 | -0.16456 | 3.4827
36 | 0.0026297 | 0.00065882 | -0.0026295 | -0.00065901 | 2.126e-07 | -1.8685e-07 | 0.0039951 | 0.0039952 | 0.0039952 | 0.97944 | -0.14527 | 0.97935 | -0.14586 | 1.4797
37 | -0.024457 | -0.0060674 | 0.024483 | 0.0060741 | 2.6701e-05 | 6.7508e-06 | 0.037134 | 0.037133 | 0.037134 | 0.97944 | -0.14527 | 0.98054 | -0.13723 | 4.5844
38 | 0.021827 | 0.0054086 | -0.021775 | -0.0053972 | 5.153e-05 | 1.1323e-05 | 0.033139 | 0.033142 | 0.033142 | 0.97944 | -0.14527 | 0.97705 | -0.16272 | 4.0916
39 | -0.041519 | -0.010354 | 0.041576 | 0.010373 | 5.684e-05 | 1.9251e-05 | 0.062988 | 0.062987 | 0.062988 | 0.98054 | -0.13723 | 0.98193 | -0.12725 | 7.7763
40 | 0.017035 | 0.0042795 | -0.017007 | -0.0042695 | 2.8022e-05 | 9.9317e-06 | 0.025855 | 0.025856 | 0.025856 | 0.98054 | -0.13723 | 0.97888 | -0.14907 | 9.5762
41 | 0.019992 | 0.0049502 | -0.019987 | -0.0049493 | 4.9546e-06 | 9.3909e-07 | 0.030426 | 0.030426 | 0.030426 | 0.97705 | -0.16272 | 0.9768 | -0.16456 | 3.7563
42 | 0.0015422 | 0.00038519 | -0.001542 | -0.00038556 | 1.1403e-07 | -3.6701e-07 | 0.0023541 | 0.0023542 | 0.0023542 | 0.97461 | -0.18072 | 0.97453 | -0.18126 | 0.87193
43 | -0.0077262 | -0.0019039 | 0.0077267 | 0.0019035 | 4.2575e-07 | -3.8098e-07 | 0.011819 | 0.011818 | 0.011819 | 0.97181 | -0.20158 | 0.97186 | -0.20117 | 1.4591
44 | 0.0069386 | 0.0017065 | -0.0069379 | -0.0017073 | 6.7622e-07 | -8.1269e-07 | 0.010613 | 0.010613 | 0.010613 | 0.97181 | -0.20158 | 0.97171 | -0.20231 | 1.3102
45 | -0.0080498 | -0.0019845 | 0.0080509 | 0.0019836 | 1.1608e-06 | -9.2213e-07 | 0.012313 | 0.012313 | 0.012313 | 0.97186 | -0.20117 | 0.97201 | -0.2001 | 1.5201
46 | 0.0062838 | 0.0015435 | -0.0062837 | -0.0015437 | 1.0276e-07 | -1.5922e-07 | 0.0096114 | 0.0096115 | 0.0096115 | 0.97171 | -0.20231 | 0.97169 | -0.20244 | 1.1866
47 | 0.00065412 | 0.00016376 | -0.00065411 | -0.00016394 | 9.0484e-09 | -1.7555e-07 | 0.0010016 | 0.0010017 | 0.0010017 | 0.97171 | -0.20231 | 0.9717 | -0.20241 | 0.37099
48 | -0.0088014 | -0.0021712 | 0.0088024 | 0.0021706 | 9.9141e-07 | -5.9692e-07 | 0.013461 | 0.013461 | 0.013461 | 0.97201 | -0.2001 | 0.97212 | -0.19926 | 1.6619
49 | 0.0062837 | 0.0015437 | -0.0062836 | -0.0015439 | 1.2542e-07 | -1.9431e-07 | 0.0096115 | 0.0096116 | 0.0096116 | 0.97169 | -0.20244 | 0.97167 | -0.20259 | 1.1866
50 | 0.012343 | 0.0030936 | -0.012334 | -0.0030909 | 8.3545e-06 | 2.7459e-06 | 0.018866 | 0.018866 | 0.018866 | 0.97352 | -0.18744 | 0.97284 | -0.19233 | 6.9874
51 | -0.013922 | -0.0034895 | 0.013975 | 0.0035074 | 5.263e-05 | 1.7917e-05 | 0.02128 | 0.021279 | 0.02128 | 0.97352 | -0.18744 | 0.97731 | -0.16023 | 7.8815
52 | 0.010373 | 0.0025993 | -0.010372 | -0.002599 | 1.1553e-06 | 3.5304e-07 | 0.015866 | 0.015866 | 0.015866 | 0.97284 | -0.19233 | 0.97273 | -0.19314 | 5.8764
53 | -0.013975 | -0.0035074 | 0.013988 | 0.0035118 | 1.3042e-05 | 4.4374e-06 | 0.021279 | 0.021279 | 0.021279 | 0.97731 | -0.16023 | 0.97825 | -0.15351 | 7.8812
54 | 0.002284 | 0.00057201 | -0.0022837 | -0.00057234 | 2.6724e-07 | -3.3267e-07 | 0.0034938 | 0.0034939 | 0.0034939 | 0.97273 | -0.19314 | 0.97261 | -0.19398 | 1.294
55 | -0.015817 | -0.0039701 | 0.015826 | 0.0039736 | 9.7447e-06 | 3.4091e-06 | 0.024061 | 0.024061 | 0.024061 | 0.97825 | -0.15351 | 0.97888 | -0.14907 | 8.9114
56 | 0.00069991 | 0.0001754 | -0.0006999 | -0.00017541 | 8.9843e-10 | -1.524e-08 | 0.0010708 | 0.0010708 | 0.0010708 | 0.97261 | -0.19398 | 0.97261 | -0.19399 | 0.39659
57 | 0.22649 | 0.057163 | -0.22609 | -0.05701 | 0.00040095 | 0.00015354 | 0.33717 | 0.33717 | 0.33717 | 1 | 0 | 0.99817 | -0.012632 | 41.6256
58 | 0.22375 | 0.056422 | -0.22311 | -0.056177 | 0.00063871 | 0.00024458 | 0.33367 | 0.33367 | 0.33367 | 0.99817 | -0.012632 | 0.99524 | -0.033059 | 41.1936
59 | -0.048593 | -0.012132 | 0.048642 | 0.012149 | 4.8961e-05 | 1.7181e-05 | 0.073622 | 0.073621 | 0.073622 | 0.98193 | -0.12725 | 0.98295 | -0.11993 | 9.0891
60 | -0.055536 | -0.013876 | 0.055584 | 0.013894 | 4.8532e-05 | 1.7409e-05 | 0.084057 | 0.084056 | 0.084057 | 0.98295 | -0.11993 | 0.98383 | -0.11358 | 10.3774
61 | 0.22127 | 0.055716 | -0.22085 | -0.055558 | 0.0004136 | 0.00015837 | 0.33092 | 0.33092 | 0.33092 | 0.99524 | -0.033059 | 0.99332 | -0.046461 | 40.8541
62 | 0.13525 | 0.033981 | -0.13508 | -0.033917 | 0.00017042 | 6.4771e-05 | 0.20263 | 0.20263 | 0.20263 | 0.99332 | -0.046461 | 0.99203 | -0.055529 | 25.0165
63 | 0.082383 | 0.020768 | -0.082201 | -0.020698 | 0.00018204 | 6.977e-05 | 0.12345 | 0.12345 | 0.12345 | 0.99332 | -0.046461 | 0.99105 | -0.062273 | 45.724
64 | 0.029308 | 0.007348 | -0.029289 | -0.0073406 | 1.9646e-05 | 7.3459e-06 | 0.043963 | 0.043963 | 0.043963 | 0.99203 | -0.055529 | 0.99134 | -0.06037 | 16.2824
65 | 0.10577 | 0.026569 | -0.10573 | -0.026553 | 4.2145e-05 | 1.5898e-05 | 0.15867 | 0.15867 | 0.15867 | 0.99203 | -0.055529 | 0.99162 | -0.058395 | 19.589
66 | 0.080556 | 0.020286 | -0.080453 | -0.020246 | 0.00010349 | 3.9657e-05 | 0.12099 | 0.12099 | 0.12099 | 0.99105 | -0.062273 | 0.98974 | -0.071476 | 44.8095
67 | 0.0042459 | 0.0010633 | -0.0042456 | -0.0010633 | 3.612e-07 | -4.4816e-08 | 0.0063729 | 0.006373 | 0.006373 | 0.99134 | -0.06037 | 0.99125 | -0.060986 | 2.3604
68 | 0.025043 | 0.0062773 | -0.025027 | -0.0062718 | 1.508e-05 | 5.5797e-06 | 0.03759 | 0.03759 | 0.03759 | 0.99134 | -0.06037 | 0.99072 | -0.064721 | 13.9221
69 | 0.10362 | 0.026025 | -0.10335 | -0.025924 | 0.00026656 | 0.00010048 | 0.15551 | 0.15551 | 0.15551 | 0.99162 | -0.058395 | 0.98899 | -0.076946 | 19.1987
70 | 0.078161 | 0.019672 | -0.078021 | -0.019618 | 0.00013994 | 5.3616e-05 | 0.11754 | 0.11754 | 0.11754 | 0.98974 | -0.071476 | 0.98791 | -0.084324 | 43.5333
71 | 0.0015953 | 0.00039909 | -0.0015951 | -0.00039976 | 2.0765e-07 | -6.6813e-07 | 0.0023945 | 0.0023948 | 0.0023948 | 0.99125 | -0.060986 | 0.99112 | -0.061928 | 0.88695
72 | 0.021929 | 0.0054953 | -0.021924 | -0.0054932 | 5.7455e-06 | 2.1005e-06 | 0.032936 | 0.032937 | 0.032937 | 0.99072 | -0.064721 | 0.99046 | -0.066615 | 12.1987
73 | 0.10059 | 0.025231 | -0.10056 | -0.02522 | 2.9913e-05 | 1.1263e-05 | 0.15135 | 0.15135 | 0.15135 | 0.98899 | -0.076946 | 0.98868 | -0.079091 | 18.6853
74 | 0.074049 | 0.018623 | -0.074037 | -0.018619 | 1.1304e-05 | 4.3291e-06 | 0.11156 | 0.11156 | 0.11156 | 0.98791 | -0.084324 | 0.98776 | -0.085419 | 41.3173
75 | 0.099446 | 0.024942 | -0.099381 | -0.024917 | 6.5707e-05 | 2.473e-05 | 0.14968 | 0.14968 | 0.14968 | 0.98868 | -0.079091 | 0.98801 | -0.08386 | 18.4788
76 | 0.097664 | 0.024487 | -0.097585 | -0.024457 | 7.9067e-05 | 2.9736e-05 | 0.14709 | 0.14709 | 0.14709 | 0.98801 | -0.08386 | 0.98718 | -0.089708 | 18.1596
77 | 0.095746 | 0.023996 | -0.095656 | -0.023962 | 8.9604e-05 | 3.367e-05 | 0.14432 | 0.14432 | 0.14432 | 0.98718 | -0.089708 | 0.98623 | -0.096475 | 17.8174
78 | 0.019466 | 0.0048772 | -0.019457 | -0.0048742 | 8.1673e-06 | 2.9444e-06 | 0.029244 | 0.029244 | 0.029244 | 0.99046 | -0.066615 | 0.99003 | -0.069648 | 10.8311
79 | 0.050341 | 0.012645 | -0.050298 | -0.012629 | 4.2875e-05 | 1.634e-05 | 0.076167 | 0.076167 | 0.076167 | 0.9836 | -0.11476 | 0.98274 | -0.12089 | 28.21
80 | -0.052379 | -0.013156 | 0.052487 | 0.013197 | 0.00010747 | 4.0984e-05 | 0.07925 | 0.07925 | 0.07925 | 0.9836 | -0.11476 | 0.98568 | -0.10003 | 29.352
81 | 0.048926 | 0.012285 | -0.048893 | -0.012273 | 3.2268e-05 | 1.2291e-05 | 0.074089 | 0.074089 | 0.074089 | 0.98274 | -0.12089 | 0.98207 | -0.12564 | 27.4405
82 | 0.016989 | 0.0042591 | -0.016984 | -0.0042571 | 5.6435e-06 | 1.9954e-06 | 0.025648 | 0.025648 | 0.025648 | 0.98568 | -0.10003 | 0.98535 | -0.10243 | 9.4993
83 | 0.0026492 | 0.00066372 | -0.002649 | -0.0006639 | 1.9725e-07 | -1.7604e-07 | 0.0039992 | 0.0039993 | 0.0039993 | 0.98568 | -0.10003 | 0.98561 | -0.10057 | 1.4812
84 | -0.072125 | -0.01812 | 0.072272 | 0.018176 | 0.00014693 | 5.6257e-05 | 0.1089 | 0.1089 | 0.1089 | 0.98568 | -0.10003 | 0.98776 | -0.085419 | 40.3325
85 | 0.047524 | 0.011929 | -0.047518 | -0.011927 | 5.7079e-06 | 2.173e-06 | 0.072014 | 0.072014 | 0.072014 | 0.98207 | -0.12564 | 0.98195 | -0.1265 | 26.672
86 | 0.01522 | 0.003815 | -0.015211 | -0.0038121 | 8.5281e-06 | 2.9507e-06 | 0.022984 | 0.022984 | 0.022984 | 0.98535 | -0.10243 | 0.98478 | -0.10648 | 8.5127
87 | 0.044454 | 0.011159 | -0.044432 | -0.011151 | 2.2119e-05 | 8.4084e-06 | 0.067371 | 0.067372 | 0.067372 | 0.98195 | -0.1265 | 0.98144 | -0.13009 | 24.9524
88 | 0.013258 | 0.0033225 | -0.013257 | -0.0033222 | 8.7694e-07 | 2.9273e-07 | 0.020033 | 0.020033 | 0.020033 | 0.98478 | -0.10648 | 0.98471 | -0.10696 | 7.4195
89 | 0.042945 | 0.010778 | -0.04292 | -0.010769 | 2.5659e-05 | 9.7464e-06 | 0.065117 | 0.065117 | 0.065117 | 0.98144 | -0.13009 | 0.98084 | -0.13439 | 24.1174
90 | 0.010797 | 0.0027056 | -0.010796 | -0.0027054 | 6.0684e-07 | 1.8692e-07 | 0.016315 | 0.016315 | 0.016315 | 0.98471 | -0.10696 | 0.98465 | -0.10736 | 6.0425
91 | 0.01565 | 0.0039229 | -0.015641 | -0.0039197 | 9.2692e-06 | 3.2361e-06 | 0.023804 | 0.023804 | 0.023804 | 0.97829 | -0.15259 | 0.97769 | -0.15687 | 8.8165
92 | 0.010407 | 0.0026076 | -0.010404 | -0.0026067 | 3.0134e-06 | 9.1707e-07 | 0.015829 | 0.015829 | 0.015829 | 0.97829 | -0.15259 | 0.978 | -0.15468 | 5.8626
93 | -0.026057 | -0.0065305 | 0.026074 | 0.006537 | 1.7361e-05 | 6.4548e-06 | 0.039633 | 0.039633 | 0.039633 | 0.97829 | -0.15259 | 0.97896 | -0.14778 | 14.679
94 | 0.010642 | 0.0026669 | -0.010638 | -0.0026657 | 3.9344e-06 | 1.212e-06 | 0.016197 | 0.016197 | 0.016197 | 0.97769 | -0.15687 | 0.97732 | -0.15954 | 5.9989
95 | 0.0054032 | 0.0013534 | -0.0054018 | -0.0013533 | 1.4388e-06 | 1.2537e-07 | 0.0082207 | 0.0082208 | 0.0082208 | 0.978 | -0.15468 | 0.97773 | -0.15661 | 3.0447
96 | -0.038085 | -0.0095475 | 0.038117 | 0.0095597 | 3.227e-05 | 1.2217e-05 | 0.05789 | 0.05789 | 0.05789 | 0.97896 | -0.14778 | 0.97982 | -0.14167 | 21.4406
97 | 0.012011 | 0.0030105 | -0.012001 | -0.0030074 | 9.5185e-06 | 3.086e-06 | 0.018256 | 0.018257 | 0.018257 | 0.97896 | -0.14778 | 0.97816 | -0.15351 | 6.7617
98 | -0.005414 | -0.0013566 | 0.0054152 | 0.0013567 | 1.1983e-06 | 1.0641e-07 | 0.0082416 | 0.0082415 | 0.0082416 | 0.97748 | -0.15843 | 0.9777 | -0.15683 | 3.0525
99 | 0.0024935 | 0.00062465 | -0.0024933 | -0.00062488 | 2.2469e-07 | -2.2682e-07 | 0.0037958 | 0.0037959 | 0.0037959 | 0.97748 | -0.15843 | 0.97739 | -0.15908 | 1.4059
100 | -0.0087289 | -0.0021872 | 0.0087329 | 0.0021883 | 4.0141e-06 | 1.0866e-06 | 0.013285 | 0.013285 | 0.013285 | 0.9777 | -0.15683 | 0.97816 | -0.15351 | 4.9203
101 | -0.039766 | -0.009973 | 0.039784 | 0.0099796 | 1.7276e-05 | 6.549e-06 | 0.060394 | 0.060394 | 0.060394 | 0.97982 | -0.14167 | 0.98026 | -0.13854 | 22.3682
102 | -0.0023263 | -0.00058303 | 0.0023265 | 0.0005828 | 1.8906e-07 | -2.294e-07 | 0.0035436 | 0.0035435 | 0.0035436 | 0.97687 | -0.16278 | 0.97695 | -0.1622 | 1.3124
103 | -0.004903 | -0.0012285 | 0.0049037 | 0.0012286 | 7.3401e-07 | 1.8156e-08 | 0.0074678 | 0.0074677 | 0.0074678 | 0.97695 | -0.1622 | 0.9771 | -0.16111 | 2.7659
104 | -0.041441 | -0.010395 | 0.041465 | 0.010404 | 2.3828e-05 | 9.043e-06 | 0.06291 | 0.06291 | 0.06291 | 0.98026 | -0.13854 | 0.98084 | -0.13439 | 23.3001
105 | 0.007483 | 0.0018749 | -0.0074813 | -0.0018746 | 1.6274e-06 | 3.7419e-07 | 0.011393 | 0.011393 | 0.011393 | 0.97732 | -0.15954 | 0.9771 | -0.16111 | 4.2197
106 | 0.0036994 | 0.00092663 | -0.0036989 | -0.00092675 | 5.0288e-07 | -1.2541e-07 | 0.00563 | 0.0056301 | 0.0056301 | 0.97773 | -0.15661 | 0.97759 | -0.15759 | 2.0852
107 | -0.0014735 | -0.00036928 | 0.0014738 | 0.00036796 | 3.6016e-07 | -1.3233e-06 | 0.0022341 | 0.0022336 | 0.0022341 | 0.98138 | -0.13098 | 0.98163 | -0.12921 | 0.82745
108 | -0.011571 | -0.0028988 | 0.011574 | 0.0028996 | 2.576e-06 | 8.2109e-07 | 0.01754 | 0.01754 | 0.01754 | 0.98163 | -0.12921 | 0.98186 | -0.1276 | 6.4962
109 | 0.010097 | 0.0025308 | -0.010088 | -0.0025282 | 8.7262e-06 | 2.6023e-06 | 0.015306 | 0.015306 | 0.015306 | 0.98163 | -0.12921 | 0.98076 | -0.13545 | 5.669
110 | -0.011574 | -0.0028996 | 0.011582 | 0.0029022 | 8.3591e-06 | 2.6639e-06 | 0.01754 | 0.017539 | 0.01754 | 0.98186 | -0.1276 | 0.98259 | -0.12238 | 6.4961
111 | 0.0077948 | 0.0019533 | -0.0077932 | -0.001953 | 1.5607e-06 | 3.7466e-07 | 0.011826 | 0.011826 | 0.011826 | 0.98076 | -0.13545 | 0.98055 | -0.1369 | 4.3801
112 | -0.013488 | -0.0033799 | 0.013494 | 0.0033819 | 6.0235e-06 | 2.0235e-06 | 0.020426 | 0.020426 | 0.020426 | 0.98259 | -0.12238 | 0.98304 | -0.11915 | 7.5651
113 | 0.0062062 | 0.0015552 | -0.0062061 | -0.0015552 | 1.5557e-07 | 2.4381e-08 | 0.0094181 | 0.0094181 | 0.0094181 | 0.98055 | -0.1369 | 0.98053 | -0.13708 | 3.4882
114 | -0.015938 | -0.0039946 | 0.015949 | 0.0039982 | 1.0487e-05 | 3.6671e-06 | 0.024126 | 0.024126 | 0.024126 | 0.98304 | -0.11915 | 0.98371 | -0.1144 | 8.9354
115 | 0.004098 | 0.0010269 | -0.0040975 | -0.0010269 | 4.9248e-07 | -6.7952e-08 | 0.0062189 | 0.0062189 | 0.0062189 | 0.98053 | -0.13708 | 0.98041 | -0.13795 | 2.3033
116 | 0.0020948 | 0.00052472 | -0.0020946 | -0.00052496 | 1.5027e-07 | -2.3919e-07 | 0.0031884 | 0.0031885 | 0.0031885 | 0.97759 | -0.15759 | 0.97752 | -0.15811 | 1.1809
117 | 0.095656 | 0.023962 | -0.095629 | -0.023952 | 2.7029e-05 | 1.0157e-05 | 0.14432 | 0.14432 | 0.14432 | 0.98623 | -0.096475 | 0.98594 | -0.098518 | 17.8174
118 | 0.070267 | 0.01759 | -0.070218 | -0.017572 | 4.8233e-05 | 1.7763e-05 | 0.10604 | 0.10604 | 0.10604 | 0.98594 | -0.098518 | 0.98525 | -0.10349 | 13.0915
119 | 0.025362 | 0.0063624 | -0.025332 | -0.0063513 | 2.9957e-05 | 1.1105e-05 | 0.03828 | 0.03828 | 0.03828 | 0.98594 | -0.098518 | 0.98474 | -0.10704 | 14.1778
120 | 0.068256 | 0.01708 | -0.068249 | -0.017077 | 7.1145e-06 | 2.6134e-06 | 0.10308 | 0.10308 | 0.10308 | 0.98525 | -0.10349 | 0.98514 | -0.10425 | 12.7256
121 | 0.02346 | 0.005882 | -0.023453 | -0.0058796 | 6.4425e-06 | 2.3734e-06 | 0.03545 | 0.03545 | 0.03545 | 0.98474 | -0.10704 | 0.98446 | -0.10903 | 13.1297
122 | 0.066161 | 0.016554 | -0.066103 | -0.016533 | 5.7752e-05 | 2.1151e-05 | 0.099924 | 0.099924 | 0.099924 | 0.98514 | -0.10425 | 0.98425 | -0.11058 | 12.3363
123 | 0.01858 | 0.0046591 | -0.018576 | -0.0046574 | 4.7953e-06 | 1.7205e-06 | 0.028085 | 0.028085 | 0.028085 | 0.98446 | -0.10903 | 0.9842 | -0.11089 | 10.4019
124 | 0.0048729 | 0.0012205 | -0.0048725 | -0.0012205 | 4.3995e-07 | 3.9691e-09 | 0.0073651 | 0.0073652 | 0.0073652 | 0.98446 | -0.10903 | 0.98437 | -0.10968 | 2.7279
125 | 0.064091 | 0.016029 | -0.064064 | -0.016019 | 2.653e-05 | 9.6859e-06 | 0.096882 | 0.096882 | 0.096882 | 0.98425 | -0.11058 | 0.98383 | -0.11358 | 11.9608
126 | 0.0084804 | 0.0021251 | -0.0084783 | -0.0021245 | 2.0904e-06 | 5.4547e-07 | 0.012826 | 0.012826 | 0.012826 | 0.98383 | -0.11358 | 0.98358 | -0.11536 | 4.7505
127 | 0.0031547 | 0.00079034 | -0.0031543 | -0.00079054 | 4.1111e-07 | -2.0894e-07 | 0.0047725 | 0.0047727 | 0.0047727 | 0.98358 | -0.11536 | 0.98345 | -0.11631 | 1.7676
128 | 0.0082563 | 0.0020689 | -0.0082546 | -0.0020684 | 1.7612e-06 | 4.4681e-07 | 0.012477 | 0.012477 | 0.012477 | 0.98465 | -0.10736 | 0.98444 | -0.10891 | 4.6211
129 | 0.0049974 | 0.0012523 | -0.0049969 | -0.0012523 | 5.6363e-07 | 1.5541e-08 | 0.0075538 | 0.0075538 | 0.0075538 | 0.98444 | -0.10891 | 0.98432 | -0.10972 | 2.7977
130 | 0.0032571 | 0.00081614 | -0.0032569 | -0.00081625 | 2.5396e-07 | -1.1579e-07 | 0.0049232 | 0.0049233 | 0.0049233 | 0.98444 | -0.10891 | 0.98436 | -0.10947 | 1.8235
131 | 0.0035609 | 0.0008924 | -0.0035608 | -0.00089242 | 6.7044e-08 | -2.1344e-08 | 0.005383 | 0.005383 | 0.005383 | 0.98432 | -0.10972 | 0.9843 | -0.10986 | 1.9937
132 | 0.011009 | 0.0027566 | -0.011006 | -0.0027558 | 2.6633e-06 | 8.2405e-07 | 0.016548 | 0.016548 | 0.016548 | 0.98987 | -0.070774 | 0.98962 | -0.072525 | 6.129
133 | -0.013509 | -0.0033833 | 0.013511 | 0.003384 | 2.1031e-06 | 7.0381e-07 | 0.020307 | 0.020307 | 0.020307 | 0.98987 | -0.070774 | 0.99003 | -0.069648 | 7.5211
134 | 0.0074856 | 0.0018735 | -0.0074841 | -0.0018731 | 1.5307e-06 | 3.3996e-07 | 0.011255 | 0.011255 | 0.011255 | 0.98962 | -0.072525 | 0.98941 | -0.074007 | 4.1684
135 | 0.0055832 | 0.0013967 | -0.0055824 | -0.0013966 | 7.5129e-07 | 6.963e-08 | 0.0083959 | 0.0083959 | 0.0083959 | 0.98941 | -0.074007 | 0.98928 | -0.074982 | 3.1096
136 | 0.0047454 | 0.0011869 | -0.0047454 | -0.0011869 | 2.6366e-08 | -5.0993e-10 | 0.0071369 | 0.0071369 | 0.0071369 | 0.98928 | -0.074982 | 0.98927 | -0.075023 | 2.6433
137 | 0.0041019 | 0.0010256 | -0.0041007 | -0.0010258 | 1.228e-06 | -1.9139e-07 | 0.006169 | 0.0061692 | 0.0061692 | 0.98927 | -0.075023 | 0.98896 | -0.077194 | 2.2849
138 | 0.0017896 | 0.00044813 | -0.0017895 | -0.00044821 | 3.3674e-08 | -8.0769e-08 | 0.0027053 | 0.0027053 | 0.0027053 | 0.9843 | -0.11022 | 0.98428 | -0.11036 | 1.002
139 | -0.0020423 | -0.00051147 | 0.0020425 | 0.0005112 | 1.5276e-07 | -2.6772e-07 | 0.0030874 | 0.0030872 | 0.0030874 | 0.9843 | -0.11022 | 0.98437 | -0.10968 | 1.1435
140 | 0.00037478 | 9.3635e-05 | -0.00037478 | -9.3928e-05 | 4.6452e-09 | -2.9299e-07 | 0.00056649 | 0.00056659 | 0.00056659 | 0.98428 | -0.11036 | 0.98426 | -0.11045 | 0.20985
141 | 0.017345 | 0.0043489 | -0.017336 | -0.0043459 | 8.4387e-06 | 2.9959e-06 | 0.026224 | 0.026224 | 0.026224 | 0.9842 | -0.11089 | 0.98371 | -0.1144 | 9.7127
142 | 0.0041007 | 0.0010258 | -0.0040987 | -0.0010261 | 1.9732e-06 | -3.0658e-07 | 0.0061692 | 0.0061696 | 0.0061696 | 0.98896 | -0.077194 | 0.98847 | -0.080682 | 2.285
143 | 0.0026502 | 0.00066392 | -0.0026499 | -0.00066413 | 2.3497e-07 | -2.1289e-07 | 0.0039894 | 0.0039895 | 0.0039895 | 0.98847 | -0.080682 | 0.98838 | -0.081322 | 1.4776
144 | 0.0014485 | 0.00036216 | -0.0014484 | -0.00036252 | 9.1574e-08 | -3.6048e-07 | 0.0021802 | 0.0021804 | 0.0021804 | 0.98847 | -0.080682 | 0.98841 | -0.08114 | 0.80755
145 | 0.0014484 | 0.00036252 | -0.0014483 | -0.00036298 | 1.1663e-07 | -4.5895e-07 | 0.0021804 | 0.0021806 | 0.0021806 | 0.98841 | -0.08114 | 0.98833 | -0.081722 | 0.80762
146 | 0.0022119 | 0.00055435 | -0.0022119 | -0.00055435 | 1.6504e-09 | -2.3245e-09 | 0.0033571 | 0.0033571 | 0.0033571 | 0.98041 | -0.13795 | 0.9804 | -0.13795 | 1.2434

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2314 | 0.058192

## res_load
| p_mw | q_mvar
0 | 0.0011285 | 0.00028284
1 | 0.000421 | 0.00010551
2 | 0.00020259 | 5.0773e-05
3 | 0.00017457 | 4.3751e-05
4 | 0.00013447 | 3.3701e-05
5 | 0.00013955 | 3.4974e-05
6 | 0.00061088 | 0.0001531
7 | 0.00048456 | 0.00012144
8 | 0.00019149 | 4.7992e-05
9 | 0.0011386 | 0.00028536
10 | 0.00022586 | 5.6605e-05
11 | 0.0013426 | 0.0003365
12 | 0.0019102 | 0.00047875
13 | 0.00015873 | 3.9782e-05
14 | 0.00044489 | 0.0001115
15 | 0.00041821 | 0.00010481
16 | 0.00043547 | 0.00010914
17 | 0.00014875 | 3.7279e-05
18 | 0.00025983 | 6.512e-05
19 | 9.2745e-05 | 2.3244e-05
20 | 0.00067596 | 0.00016941
21 | 0.0020397 | 0.00051121
22 | 0.0025427 | 0.00063727
23 | 0.0055437 | 0.0013894
24 | 0.00059641 | 0.00014947
25 | 0.0019569 | 0.00049046
26 | 0.0007906 | 0.00019814
27 | 0.0026295 | 0.00065901
28 | 0.0017835 | 0.000447
29 | 6.0176e-05 | 1.5081e-05
30 | 0.0014549 | 0.00036463
31 | 0.00026677 | 6.6859e-05
32 | 0.00078764 | 0.0001974
33 | 0.00032312 | 8.098e-05
34 | 0.00065411 | 0.00016394
35 | 0.00024882 | 6.236e-05
36 | 0.0015795 | 0.00039586
37 | 0.0019613 | 0.00049154
38 | 0.0018287 | 0.00045831
39 | 0.0015838 | 0.00039694
40 | 0.0006999 | 0.00017541
41 | 0.001181 | 0.00029598
42 | 0.0041026 | 0.0010282
43 | 0.0023473 | 0.0005883
44 | 0.0070177 | 0.0017588
45 | 0.0068934 | 0.0017276
46 | 0.0018395 | 0.00046102
47 | 0.0032247 | 0.00080818
48 | 0.0016445 | 0.00041215
49 | 0.0021071 | 0.00052808
50 | 0.002292 | 0.00057442
51 | 0.0026503 | 0.00066423
52 | 0.0030982 | 0.00077647
53 | 0.0027643 | 0.0006928
54 | 0.0039723 | 0.00099555
55 | 0.0011115 | 0.00027856
56 | 0.0017166 | 0.00043021
57 | 0.0018394 | 0.000461
58 | 0.0015951 | 0.00039976
59 | 0.0024579 | 0.00061602
60 | 0.0020382 | 0.00051082
61 | 0.0013723 | 0.00034393
62 | 0.0013693 | 0.00034319
63 | 0.0017641 | 0.00044212
64 | 0.002649 | 0.0006639
65 | 0.0017652 | 0.00044241
66 | 0.0030639 | 0.00076789
67 | 0.0019535 | 0.00048958
68 | 0.001487 | 0.00037268
69 | 0.0024603 | 0.00061661
70 | 0.0049985 | 0.0012527
71 | 0.0050007 | 0.0012533
72 | 0.0029205 | 0.00073194
73 | 0.0033138 | 0.00083051
74 | 0.0024933 | 0.00062488
75 | 0.0032683 | 0.00081912
76 | 0.0016492 | 0.00041332
77 | 0.0023263 | 0.00058303
78 | 0.0025765 | 0.00064573
79 | 0.0016576 | 0.00041542
80 | 0.0014546 | 0.00036457
81 | 0.0031553 | 0.0007908
82 | 0.0017024 | 0.00042665
83 | 0.0014735 | 0.00036928
84 | 0.0022937 | 0.00057485
85 | 0.001906 | 0.00047768
86 | 0.001587 | 0.00039774
87 | 0.0024444 | 0.00061262
88 | 0.0021081 | 0.00052834
89 | 0.0025776 | 0.000646
90 | 0.0016041 | 0.00040203
91 | 0.0020946 | 0.00052496
92 | 0.0019627 | 0.00049189
93 | 0.0018727 | 0.00046935
94 | 0.0020878 | 0.00052326
95 | 0.002012 | 0.00050426
96 | 0.0053236 | 0.0013342
97 | 0.0031543 | 0.00079054
98 | 0.0025396 | 0.00063649
99 | 0.001436 | 0.0003599
100 | 0.0032569 | 0.00081625
101 | 0.0035608 | 0.00089242
102 | 0.0025004 | 0.00062667
103 | 0.0035206 | 0.00088234
104 | 0.0059461 | 0.0014902
105 | 0.0019009 | 0.00047641
106 | 0.00083702 | 0.00020978
107 | 0.00064351 | 0.00016128
108 | 0.00025274 | 6.3343e-05
109 | 0.0014148 | 0.00035457
110 | 0.00283 | 0.00070927
111 | 0.00037478 | 9.3928e-05
112 | 0.0012309 | 0.00030849
113 | 0.0013874 | 0.00034771
114 | 0.0026499 | 0.00066413
115 | 0.0018856 | 0.00047257
116 | 0.0022119 | 0.00055435
117 | 0.0014483 | 0.00036298

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1