## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1150-8_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1150-8_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1150-8_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1150-8_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1150-8_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1150-8_0_3_node_16 | 0.4 | n |  | TRUE
6 | bus_LV_1150-8_0_3_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_1150-8_0_3_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_1150-8_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1150-8_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_1150-8_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1150-8_0_3_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_1150-8_0_3_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_1150-8_0_3_node_17 | 0.4 | n |  | TRUE
14 | bus_LV_1150-8_0_3_node_21 | 0.4 | n |  | TRUE
15 | bus_LV_1150-8_0_3_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1150-8_0_3_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1150-8_0_3_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1150-8_0_3_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1150-8_0_3_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1150-8_0_3_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1150-8_0_3_node_36 | 0.4 | n |  | TRUE
22 | bus_LV_1150-8_0_3_node_33 | 0.4 | n |  | TRUE
23 | bus_LV_1150-8_0_3_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1150-8_0_3_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1150-8_0_3_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_1150-8_0_3_node_27 | 0.4 | n |  | TRUE
27 | bus_LV_1150-8_0_3_node_28 | 0.4 | n |  | TRUE
28 | bus_LV_1150-8_0_3_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_1150-8_0_3_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_1150-8_0_3_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1150-8_0_3_node_37 | 0.4 | n |  | TRUE
32 | bus_LV_1150-8_0_3_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_1150-8_0_3_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_1150-8_0_3_node_39 | 0.4 | n |  | TRUE
35 | bus_MV_129_0_node_248 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1150-8_0_3_load_0 | 0 | 0.012126 | 0.003039 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1150-8_0_3_load_1 | 1 | 0.0062002 | 0.0015539 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1150-8_0_3_load_2 | 2 | 0.011765 | 0.0029486 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1150-8_0_3_load_3 | 3 | 0.0083113 | 0.002083 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1150-8_0_3_load_16 | 5 | 0.0022824 | 0.00057203 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1150-8_0_3_load_19 | 6 | 0.005951 | 0.0014915 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1150-8_0_3_load_14 | 7 | 0.0022824 | 0.00057203 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1150-8_0_3_load_5 | 8 | 0.0042799 | 0.0010727 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1150-8_0_3_load_11 | 11 | 0.0025508 | 0.0006393 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1150-8_0_3_load_35 | 12 | 0.04618 | 0.011574 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1150-8_0_3_load_21 | 14 | 0.0044745 | 0.0011214 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1150-8_0_3_load_18 | 16 | 0.046175 | 0.011572 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1150-8_0_3_load_15 | 17 | 0.0043243 | 0.0010838 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1150-8_0_3_load_12 | 18 | 0.0082288 | 0.0020623 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1150-8_0_3_load_13 | 19 | 0.017375 | 0.0043547 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1150-8_0_3_load_23 | 20 | 0.0032733 | 0.00082036 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1150-8_0_3_load_36 | 21 | 0.011443 | 0.002868 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1150-8_0_3_load_33 | 22 | 0.0087164 | 0.0021845 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1150-8_0_3_load_24 | 23 | 0.0023275 | 0.00058332 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1150-8_0_3_load_29 | 25 | 0.0073499 | 0.0018421 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1150-8_0_3_load_27 | 26 | 0.0016779 | 0.00042053 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1150-8_0_3_load_34 | 29 | 0.00248 | 0.00062154 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1150-8_0_3_load_31 | 30 | 0.0017862 | 0.00044766 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1150-8_0_3_load_32 | 32 | 0.0014319 | 0.00035888 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1150-8_0_3_load_39 | 34 | 0.0098604 | 0.0024713 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 13 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1150-8_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.027465 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1150-8_0_3_line_1 | NAYY 4x150 SE | 1 | 2 | 0.0026688 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1150-8_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.046416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1150-8_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.020665 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1150-8_0_3_line_4 | NAYY 4x150 SE | 4 | 5 | 0.023092 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1150-8_0_3_line_5 | NAYY 4x150 SE | 4 | 6 | 0.0012521 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1150-8_0_3_line_6 | NAYY 4x150 SE | 5 | 7 | 0.0071257 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1150-8_0_3_line_7 | NAYY 4x150 SE | 7 | 18 | 0.015795 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1150-8_0_3_line_8 | NAYY 4x150 SE | 8 | 9 | 0.014877 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1150-8_0_3_line_9 | NAYY 4x150 SE | 9 | 10 | 0.020904 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1150-8_0_3_line_10 | NAYY 4x150 SE | 9 | 11 | 0.004519 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1150-8_0_3_line_11 | NAYY 4x150 SE | 10 | 12 | 0.013623 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1150-8_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.033922 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1150-8_0_3_line_13 | NAYY 4x150 SE | 13 | 16 | 0.04752 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1150-8_0_3_line_14 | NAYY 4x150 SE | 13 | 17 | 0.019435 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1150-8_0_3_line_15 | NAYY 4x150 SE | 14 | 15 | 0.029972 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1150-8_0_3_line_16 | NAYY 4x150 SE | 15 | 20 | 0.0098707 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1150-8_0_3_line_17 | NAYY 4x150 SE | 15 | 16 | 0.026123 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1150-8_0_3_line_18 | NAYY 4x150 SE | 17 | 19 | 0.00089782 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1150-8_0_3_line_19 | NAYY 4x150 SE | 18 | 19 | 0.029751 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1150-8_0_3_line_20 | NAYY 4x150 SE | 20 | 21 | 0.00022894 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1150-8_0_3_line_21 | NAYY 4x150 SE | 21 | 22 | 0.015335 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1150-8_0_3_line_22 | NAYY 4x150 SE | 22 | 32 | 0.02193 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1150-8_0_3_line_23 | NAYY 4x150 SE | 23 | 24 | 0.0373 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1150-8_0_3_line_24 | NAYY 4x150 SE | 24 | 25 | 0.040787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1150-8_0_3_line_25 | NAYY 4x150 SE | 25 | 26 | 0.022137 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1150-8_0_3_line_26 | NAYY 4x150 SE | 26 | 27 | 0.0078501 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1150-8_0_3_line_27 | NAYY 4x150 SE | 27 | 28 | 0.021181 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1150-8_0_3_line_28 | NAYY 4x150 SE | 28 | 29 | 0.018531 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1150-8_0_3_line_29 | NAYY 4x150 SE | 28 | 30 | 0.021403 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1150-8_0_3_line_30 | NAYY 4x150 SE | 29 | 31 | 0.012381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1150-8_0_3_line_31 | NAYY 4x150 SE | 30 | 32 | 0.017243 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1150-8_0_3_line_32 | NAYY 4x150 SE | 31 | 33 | 0.091942 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1150-8_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.045215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1150-8_0_3_trafo_17 | 0.25 MVA 20/0.4 kV | 35 | 13 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2636796.4604 | 1221150.9261 | 2636819.2877 | 1221135.6545
1 | 2636821.5059 | 1221134.1705 | 2636819.2877 | 1221135.6545
2 | 2636821.5059 | 1221134.1705 | 2636825.4271 | 1221131.5472 | 2636829.9315 | 1221126.8945 | 2636843.3427 | 1221097.571 | 2636843.945 | 1221094.6546
3 | 2636842.4255 | 1221074.1403 | 2636844.3906 | 1221092.4967 | 2636843.945 | 1221094.6546
4 | 2636842.4255 | 1221074.1403 | 2636820.1258 | 1221077.3267 | 2636819.5661 | 1221077.4064
5 | 2636842.4255 | 1221074.1403 | 2636843.6651 | 1221073.9635
6 | 2636812.5117 | 1221078.4115 | 2636819.5661 | 1221077.4064
7 | 2636812.5117 | 1221078.4115 | 2636807.6358 | 1221079.1062 | 2636797.0308 | 1221081.4934
8 | 2636744.8562 | 1221130.4272 | 2636742.9396 | 1221137.3862 | 2636740.6414 | 1221144.6927
9 | 2636744.8562 | 1221130.4272 | 2636736.7555 | 1221129.0209 | 2636732.7992 | 1221127.2066 | 2636725.0279 | 1221124.0569
10 | 2636744.8562 | 1221130.4272 | 2636745.8599 | 1221126.0212
11 | 2636725.0279 | 1221124.0569 | 2636712.4048 | 1221118.9349
12 | 2636748.17 | 1221092.4918 | 2636749.0168 | 1221097.878 | 2636749.1242 | 1221107.5177 | 2636748.5208 | 1221114.3403 | 2636745.8599 | 1221126.0212
13 | 2636748.17 | 1221092.4918 | 2636745.9702 | 1221082.6391 | 2636741.9675 | 1221072.3527 | 2636732.071 | 1221047.8923
14 | 2636748.17 | 1221092.4918 | 2636767.1303 | 1221088.2239
15 | 2636723.6545 | 1221023.1774 | 2636715.0143 | 1221042.8247 | 2636713.6731 | 1221046.263 | 2636712.3241 | 1221049.7456 | 2636711.9309 | 1221050.7553
16 | 2636723.6545 | 1221023.1774 | 2636722.5886 | 1221013.3644
17 | 2636723.6545 | 1221023.1774 | 2636729.5487 | 1221041.658 | 2636732.071 | 1221047.8923
18 | 2636768.0062 | 1221088.0267 | 2636767.1303 | 1221088.2239
19 | 2636768.0062 | 1221088.0267 | 2636797.0308 | 1221081.4934
20 | 2636722.5639 | 1221013.1368 | 2636722.5886 | 1221013.3644
21 | 2636722.5639 | 1221013.1368 | 2636721.9603 | 1221007.5799 | 2636721.7606 | 1220997.8366
22 | 2636721.3114 | 1220975.9113 | 2636721.7606 | 1220997.8366
23 | 2636787.2244 | 1220896.8164 | 2636792.0746 | 1220900.0816 | 2636802.2185 | 1220904.8137 | 2636821.6585 | 1220910.5186
24 | 2636760.875 | 1220927.9502 | 2636787.2244 | 1220896.8164
25 | 2636760.875 | 1220927.9502 | 2636738.7535 | 1220927.1244
26 | 2636730.9089 | 1220926.8315 | 2636738.7535 | 1220927.1244
27 | 2636720.5197 | 1220937.2737 | 2636720.5637 | 1220926.4454 | 2636730.9089 | 1220926.8315
28 | 2636720.5197 | 1220937.2737 | 2636710.7133 | 1220936.8687 | 2636702.086 | 1220935.6259
29 | 2636720.5197 | 1220937.2737 | 2636720.9581 | 1220958.6718
30 | 2636689.8319 | 1220933.8606 | 2636702.086 | 1220935.6259
31 | 2636720.9581 | 1220958.6718 | 2636721.3114 | 1220975.9113
32 | 2636612.6992 | 1220944.3705 | 2636612.9691 | 1220938.7244 | 2636614.7461 | 1220928.5515 | 2636620.8275 | 1220928.9891 | 2636626.8134 | 1220928.9258 | 2636656.8498 | 1220927.2538 | 2636665.8285 | 1220927.7982 | 2636681.3517 | 1220932.4409 | 2636689.8319 | 1220933.8606
33 | 2636637.4046 | 1220969.5038 | 2636620.1139 | 1220968.586 | 2636616.255 | 1220966.9391 | 2636613.2292 | 1220963.0738 | 2636612.0386 | 1220958.0524 | 2636612.6992 | 1220944.3705

## bus_geodata
| x | y | coords
0 | 2636796.4604 | 1221150.9261
1 | 2636819.2877 | 1221135.6545
2 | 2636821.5059 | 1221134.1705
3 | 2636843.945 | 1221094.6546
4 | 2636842.4255 | 1221074.1403
5 | 2636819.5661 | 1221077.4064
6 | 2636843.6651 | 1221073.9635
7 | 2636812.5117 | 1221078.4115
8 | 2636740.6414 | 1221144.6926
9 | 2636744.8562 | 1221130.4272
10 | 2636725.0279 | 1221124.0569
11 | 2636745.8599 | 1221126.0212
12 | 2636712.4048 | 1221118.9349
13 | 2636748.17 | 1221092.4918
14 | 2636711.9309 | 1221050.7553
15 | 2636723.6545 | 1221023.1774
16 | 2636732.071 | 1221047.8923
17 | 2636767.1303 | 1221088.2239
18 | 2636797.0308 | 1221081.4934
19 | 2636768.0062 | 1221088.0267
20 | 2636722.5886 | 1221013.3644
21 | 2636722.5639 | 1221013.1368
22 | 2636721.7606 | 1220997.8366
23 | 2636821.6585 | 1220910.5186
24 | 2636787.2244 | 1220896.8164
25 | 2636760.875 | 1220927.9502
26 | 2636738.7535 | 1220927.1244
27 | 2636730.9089 | 1220926.8315
28 | 2636720.5197 | 1220937.2737
29 | 2636702.086 | 1220935.6259
30 | 2636720.9581 | 1220958.6718
31 | 2636689.8319 | 1220933.8606
32 | 2636721.3114 | 1220975.9113
33 | 2636612.6992 | 1220944.3705
34 | 2636637.4046 | 1220969.5038
35 | 2636744.8562 | 1221130.4272

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98848 | -0.080799 | 0.012126 | 0.003039
1 | 0.98896 | -0.077398 | 0.0062002 | 0.0015539
2 | 0.98903 | -0.076899 | 0.011765 | 0.0029486
3 | 0.99105 | -0.062675 | 0.0083113 | 0.002083
4 | 0.99219 | -0.054619 | 0 | 0
5 | 0.99367 | -0.044249 | 0.0022824 | 0.00057203
6 | 0.99218 | -0.054694 | 0.005951 | 0.0014915
7 | 0.99415 | -0.04089 | 0.0022824 | 0.00057203
8 | 0.99701 | -0.020924 | 0.0042799 | 0.0010727
9 | 0.9971 | -0.020284 | 0 | 0
10 | 0.99571 | -0.029989 | 0 | 0
11 | 0.99742 | -0.017996 | 0.0025508 | 0.0006393
12 | 0.99481 | -0.036327 | 0.04618 | 0.011574
13 | 1 | 0 | -0.23541 | -0.059026
14 | 0.99083 | -0.064149 | 0.0044745 | 0.0011214
15 | 0.99103 | -0.062786 | 0 | 0
16 | 0.99309 | -0.048253 | 0.046175 | 0.011572
17 | 0.9978 | -0.015331 | 0.0043243 | 0.0010838
18 | 0.99526 | -0.033094 | 0.0082288 | 0.0020623
19 | 0.9977 | -0.016001 | 0.017375 | 0.0043547
20 | 0.99031 | -0.067843 | 0.0032733 | 0.00082036
21 | 0.99029 | -0.067953 | 0.011443 | 0.002868
22 | 0.98951 | -0.073523 | 0.0087164 | 0.0021845
23 | 0.98624 | -0.096688 | 0.0023275 | 0.00058332
24 | 0.98636 | -0.095797 | 0 | 0
25 | 0.9865 | -0.094821 | 0.0073499 | 0.0018421
26 | 0.98681 | -0.092622 | 0.0016779 | 0.00042053
27 | 0.98694 | -0.091708 | 0 | 0
28 | 0.98728 | -0.089242 | 0 | 0
29 | 0.98695 | -0.091587 | 0.00248 | 0.00062154
30 | 0.98802 | -0.084047 | 0.0017862 | 0.00044766
31 | 0.98678 | -0.09284 | 0 | 0
32 | 0.98865 | -0.079552 | 0.0014319 | 0.00035888
33 | 0.98546 | -0.10215 | 0 | 0
34 | 0.98482 | -0.10674 | 0.0098604 | 0.0024713
35 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.012126 | -0.003039 | 0.012131 | 0.0030409 | 5.7102e-06 | 1.844e-06 | 0.018254 | 0.018253 | 0.018254 | 0.98848 | -0.080799 | 0.98896 | -0.077398 | 6.7606
1 | -0.018332 | -0.0045948 | 0.018333 | 0.0045952 | 1.267e-06 | 4.5305e-07 | 0.027582 | 0.027582 | 0.027582 | 0.98896 | -0.077398 | 0.98903 | -0.076899 | 10.2157
2 | -0.030098 | -0.0075438 | 0.030157 | 0.007566 | 5.9391e-05 | 2.2246e-05 | 0.045283 | 0.045283 | 0.045283 | 0.98903 | -0.076899 | 0.99105 | -0.062675 | 16.7714
3 | -0.038469 | -0.009649 | 0.038512 | 0.0096653 | 4.3022e-05 | 1.628e-05 | 0.057762 | 0.057762 | 0.057762 | 0.99105 | -0.062675 | 0.99219 | -0.054619 | 21.3932
4 | -0.044463 | -0.011157 | 0.044527 | 0.011181 | 6.4079e-05 | 2.4347e-05 | 0.066687 | 0.066686 | 0.066687 | 0.99219 | -0.054619 | 0.99367 | -0.044249 | 24.6987
5 | 0.005951 | 0.0014915 | -0.005951 | -0.0014915 | 6.2235e-08 | 7.7655e-09 | 0.0089249 | 0.0089249 | 0.0089249 | 0.99219 | -0.054619 | 0.99218 | -0.054694 | 3.3055
6 | -0.046809 | -0.011753 | 0.046831 | 0.011761 | 2.1852e-05 | 8.3124e-06 | 0.070104 | 0.070104 | 0.070104 | 0.99367 | -0.044249 | 0.99415 | -0.04089 | 25.9646
7 | -0.049113 | -0.012333 | 0.049167 | 0.012354 | 5.3276e-05 | 2.0286e-05 | 0.073521 | 0.073521 | 0.073521 | 0.99415 | -0.04089 | 0.99526 | -0.033094 | 27.2298
8 | -0.0042799 | -0.0010727 | 0.0042803 | 0.0010726 | 3.7879e-07 | -4.8343e-08 | 0.0063877 | 0.0063877 | 0.0063877 | 0.99701 | -0.020924 | 0.9971 | -0.020284 | 2.3658
9 | 0.046283 | 0.011613 | -0.046221 | -0.011589 | 6.2238e-05 | 2.3665e-05 | 0.069075 | 0.069075 | 0.069075 | 0.9971 | -0.020284 | 0.99571 | -0.029989 | 25.5834
10 | -0.050563 | -0.012686 | 0.050579 | 0.012692 | 1.6058e-05 | 6.1171e-06 | 0.075463 | 0.075463 | 0.075463 | 0.9971 | -0.020284 | 0.99742 | -0.017996 | 27.9491
11 | 0.046221 | 0.011589 | -0.04618 | -0.011574 | 4.0559e-05 | 1.5423e-05 | 0.069075 | 0.069075 | 0.069075 | 0.99571 | -0.029989 | 0.99481 | -0.036327 | 25.5834
12 | -0.05313 | -0.013331 | 0.053263 | 0.013382 | 0.000133 | 5.0711e-05 | 0.079268 | 0.079268 | 0.079268 | 0.99742 | -0.017996 | 1 | 0 | 29.3586
13 | 0.10194 | 0.02567 | -0.10126 | -0.025408 | 0.00068271 | 0.00026196 | 0.15174 | 0.15174 | 0.15174 | 1 | 0 | 0.99309 | -0.048253 | 56.1986
14 | 0.079408 | 0.019974 | -0.079239 | -0.019909 | 0.00016939 | 6.4897e-05 | 0.11819 | 0.11819 | 0.11819 | 1 | 0 | 0.9978 | -0.015331 | 43.7728
15 | -0.0044745 | -0.0011214 | 0.0044753 | 0.0011214 | 8.4449e-07 | -6.131e-08 | 0.0067197 | 0.0067196 | 0.0067197 | 0.99083 | -0.064149 | 0.99103 | -0.062786 | 2.4888
16 | 0.0505 | 0.012672 | -0.050464 | -0.012659 | 3.5417e-05 | 1.3495e-05 | 0.07583 | 0.07583 | 0.07583 | 0.99103 | -0.062786 | 0.99031 | -0.067843 | 28.0853
17 | -0.054975 | -0.013793 | 0.055086 | 0.013836 | 0.00011108 | 4.2386e-05 | 0.08255 | 0.08255 | 0.08255 | 0.99103 | -0.062786 | 0.99309 | -0.048253 | 30.574
18 | 0.074915 | 0.018826 | -0.074908 | -0.018823 | 6.9947e-06 | 2.6786e-06 | 0.11174 | 0.11174 | 0.11174 | 0.9978 | -0.015331 | 0.9977 | -0.016001 | 41.3843
19 | -0.057395 | -0.014416 | 0.057532 | 0.014468 | 0.00013674 | 5.2205e-05 | 0.085823 | 0.085823 | 0.085823 | 0.99526 | -0.033094 | 0.9977 | -0.016001 | 31.7864
20 | 0.047191 | 0.011838 | -0.04719 | -0.011838 | 7.1838e-07 | 2.7335e-07 | 0.070912 | 0.070912 | 0.070912 | 0.99031 | -0.067843 | 0.99029 | -0.067953 | 26.2637
21 | 0.035747 | 0.0089699 | -0.035719 | -0.0089595 | 2.7612e-05 | 1.0423e-05 | 0.053717 | 0.053717 | 0.053717 | 0.99029 | -0.067953 | 0.98951 | -0.073523 | 19.8953
22 | 0.027003 | 0.0067749 | -0.02698 | -0.0067666 | 2.2567e-05 | 8.3983e-06 | 0.04061 | 0.04061 | 0.04061 | 0.98951 | -0.073523 | 0.98865 | -0.079552 | 15.0406
23 | -0.0023275 | -0.00058332 | 0.0023277 | 0.00058295 | 2.8701e-07 | -3.6565e-07 | 0.0035116 | 0.0035115 | 0.0035116 | 0.98624 | -0.096688 | 0.98636 | -0.095797 | 1.3006
24 | -0.0023277 | -0.00058295 | 0.0023281 | 0.00058255 | 3.1381e-07 | -3.9998e-07 | 0.0035115 | 0.0035113 | 0.0035115 | 0.98636 | -0.095797 | 0.9865 | -0.094821 | 1.3005
25 | -0.0096779 | -0.0024246 | 0.0096809 | 0.0024255 | 2.9435e-06 | 8.494e-07 | 0.014598 | 0.014598 | 0.014598 | 0.9865 | -0.094821 | 0.98681 | -0.092622 | 5.4066
26 | -0.011359 | -0.002846 | 0.01136 | 0.0028464 | 1.437e-06 | 4.524e-07 | 0.017128 | 0.017128 | 0.017128 | 0.98681 | -0.092622 | 0.98694 | -0.091708 | 6.3436
27 | -0.01136 | -0.0028464 | 0.011364 | 0.0028477 | 3.8773e-06 | 1.2205e-06 | 0.017128 | 0.017128 | 0.017128 | 0.98694 | -0.091708 | 0.98728 | -0.089242 | 6.3436
28 | 0.012365 | 0.0031002 | -0.012361 | -0.0030989 | 4.0164e-06 | 1.3079e-06 | 0.018637 | 0.018637 | 0.018637 | 0.98728 | -0.089242 | 0.98695 | -0.091587 | 6.9026
29 | -0.023729 | -0.0059478 | 0.023746 | 0.0059541 | 1.7083e-05 | 6.2963e-06 | 0.035765 | 0.035764 | 0.035765 | 0.98728 | -0.089242 | 0.98802 | -0.084047 | 13.2461
30 | 0.0098811 | 0.0024773 | -0.0098794 | -0.0024768 | 1.7147e-06 | 5.013e-07 | 0.014898 | 0.014898 | 0.014898 | 0.98695 | -0.091587 | 0.98678 | -0.09284 | 5.5178
31 | -0.025533 | -0.0064018 | 0.025548 | 0.0064077 | 1.5911e-05 | 5.8986e-06 | 0.038455 | 0.038454 | 0.038455 | 0.98802 | -0.084047 | 0.98865 | -0.079552 | 14.2424
32 | 0.0098794 | 0.0024768 | -0.0098667 | -0.0024731 | 1.2734e-05 | 3.7247e-06 | 0.014898 | 0.014898 | 0.014898 | 0.98678 | -0.09284 | 0.98546 | -0.10215 | 5.5179
33 | 0.0098667 | 0.0024731 | -0.0098604 | -0.0024713 | 6.2626e-06 | 1.833e-06 | 0.014898 | 0.014899 | 0.014899 | 0.98546 | -0.10215 | 0.98482 | -0.10674 | 5.518

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.23541 | 0.059026

## res_load
| p_mw | q_mvar
0 | 0.012126 | 0.003039
1 | 0.0062002 | 0.0015539
2 | 0.011765 | 0.0029486
3 | 0.0083113 | 0.002083
4 | 0.0022824 | 0.00057203
5 | 0.005951 | 0.0014915
6 | 0.0022824 | 0.00057203
7 | 0.0042799 | 0.0010727
8 | 0.0025508 | 0.0006393
9 | 0.04618 | 0.011574
10 | 0.0044745 | 0.0011214
11 | 0.046175 | 0.011572
12 | 0.0043243 | 0.0010838
13 | 0.0082288 | 0.0020623
14 | 0.017375 | 0.0043547
15 | 0.0032733 | 0.00082036
16 | 0.011443 | 0.002868
17 | 0.0087164 | 0.0021845
18 | 0.0023275 | 0.00058332
19 | 0.0073499 | 0.0018421
20 | 0.0016779 | 0.00042053
21 | 0.00248 | 0.00062154
22 | 0.0017862 | 0.00044766
23 | 0.0014319 | 0.00035888
24 | 0.0098604 | 0.0024713

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1