## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1151-30_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1151-30_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1151-30_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1151-30_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1151-30_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1151-30_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1151-30_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_1151-30_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_1151-30_0_3_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_1151-30_0_3_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1151-30_0_3_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1151-30_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_1151-30_0_3_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1151-30_0_3_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_1151-30_0_3_node_48 | 0.4 | n |  | TRUE
15 | bus_LV_1151-30_0_3_node_22 | 0.4 | n |  | TRUE
16 | bus_LV_1151-30_0_3_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_1151-30_0_3_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_1151-30_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_1151-30_0_3_node_31 | 0.4 | n |  | TRUE
20 | bus_LV_1151-30_0_3_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_1151-30_0_3_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1151-30_0_3_node_36 | 0.4 | n |  | TRUE
23 | bus_LV_1151-30_0_3_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_1151-30_0_3_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_1151-30_0_3_node_49 | 0.4 | n |  | TRUE
26 | bus_LV_1151-30_0_3_node_43 | 0.4 | n |  | TRUE
27 | bus_LV_1151-30_0_3_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_1151-30_0_3_node_46 | 0.4 | n |  | TRUE
29 | bus_LV_1151-30_0_3_node_47 | 0.4 | n |  | TRUE
30 | bus_LV_1151-30_0_3_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_1151-30_0_3_node_42 | 0.4 | n |  | TRUE
32 | bus_LV_1151-30_0_3_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_1151-30_0_3_node_24 | 0.4 | n |  | TRUE
34 | bus_LV_1151-30_0_3_node_25 | 0.4 | n |  | TRUE
35 | bus_LV_1151-30_0_3_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_1151-30_0_3_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_1151-30_0_3_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_1151-30_0_3_node_30 | 0.4 | n |  | TRUE
39 | bus_LV_1151-30_0_3_node_44 | 0.4 | n |  | TRUE
40 | bus_LV_1151-30_0_3_node_41 | 0.4 | n |  | TRUE
41 | bus_LV_1151-30_0_3_node_34 | 0.4 | n |  | TRUE
42 | bus_LV_1151-30_0_3_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_1151-30_0_3_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_1151-30_0_3_node_39 | 0.4 | n |  | TRUE
45 | bus_MV_128_0_node_171 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1151-30_0_3_load_0 | 0 | 0.012717 | 0.0031871 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1151-30_0_3_load_1 | 1 | 0.0046216 | 0.0011583 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1151-30_0_3_load_2 | 2 | 0.0030471 | 0.00076367 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1151-30_0_3_load_4 | 4 | 0.0084213 | 0.0021106 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1151-30_0_3_load_5 | 5 | 0.0019526 | 0.00048938 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1151-30_0_3_load_6 | 6 | 0.0023762 | 0.00059553 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1151-30_0_3_load_9 | 8 | 0.016511 | 0.0041379 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1151-30_0_3_load_8 | 11 | 0.019579 | 0.0049071 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1151-30_0_3_load_48 | 14 | 0.0083538 | 0.0020937 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1151-30_0_3_load_22 | 15 | 0.0021786 | 0.00054601 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1151-30_0_3_load_23 | 16 | 0.0043796 | 0.0010976 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1151-30_0_3_load_21 | 17 | 0.0054697 | 0.0013708 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1151-30_0_3_load_31 | 19 | 0.0013594 | 0.00034069 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1151-30_0_3_load_45 | 20 | 0.0057637 | 0.0014445 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1151-30_0_3_load_36 | 22 | 0.008874 | 0.002224 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1151-30_0_3_load_33 | 23 | 0.0032621 | 0.00081756 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1151-30_0_3_load_18 | 24 | 0.017596 | 0.0044099 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1151-30_0_3_load_49 | 25 | 0.003273 | 0.00082029 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1151-30_0_3_load_29 | 27 | 0.0051808 | 0.0012984 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1151-30_0_3_load_46 | 28 | 0.0053645 | 0.0013445 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1151-30_0_3_load_47 | 29 | 0.001956 | 0.00049022 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1151-30_0_3_load_32 | 30 | 0.0050283 | 0.0012602 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1151-30_0_3_load_42 | 31 | 0.0043884 | 0.0010998 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1151-30_0_3_load_38 | 32 | 0.0031871 | 0.00079877 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1151-30_0_3_load_24 | 33 | 0.0061011 | 0.0015291 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1151-30_0_3_load_26 | 35 | 0.0040026 | 0.0010031 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1151-30_0_3_load_27 | 36 | 0.0032309 | 0.00080975 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1151-30_0_3_load_28 | 37 | 0.0036498 | 0.00091473 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1151-30_0_3_load_30 | 38 | 0.0046355 | 0.0011618 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1151-30_0_3_load_44 | 39 | 0.0093157 | 0.0023347 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1151-30_0_3_load_41 | 40 | 0.0035581 | 0.00089173 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1151-30_0_3_load_34 | 41 | 0.0033169 | 0.00083129 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1151-30_0_3_load_35 | 42 | 0.003141 | 0.00078722 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1151-30_0_3_load_37 | 43 | 0.0066768 | 0.0016734 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1151-30_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.022925 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1151-30_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.017541 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1151-30_0_3_line_2 | NAYY 4x150 SE | 1 | 3 | 0.023114 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1151-30_0_3_line_3 | NAYY 4x150 SE | 2 | 4 | 0.0092138 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1151-30_0_3_line_4 | NAYY 4x150 SE | 3 | 5 | 0.0098164 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1151-30_0_3_line_5 | NAYY 4x150 SE | 3 | 6 | 0.013452 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1151-30_0_3_line_6 | NAYY 4x150 SE | 4 | 7 | 0.023789 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1151-30_0_3_line_7 | NAYY 4x150 SE | 5 | 8 | 0.0070627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1151-30_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.023813 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1151-30_0_3_line_9 | NAYY 4x150 SE | 7 | 10 | 0.055564 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1151-30_0_3_line_10 | NAYY 4x150 SE | 8 | 11 | 0.036803 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1151-30_0_3_line_11 | NAYY 4x150 SE | 9 | 15 | 0.021398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1151-30_0_3_line_12 | NAYY 4x150 SE | 9 | 16 | 0.015308 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1151-30_0_3_line_13 | NAYY 4x150 SE | 9 | 17 | 0.021235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1151-30_0_3_line_14 | NAYY 4x150 SE | 10 | 24 | 0.029732 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1151-30_0_3_line_15 | NAYY 4x150 SE | 12 | 13 | 0.025561 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1151-30_0_3_line_16 | NAYY 4x150 SE | 12 | 14 | 0.017398 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1151-30_0_3_line_17 | NAYY 4x150 SE | 13 | 31 | 0.021024 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1151-30_0_3_line_18 | NAYY 4x150 SE | 13 | 32 | 0.021416 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1151-30_0_3_line_19 | NAYY 4x150 SE | 14 | 26 | 0.026196 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1151-30_0_3_line_20 | NAYY 4x150 SE | 15 | 33 | 0.015832 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
21 | LV_1151-30_0_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.041422 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1151-30_0_3_line_22 | NAYY 4x150 SE | 18 | 20 | 0.022633 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1151-30_0_3_line_23 | NAYY 4x150 SE | 19 | 27 | 0.024975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1151-30_0_3_line_24 | NAYY 4x150 SE | 20 | 28 | 0.03679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1151-30_0_3_line_25 | NAYY 4x150 SE | 21 | 22 | 0.014215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1151-30_0_3_line_26 | NAYY 4x150 SE | 21 | 23 | 0.018239 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1151-30_0_3_line_27 | NAYY 4x150 SE | 22 | 29 | 0.00070104 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1151-30_0_3_line_28 | NAYY 4x150 SE | 23 | 30 | 0.0046174 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1151-30_0_3_line_29 | NAYY 4x150 SE | 25 | 26 | 0.013724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1151-30_0_3_line_30 | NAYY 4x150 SE | 28 | 29 | 0.026236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1151-30_0_3_line_31 | NAYY 4x150 SE | 30 | 41 | 0.0030533 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1151-30_0_3_line_32 | NAYY 4x150 SE | 32 | 44 | 0.011033 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1151-30_0_3_line_33 | NAYY 4x150 SE | 33 | 34 | 0.018797 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1151-30_0_3_line_34 | NAYY 4x150 SE | 34 | 35 | 0.028953 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1151-30_0_3_line_35 | NAYY 4x150 SE | 34 | 36 | 0.012975 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
36 | LV_1151-30_0_3_line_36 | NAYY 4x150 SE | 34 | 37 | 0.051344 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
37 | LV_1151-30_0_3_line_37 | NAYY 4x150 SE | 36 | 38 | 0.007053 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
38 | LV_1151-30_0_3_line_38 | NAYY 4x150 SE | 38 | 39 | 0.016144 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
39 | LV_1151-30_0_3_line_39 | NAYY 4x150 SE | 39 | 40 | 0.0038192 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
40 | LV_1151-30_0_3_line_40 | NAYY 4x150 SE | 40 | 44 | 0.022761 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
41 | LV_1151-30_0_3_line_41 | NAYY 4x150 SE | 41 | 42 | 0.0049025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
42 | LV_1151-30_0_3_line_42 | NAYY 4x150 SE | 42 | 43 | 0.036542 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1151-30_0_3_line_43 | NAYY 4x150 SE | 43 | 44 | 0.017777 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1151-30_0_3_trafo_22 | 0.25 MVA 20/0.4 kV | 45 | 15 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2642285.0497 | 1219049.6428 | 2642290.1142 | 1219049.3945 | 2642300.6219 | 1219055.1057 | 2642306.4415 | 1219054.1687 | 2642306.4415 | 1219054.1687
1 | 2642285.0497 | 1219049.6428 | 2642267.53 | 1219050.5017 | 2642267.53 | 1219050.5017
2 | 2642313.8878 | 1219073.1551 | 2642310.9972 | 1219054.8792 | 2642306.4415 | 1219054.1687
3 | 2642266.2981 | 1219041.3706 | 2642267.53 | 1219050.5017
4 | 2642313.8878 | 1219073.1551 | 2642308.1635 | 1219074.5708 | 2642305.8012 | 1219077.6987
5 | 2642313.8878 | 1219073.1551 | 2642327.2428 | 1219071.5398
6 | 2642263.1177 | 1219017.7954 | 2642266.2981 | 1219041.3706
7 | 2642301.5447 | 1219083.3346 | 2642305.8012 | 1219077.6987
8 | 2642263.1177 | 1219017.7954 | 2642282.9369 | 1219014.9342 | 2642282.5843 | 1219011.1627
9 | 2642221.0096 | 1219035.7522 | 2642221.1982 | 1219027.3486 | 2642221.2644 | 1219022.2905 | 2642229.8366 | 1219021.6508 | 2642263.1177 | 1219017.7954
10 | 2642279.3648 | 1219112.7026 | 2642301.5447 | 1219083.3346
11 | 2642282.5843 | 1219011.1627 | 2642280.5772 | 1218989.8593
12 | 2642282.5843 | 1219011.1627 | 2642297.6307 | 1219008.3435
13 | 2642282.5843 | 1219011.1627 | 2642269.767 | 1219013.2843 | 2642261.5738 | 1219014.1947
14 | 2642221.0096 | 1219035.7522 | 2642221.0617 | 1219038.0428 | 2642221.2355 | 1219062.781 | 2642221.2391 | 1219065.4827
15 | 2642281.346 | 1218835.9163 | 2642281.0448 | 1218852.7019 | 2642280.8687 | 1218861.4725
16 | 2642281.346 | 1218835.9163 | 2642263.9659 | 1218835.1318
17 | 2642280.8687 | 1218861.4725 | 2642301.884 | 1218862.0913
18 | 2642280.8687 | 1218861.4725 | 2642280.4564 | 1218882.8843
19 | 2642241.2664 | 1218838.3782 | 2642242.8265 | 1218838.845 | 2642244.2327 | 1218834.2411 | 2642263.9659 | 1218835.1318
20 | 2642280.1653 | 1218974.0332 | 2642280.5729 | 1218989.8135 | 2642280.5772 | 1218989.8593
21 | 2642125.253 | 1218954.4933 | 2642137.9064 | 1218962.6765 | 2642141.1613 | 1218963.8557 | 2642144.2706 | 1218964.1445 | 2642149.8416 | 1218964.0394 | 2642164.0299 | 1218963.5626
22 | 2642125.253 | 1218954.4933 | 2642141.1055 | 1218938.339
23 | 2642164.0299 | 1218963.5626 | 2642188.9911 | 1218962.7239
24 | 2642141.1055 | 1218938.339 | 2642166.8735 | 1218912.0804
25 | 2642193.8968 | 1218881.1794 | 2642189.9078 | 1218887.2103 | 2642185.406 | 1218892.5505
26 | 2642193.8968 | 1218881.1794 | 2642199.1897 | 1218883.8962 | 2642210.9327 | 1218887.5204
27 | 2642184.9541 | 1218893.0865 | 2642185.406 | 1218892.5505
28 | 2642215.3447 | 1218888.8821 | 2642210.9327 | 1218887.5204
29 | 2642241.2664 | 1218838.3782 | 2642228.0325 | 1218834.7433
30 | 2642166.8735 | 1218912.0804 | 2642181.5506 | 1218897.1238 | 2642184.9541 | 1218893.0865
31 | 2642215.3447 | 1218888.8821 | 2642218.2622 | 1218889.7825
32 | 2642277.1498 | 1218892.5425 | 2642280.328 | 1218889.5521 | 2642280.4564 | 1218882.8843
33 | 2642279.6799 | 1218955.2422 | 2642280.1653 | 1218974.0332
34 | 2642279.6799 | 1218955.2422 | 2642250.8372 | 1218957.7657
35 | 2642279.6799 | 1218955.2422 | 2642279.4084 | 1218950.7153 | 2642279.1116 | 1218942.2805
36 | 2642279.6799 | 1218955.2422 | 2642299.75 | 1218952.3495 | 2642302.1965 | 1218949.8097 | 2642300.7152 | 1218924.3507 | 2642302.6483 | 1218923.7052
37 | 2642278.8636 | 1218935.2318 | 2642279.1116 | 1218942.2805
38 | 2642278.8636 | 1218935.2318 | 2642278.2958 | 1218919.0973
39 | 2642278.2958 | 1218919.0973 | 2642278.1615 | 1218915.2805
40 | 2642277.1498 | 1218892.5425 | 2642277.779 | 1218904.4095 | 2642278.1615 | 1218915.2805
41 | 2642218.2622 | 1218889.7825 | 2642222.823 | 1218891.1901 | 2642222.9509 | 1218891.2103
42 | 2642259.3731 | 1218892.6207 | 2642232.6396 | 1218892.7383 | 2642222.9509 | 1218891.2103
43 | 2642277.1498 | 1218892.5425 | 2642259.3731 | 1218892.6207

## bus_geodata
| x | y | coords
0 | 2642285.0497 | 1219049.6428
1 | 2642306.4415 | 1219054.1687
2 | 2642267.53 | 1219050.5017
3 | 2642313.8878 | 1219073.1551
4 | 2642266.2981 | 1219041.3706
5 | 2642305.8012 | 1219077.6987
6 | 2642327.2428 | 1219071.5398
7 | 2642263.1177 | 1219017.7954
8 | 2642301.5447 | 1219083.3346
9 | 2642282.5843 | 1219011.1627
10 | 2642221.0096 | 1219035.7522
11 | 2642279.3648 | 1219112.7026
12 | 2642281.346 | 1218835.9163
13 | 2642280.8687 | 1218861.4725
14 | 2642263.9659 | 1218835.1318
15 | 2642280.5772 | 1218989.8593
16 | 2642297.6307 | 1219008.3435
17 | 2642261.5738 | 1219014.1947
18 | 2642125.253 | 1218954.4933
19 | 2642164.0299 | 1218963.5626
20 | 2642141.1055 | 1218938.339
21 | 2642193.8968 | 1218881.1794
22 | 2642185.406 | 1218892.5505
23 | 2642210.9327 | 1218887.5204
24 | 2642221.2392 | 1219065.4827
25 | 2642228.0325 | 1218834.7433
26 | 2642241.2664 | 1218838.3782
27 | 2642188.9911 | 1218962.7239
28 | 2642166.8735 | 1218912.0804
29 | 2642184.9541 | 1218893.0865
30 | 2642215.3447 | 1218888.8821
31 | 2642301.884 | 1218862.0913
32 | 2642280.4564 | 1218882.8843
33 | 2642280.1653 | 1218974.0332
34 | 2642279.6799 | 1218955.2422
35 | 2642250.8372 | 1218957.7657
36 | 2642279.1116 | 1218942.2805
37 | 2642302.6483 | 1218923.7052
38 | 2642278.8636 | 1218935.2318
39 | 2642278.2958 | 1218919.0973
40 | 2642278.1615 | 1218915.2805
41 | 2642218.2622 | 1218889.7825
42 | 2642222.9509 | 1218891.2103
43 | 2642259.3731 | 1218892.6207
44 | 2642277.1498 | 1218892.5425
45 | 2642282.5843 | 1219011.1627

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98938 | -0.074223 | 0.012717 | 0.0031871
1 | 0.98789 | -0.084768 | 0.0046216 | 0.0011583
2 | 0.99085 | -0.063907 | 0.0030471 | 0.00076367
3 | 0.98654 | -0.094337 | 0 | 0
4 | 0.99166 | -0.058215 | 0.0084213 | 0.0021106
5 | 0.986 | -0.098169 | 0.0019526 | 0.00048938
6 | 0.98649 | -0.094665 | 0.0023762 | 0.00059553
7 | 0.99404 | -0.041539 | 0 | 0
8 | 0.98563 | -0.10079 | 0.016511 | 0.0041379
9 | 0.99702 | -0.020713 | 0 | 0
10 | 0.99263 | -0.051431 | 0 | 0
11 | 0.98459 | -0.1082 | 0.019579 | 0.0049071
12 | 0.98778 | -0.085495 | 0 | 0
13 | 0.98821 | -0.082454 | 0 | 0
14 | 0.98749 | -0.087565 | 0.0083538 | 0.0020937
15 | 1 | 0 | -0.20334 | -0.051051
16 | 0.99692 | -0.021386 | 0.0043796 | 0.0010976
17 | 0.99685 | -0.02188 | 0.0054697 | 0.0013708
18 | 0.98187 | -0.12744 | 0 | 0
19 | 0.98147 | -0.13025 | 0.0013594 | 0.00034069
20 | 0.98208 | -0.12591 | 0.0057637 | 0.0014445
21 | 0.98402 | -0.11211 | 0 | 0
22 | 0.98343 | -0.11629 | 0.008874 | 0.002224
23 | 0.98477 | -0.10676 | 0.0032621 | 0.00081756
24 | 0.99188 | -0.056734 | 0.017596 | 0.0044099
25 | 0.9873 | -0.088903 | 0.003273 | 0.00082029
26 | 0.98737 | -0.088443 | 0 | 0
27 | 0.98129 | -0.13159 | 0.0051808 | 0.0012984
28 | 0.98274 | -0.12123 | 0.0053645 | 0.0013445
29 | 0.98341 | -0.11643 | 0.001956 | 0.00049022
30 | 0.98499 | -0.10525 | 0.0050283 | 0.0012602
31 | 0.98808 | -0.083398 | 0.0043884 | 0.0010998
32 | 0.98871 | -0.078948 | 0.0031871 | 0.00079877
33 | 0.99882 | -0.0082001 | 0.0061011 | 0.0015291
34 | 0.99617 | -0.026597 | 0 | 0
35 | 0.996 | -0.027763 | 0.0040026 | 0.0010031
36 | 0.99449 | -0.038349 | 0.0032309 | 0.00080975
37 | 0.9959 | -0.028483 | 0.0036498 | 0.00091473
38 | 0.9936 | -0.044524 | 0.0046355 | 0.0011618
39 | 0.99169 | -0.057939 | 0.0093157 | 0.0023347
40 | 0.99129 | -0.060759 | 0.0035581 | 0.00089173
41 | 0.98515 | -0.10409 | 0.0033169 | 0.00083129
42 | 0.98543 | -0.10207 | 0.003141 | 0.00078722
43 | 0.98773 | -0.085856 | 0.0066768 | 0.0016734
44 | 0.98901 | -0.076785 | 0 | 0
45 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.045214 | 0.011353 | -0.045148 | -0.011328 | 6.6163e-05 | 2.5153e-05 | 0.068009 | 0.068009 | 0.068009 | 0.98938 | -0.074223 | 0.98789 | -0.084768 | 25.1884
1 | -0.057931 | -0.014541 | 0.058014 | 0.014572 | 8.3102e-05 | 3.1737e-05 | 0.087134 | 0.087134 | 0.087134 | 0.98938 | -0.074223 | 0.99085 | -0.063907 | 32.272
2 | 0.040526 | 0.01017 | -0.040472 | -0.01015 | 5.3752e-05 | 2.0378e-05 | 0.061047 | 0.061047 | 0.061047 | 0.98789 | -0.084768 | 0.98654 | -0.094337 | 22.6102
3 | -0.061061 | -0.015336 | 0.061109 | 0.015354 | 4.8357e-05 | 1.848e-05 | 0.09171 | 0.09171 | 0.09171 | 0.99085 | -0.063907 | 0.99166 | -0.058215 | 33.9667
4 | 0.038096 | 0.0095542 | -0.038076 | -0.0095466 | 2.0226e-05 | 7.6541e-06 | 0.057463 | 0.057463 | 0.057463 | 0.98654 | -0.094337 | 0.986 | -0.098169 | 21.2827
5 | 0.0023763 | 0.0005954 | -0.0023762 | -0.00059553 | 1.0783e-07 | -1.3028e-07 | 0.0035841 | 0.0035842 | 0.0035842 | 0.98654 | -0.094337 | 0.98649 | -0.094665 | 1.3275
6 | -0.06953 | -0.017465 | 0.069692 | 0.017527 | 0.00016163 | 6.1857e-05 | 0.10435 | 0.10435 | 0.10435 | 0.99166 | -0.058215 | 0.99404 | -0.041539 | 38.6469
7 | 0.036123 | 0.0090572 | -0.03611 | -0.0090523 | 1.3098e-05 | 4.9477e-06 | 0.054517 | 0.054517 | 0.054517 | 0.986 | -0.098169 | 0.98563 | -0.10079 | 20.1913
8 | -0.087325 | -0.02195 | 0.087579 | 0.022047 | 0.000254 | 9.7382e-05 | 0.13074 | 0.13074 | 0.13074 | 0.99404 | -0.041539 | 0.99702 | -0.020713 | 48.4234
9 | 0.017633 | 0.0044231 | -0.017609 | -0.0044145 | 2.4159e-05 | 8.5727e-06 | 0.026397 | 0.026397 | 0.026397 | 0.99404 | -0.041539 | 0.99263 | -0.051431 | 9.7767
10 | 0.019599 | 0.0049143 | -0.019579 | -0.0049071 | 2.0108e-05 | 7.2652e-06 | 0.02959 | 0.029591 | 0.029591 | 0.98563 | -0.10079 | 0.98459 | -0.1082 | 10.9594
11 | -0.09743 | -0.024516 | 0.097712 | 0.024624 | 0.00028245 | 0.00010836 | 0.14544 | 0.14544 | 0.14544 | 0.99702 | -0.020713 | 1 | 0 | 53.8684
12 | 0.00438 | 0.0010976 | -0.0043796 | -0.0010976 | 4.082e-07 | -4.2619e-08 | 0.006537 | 0.0065371 | 0.0065371 | 0.99702 | -0.020713 | 0.99692 | -0.021386 | 2.4211
13 | 0.0054706 | 0.0013709 | -0.0054697 | -0.0013708 | 8.8332e-07 | 6.2853e-08 | 0.0081646 | 0.0081647 | 0.0081647 | 0.99702 | -0.020713 | 0.99685 | -0.02188 | 3.024
14 | 0.017609 | 0.0044145 | -0.017596 | -0.0044099 | 1.2928e-05 | 4.5881e-06 | 0.026397 | 0.026397 | 0.026397 | 0.99263 | -0.051431 | 0.99188 | -0.056734 | 9.7767
15 | -0.011631 | -0.0029147 | 0.011636 | 0.0029163 | 4.8962e-06 | 1.5558e-06 | 0.017521 | 0.017521 | 0.017521 | 0.98778 | -0.085495 | 0.98821 | -0.082454 | 6.4892
16 | 0.011631 | 0.0029147 | -0.011627 | -0.0029137 | 3.3326e-06 | 1.0591e-06 | 0.017521 | 0.017521 | 0.017521 | 0.98778 | -0.085495 | 0.98749 | -0.087565 | 6.4892
17 | 0.004389 | 0.0010998 | -0.0043884 | -0.0010998 | 5.7299e-07 | -4.8941e-08 | 0.0066087 | 0.0066088 | 0.0066088 | 0.98821 | -0.082454 | 0.98808 | -0.083398 | 2.4477
18 | -0.016025 | -0.0040161 | 0.016032 | 0.0040188 | 7.7805e-06 | 2.718e-06 | 0.024129 | 0.024129 | 0.024129 | 0.98821 | -0.082454 | 0.98871 | -0.078948 | 8.9368
19 | 0.0032736 | 0.00082001 | -0.0032732 | -0.00082019 | 3.9774e-07 | -1.8211e-07 | 0.0049327 | 0.0049328 | 0.0049328 | 0.98749 | -0.087565 | 0.98737 | -0.088443 | 1.827
20 | 0.10483 | 0.026426 | -0.10471 | -0.026381 | 0.00012027 | 4.5841e-05 | 0.15604 | 0.15604 | 0.15604 | 1 | 0 | 0.99882 | -0.0082001 | 28.896
21 | 0.0065437 | 0.0016396 | -0.0065412 | -0.0016392 | 2.542e-06 | 4.5399e-07 | 0.0099168 | 0.009917 | 0.009917 | 0.98187 | -0.12744 | 0.98147 | -0.13025 | 3.673
22 | -0.0065437 | -0.0016396 | 0.0065451 | 0.0016399 | 1.3889e-06 | 2.4787e-07 | 0.0099168 | 0.0099167 | 0.0099168 | 0.98187 | -0.12744 | 0.98208 | -0.12591 | 3.6729
23 | 0.0051818 | 0.0012985 | -0.0051808 | -0.0012984 | 9.6186e-07 | 5.4376e-08 | 0.0078561 | 0.0078562 | 0.0078562 | 0.98147 | -0.13025 | 0.98129 | -0.13159 | 2.9097
24 | -0.012309 | -0.0030844 | 0.012317 | 0.003087 | 7.9846e-06 | 2.6052e-06 | 0.01865 | 0.018649 | 0.01865 | 0.98208 | -0.12591 | 0.98274 | -0.12123 | 6.9073
25 | 0.02854 | 0.0071562 | -0.028523 | -0.0071501 | 1.6523e-05 | 6.1744e-06 | 0.043159 | 0.043159 | 0.043159 | 0.98402 | -0.11211 | 0.98343 | -0.11629 | 15.9848
26 | -0.02854 | -0.0071562 | 0.028561 | 0.0071642 | 2.1199e-05 | 7.9217e-06 | 0.043159 | 0.043159 | 0.043159 | 0.98402 | -0.11211 | 0.98477 | -0.10676 | 15.9847
27 | 0.019649 | 0.004926 | -0.019649 | -0.0049259 | 3.8669e-07 | 1.3983e-07 | 0.029732 | 0.029732 | 0.029732 | 0.98343 | -0.11629 | 0.98341 | -0.11643 | 11.0117
28 | -0.031823 | -0.0079817 | 0.03183 | 0.0079842 | 6.6627e-06 | 2.5038e-06 | 0.048088 | 0.048088 | 0.048088 | 0.98477 | -0.10676 | 0.98499 | -0.10525 | 17.8103
29 | -0.003273 | -0.00082029 | 0.0032732 | 0.00082019 | 2.0838e-07 | -9.537e-08 | 0.0049329 | 0.0049328 | 0.0049329 | 0.9873 | -0.088903 | 0.98737 | -0.088443 | 1.827
30 | -0.017681 | -0.0044315 | 0.017693 | 0.0044357 | 1.1734e-05 | 4.1804e-06 | 0.026772 | 0.026772 | 0.026772 | 0.98274 | -0.12123 | 0.98341 | -0.11643 | 9.9156
31 | -0.036858 | -0.0092444 | 0.036864 | 0.0092467 | 5.9076e-06 | 2.2333e-06 | 0.055684 | 0.055684 | 0.055684 | 0.98499 | -0.10525 | 0.98515 | -0.10409 | 20.6237
32 | -0.01922 | -0.0048176 | 0.019225 | 0.0048197 | 5.7603e-06 | 2.074e-06 | 0.028926 | 0.028926 | 0.028926 | 0.98871 | -0.078948 | 0.98901 | -0.076785 | 10.7133
33 | 0.098605 | 0.024851 | -0.098352 | -0.024754 | 0.00025329 | 9.7173e-05 | 0.14695 | 0.14695 | 0.14695 | 0.99882 | -0.0082001 | 0.99617 | -0.026597 | 54.4256
34 | 0.0040032 | 0.001003 | -0.0040026 | -0.0010031 | 6.4601e-07 | -1.2841e-07 | 0.0059797 | 0.0059798 | 0.0059798 | 0.99617 | -0.026597 | 0.996 | -0.027763 | 2.2147
35 | 0.090698 | 0.022837 | -0.090549 | -0.02278 | 0.00014869 | 5.7019e-05 | 0.13552 | 0.13552 | 0.13552 | 0.99617 | -0.026597 | 0.99449 | -0.038349 | 50.1913
36 | 0.0036508 | 0.00091442 | -0.0036498 | -0.00091473 | 9.5274e-07 | -3.0183e-07 | 0.0054531 | 0.0054533 | 0.0054533 | 0.99617 | -0.026597 | 0.9959 | -0.028483 | 2.0197
37 | 0.087319 | 0.02197 | -0.087243 | -0.021941 | 7.5161e-05 | 2.8816e-05 | 0.13068 | 0.13068 | 0.13068 | 0.99449 | -0.038349 | 0.9936 | -0.044524 | 48.4008
38 | 0.082608 | 0.020779 | -0.082454 | -0.02072 | 0.00015425 | 5.9119e-05 | 0.12374 | 0.12374 | 0.12374 | 0.9936 | -0.044524 | 0.99169 | -0.057939 | 45.8297
39 | 0.073138 | 0.018386 | -0.073109 | -0.018375 | 2.8712e-05 | 1.0994e-05 | 0.10976 | 0.10976 | 0.10976 | 0.99169 | -0.057939 | 0.99129 | -0.060759 | 40.6527
40 | 0.069551 | 0.017483 | -0.069396 | -0.017424 | 0.00015487 | 5.9272e-05 | 0.10442 | 0.10442 | 0.10442 | 0.99129 | -0.060759 | 0.98901 | -0.076785 | 38.6746
41 | -0.040181 | -0.010078 | 0.040192 | 0.010082 | 1.1269e-05 | 4.2719e-06 | 0.060694 | 0.060694 | 0.060694 | 0.98515 | -0.10409 | 0.98543 | -0.10207 | 22.4793
42 | -0.043333 | -0.010869 | 0.043431 | 0.010907 | 9.7639e-05 | 3.7087e-05 | 0.065437 | 0.065437 | 0.065437 | 0.98543 | -0.10207 | 0.98773 | -0.085856 | 24.2359
43 | -0.050108 | -0.01258 | 0.050171 | 0.012604 | 6.3224e-05 | 2.4089e-05 | 0.075495 | 0.075495 | 0.075495 | 0.98773 | -0.085856 | 0.98901 | -0.076785 | 27.9613

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.20552 | 0.051597

## res_load
| p_mw | q_mvar
0 | 0.012717 | 0.0031871
1 | 0.0046216 | 0.0011583
2 | 0.0030471 | 0.00076367
3 | 0.0084213 | 0.0021106
4 | 0.0019526 | 0.00048938
5 | 0.0023762 | 0.00059553
6 | 0.016511 | 0.0041379
7 | 0.019579 | 0.0049071
8 | 0.0083538 | 0.0020937
9 | 0.0021786 | 0.00054601
10 | 0.0043796 | 0.0010976
11 | 0.0054697 | 0.0013708
12 | 0.0013594 | 0.00034069
13 | 0.0057637 | 0.0014445
14 | 0.008874 | 0.002224
15 | 0.0032621 | 0.00081756
16 | 0.017596 | 0.0044099
17 | 0.003273 | 0.00082029
18 | 0.0051808 | 0.0012984
19 | 0.0053645 | 0.0013445
20 | 0.001956 | 0.00049022
21 | 0.0050283 | 0.0012602
22 | 0.0043884 | 0.0010998
23 | 0.0031871 | 0.00079877
24 | 0.0061011 | 0.0015291
25 | 0.0040026 | 0.0010031
26 | 0.0032309 | 0.00080975
27 | 0.0036498 | 0.00091473
28 | 0.0046355 | 0.0011618
29 | 0.0093157 | 0.0023347
30 | 0.0035581 | 0.00089173
31 | 0.0033169 | 0.00083129
32 | 0.003141 | 0.00078722
33 | 0.0066768 | 0.0016734

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1