## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1151-36_2_4_node_145 | 0.4 | n |  | TRUE
1 | bus_LV_1151-36_2_4_node_146 | 0.4 | n |  | TRUE
2 | bus_LV_1151-36_2_4_node_147 | 0.4 | n |  | TRUE
3 | bus_LV_1151-36_2_4_node_157 | 0.4 | n |  | TRUE
4 | bus_LV_1151-36_2_4_node_156 | 0.4 | n |  | TRUE
5 | bus_LV_1151-36_2_4_node_105 | 0.4 | n |  | TRUE
6 | bus_LV_1151-36_2_4_node_158 | 0.4 | n |  | TRUE
7 | bus_LV_1151-36_2_4_node_159 | 0.4 | n |  | TRUE
8 | bus_LV_1151-36_2_4_node_104 | 0.4 | n |  | TRUE
9 | bus_LV_1151-36_2_4_node_163 | 0.4 | n |  | TRUE
10 | bus_LV_1151-36_2_4_node_164 | 0.4 | n |  | TRUE
11 | bus_LV_1151-36_2_4_node_113 | 0.4 | n |  | TRUE
12 | bus_LV_1151-36_2_4_node_168 | 0.4 | n |  | TRUE
13 | bus_LV_1151-36_2_4_node_169 | 0.4 | n |  | TRUE
14 | bus_LV_1151-36_2_4_node_170 | 0.4 | n |  | TRUE
15 | bus_LV_1151-36_2_4_node_171 | 0.4 | n |  | TRUE
16 | bus_LV_1151-36_2_4_node_192 | 0.4 | n |  | TRUE
17 | bus_LV_1151-36_2_4_node_175 | 0.4 | n |  | TRUE
18 | bus_LV_1151-36_2_4_node_172 | 0.4 | n |  | TRUE
19 | bus_LV_1151-36_2_4_node_173 | 0.4 | n |  | TRUE
20 | bus_LV_1151-36_2_4_node_174 | 0.4 | n |  | TRUE
21 | bus_LV_1151-36_2_4_node_96 | 0.4 | n |  | TRUE
22 | bus_LV_1151-36_2_4_node_183 | 0.4 | n |  | TRUE
23 | bus_LV_1151-36_2_4_node_184 | 0.4 | n |  | TRUE
24 | bus_LV_1151-36_2_4_node_185 | 0.4 | n |  | TRUE
25 | bus_LV_1151-36_2_4_node_186 | 0.4 | n |  | TRUE
26 | bus_LV_1151-36_2_4_node_187 | 0.4 | n |  | TRUE
27 | bus_LV_1151-36_2_4_node_188 | 0.4 | n |  | TRUE
28 | bus_LV_1151-36_2_4_node_193 | 0.4 | n |  | TRUE
29 | bus_LV_1151-36_2_4_node_189 | 0.4 | n |  | TRUE
30 | bus_LV_1151-36_2_4_node_190 | 0.4 | n |  | TRUE
31 | bus_LV_1151-36_2_4_node_191 | 0.4 | n |  | TRUE
32 | bus_LV_1151-36_2_4_node_196 | 0.4 | n |  | TRUE
33 | bus_LV_1151-36_2_4_node_107 | 0.4 | n |  | TRUE
34 | bus_LV_1151-36_2_4_node_91 | 0.4 | n |  | TRUE
35 | bus_LV_1151-36_2_4_node_92 | 0.4 | n |  | TRUE
36 | bus_LV_1151-36_2_4_node_93 | 0.4 | n |  | TRUE
37 | bus_LV_1151-36_2_4_node_94 | 0.4 | n |  | TRUE
38 | bus_LV_1151-36_2_4_node_98 | 0.4 | n |  | TRUE
39 | bus_LV_1151-36_2_4_node_112 | 0.4 | n |  | TRUE
40 | bus_LV_1151-36_2_4_node_95 | 0.4 | n |  | TRUE
41 | bus_LV_1151-36_2_4_node_100 | 0.4 | n |  | TRUE
42 | bus_LV_1151-36_2_4_node_101 | 0.4 | n |  | TRUE
43 | bus_LV_1151-36_2_4_node_102 | 0.4 | n |  | TRUE
44 | bus_LV_1151-36_2_4_node_103 | 0.4 | n |  | TRUE
45 | bus_LV_1151-36_2_4_node_106 | 0.4 | n |  | TRUE
46 | bus_MV_0_node_156 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1151-36_2_4_load_145 | 0 | 9.5219e-05 | 2.3864e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1151-36_2_4_load_157 | 3 | 0.0090979 | 0.0022801 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1151-36_2_4_load_156 | 4 | 0.0091265 | 0.0022873 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1151-36_2_4_load_158 | 6 | 7.8803e-05 | 1.975e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1151-36_2_4_load_159 | 7 | 0.00037055 | 9.287e-05 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1151-36_2_4_load_163 | 9 | 0.0031397 | 0.00078689 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1151-36_2_4_load_113 | 11 | 0.00083615 | 0.00020956 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1151-36_2_4_load_168 | 12 | 0.00062063 | 0.00015554 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1151-36_2_4_load_169 | 13 | 0.00034366 | 8.6129e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1151-36_2_4_load_172 | 18 | 0.0019339 | 0.00048468 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1151-36_2_4_load_173 | 19 | 0.00031484 | 7.8906e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1151-36_2_4_load_174 | 20 | 8.6424e-05 | 2.166e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1151-36_2_4_load_96 | 21 | 0.00015892 | 3.9829e-05 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1151-36_2_4_load_183 | 22 | 0.0019114 | 0.00047905 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1151-36_2_4_load_185 | 24 | 0.00028819 | 7.2228e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1151-36_2_4_load_186 | 25 | 0.0005374 | 0.00013469 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1151-36_2_4_load_187 | 26 | 0.00028084 | 7.0384e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1151-36_2_4_load_188 | 27 | 0.00028604 | 7.1688e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1151-36_2_4_load_193 | 28 | 0.00057481 | 0.00014406 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1151-36_2_4_load_190 | 30 | 0.0030754 | 0.00077076 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1151-36_2_4_load_191 | 31 | 0.00020888 | 5.235e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1151-36_2_4_load_196 | 32 | 0.0064044 | 0.0016051 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1151-36_2_4_load_91 | 34 | 0.0020616 | 0.00051669 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1151-36_2_4_load_92 | 35 | 0.00094197 | 0.00023608 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1151-36_2_4_load_93 | 36 | 0.00030076 | 7.5376e-05 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1151-36_2_4_load_94 | 37 | 0.00047162 | 0.0001182 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1151-36_2_4_load_98 | 38 | 0.00044709 | 0.00011205 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1151-36_2_4_load_112 | 39 | 0.001061 | 0.0002659 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1151-36_2_4_load_95 | 40 | 0.00019486 | 4.8837e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1151-36_2_4_load_100 | 41 | 0.0006251 | 0.00015667 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1151-36_2_4_load_101 | 42 | 0.0018013 | 0.00045145 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1151-36_2_4_load_103 | 44 | 0.001533 | 0.00038421 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1151-36_2_4_line_0 | NAYY 4x150 SE | 0 | 1 | 0.011263 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1151-36_2_4_line_1 | NAYY 4x150 SE | 1 | 2 | 0.1444 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1151-36_2_4_line_2 | NAYY 4x150 SE | 2 | 3 | 0.010152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1151-36_2_4_line_3 | NAYY 4x150 SE | 2 | 4 | 0.027532 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1151-36_2_4_line_4 | NAYY 4x150 SE | 4 | 5 | 0.091031 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
5 | LV_1151-36_2_4_line_5 | NAYY 4x150 SE | 5 | 33 | 0.2291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
6 | LV_1151-36_2_4_line_6 | NAYY 4x150 SE | 5 | 43 | 0.022503 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1151-36_2_4_line_7 | NAYY 4x150 SE | 6 | 7 | 0.024869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1151-36_2_4_line_8 | NAYY 4x150 SE | 7 | 8 | 0.017236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1151-36_2_4_line_9 | NAYY 4x150 SE | 8 | 43 | 0.22487 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1151-36_2_4_line_10 | NAYY 4x150 SE | 9 | 10 | 0.047627 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1151-36_2_4_line_11 | NAYY 4x150 SE | 10 | 11 | 0.11786 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1151-36_2_4_line_12 | NAYY 4x150 SE | 11 | 45 | 0.017285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1151-36_2_4_line_13 | NAYY 4x150 SE | 12 | 13 | 0.0052722 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
14 | LV_1151-36_2_4_line_14 | NAYY 4x150 SE | 12 | 14 | 0.029776 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
15 | LV_1151-36_2_4_line_15 | NAYY 4x150 SE | 13 | 15 | 0.019277 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
16 | LV_1151-36_2_4_line_16 | NAYY 4x150 SE | 14 | 16 | 0.45225 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1151-36_2_4_line_17 | NAYY 4x150 SE | 15 | 17 | 0.006258 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
18 | LV_1151-36_2_4_line_18 | NAYY 4x150 SE | 16 | 31 | 0.30217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1151-36_2_4_line_19 | NAYY 4x150 SE | 17 | 19 | 0.038368 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
20 | LV_1151-36_2_4_line_20 | NAYY 4x150 SE | 18 | 19 | 0.027771 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
21 | LV_1151-36_2_4_line_21 | NAYY 4x150 SE | 18 | 20 | 0.035206 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
22 | LV_1151-36_2_4_line_22 | NAYY 4x150 SE | 20 | 21 | 1.3292 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
23 | LV_1151-36_2_4_line_23 | NAYY 4x150 SE | 21 | 38 | 0.13462 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
24 | LV_1151-36_2_4_line_24 | NAYY 4x150 SE | 21 | 40 | 0.023753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1151-36_2_4_line_25 | NAYY 4x150 SE | 22 | 23 | 0.023388 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1151-36_2_4_line_26 | NAYY 4x150 SE | 23 | 24 | 0.024736 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1151-36_2_4_line_27 | NAYY 4x150 SE | 23 | 25 | 0.047897 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1151-36_2_4_line_28 | NAYY 4x150 SE | 24 | 26 | 0.042663 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1151-36_2_4_line_29 | NAYY 4x150 SE | 25 | 27 | 0.0010724 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1151-36_2_4_line_30 | NAYY 4x150 SE | 26 | 28 | 0.22332 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1151-36_2_4_line_31 | NAYY 4x150 SE | 27 | 29 | 0.082048 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1151-36_2_4_line_32 | NAYY 4x150 SE | 28 | 31 | 0.012166 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1151-36_2_4_line_33 | NAYY 4x150 SE | 29 | 30 | 0.19026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1151-36_2_4_line_34 | NAYY 4x150 SE | 32 | 33 | 0.11129 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1151-36_2_4_line_35 | NAYY 4x150 SE | 33 | 45 | 0.12027 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
36 | LV_1151-36_2_4_line_36 | NAYY 4x150 SE | 34 | 35 | 0.0021645 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
37 | LV_1151-36_2_4_line_37 | NAYY 4x150 SE | 34 | 36 | 0.011275 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
38 | LV_1151-36_2_4_line_38 | NAYY 4x150 SE | 35 | 37 | 0.0072417 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
39 | LV_1151-36_2_4_line_39 | NAYY 4x150 SE | 36 | 38 | 0.35806 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
40 | LV_1151-36_2_4_line_40 | NAYY 4x150 SE | 37 | 39 | 0.019152 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
41 | LV_1151-36_2_4_line_41 | NAYY 4x150 SE | 39 | 45 | 0.21182 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 3 | cs | TRUE
42 | LV_1151-36_2_4_line_42 | NAYY 4x150 SE | 41 | 42 | 0.022128 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
43 | LV_1151-36_2_4_line_43 | NAYY 4x150 SE | 41 | 43 | 0.21025 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
44 | LV_1151-36_2_4_line_44 | NAYY 4x150 SE | 42 | 44 | 0.0026217 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1151-36_2_4_trafo_156 | 0.25 MVA 20/0.4 kV | 46 | 4 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14
0 | 2643326.7538 | 1217091.4269 | 2643322.5048 | 1217088.0051 | 2643317.2012 | 1217085.6384
1 | 2643424.0051 | 1217194.5286 | 2643418.4865 | 1217188.2625 | 2643410.4879 | 1217182.7232 | 2643397.9237 | 1217174.5158 | 2643392.7708 | 1217169.0973 | 2643389.0479 | 1217163.289 | 2643385.5468 | 1217154.1247 | 2643380.2393 | 1217142.8239 | 2643376.1184 | 1217135.3784 | 2643370.9757 | 1217128.5481 | 2643360.8659 | 1217118.9355 | 2643326.7538 | 1217091.4269
2 | 2643424.0051 | 1217194.5286 | 2643424.0791 | 1217184.3786
3 | 2643424.0051 | 1217194.5286 | 2643428.3995 | 1217207.1458 | 2643441.4459 | 1217212.6802
4 | 2643528.137 | 1217199.0236 | 2643523.0443 | 1217198.8974 | 2643489.542 | 1217198.2527 | 2643478.5122 | 1217203.4532 | 2643460.5108 | 1217214.2839 | 2643443.0127 | 1217213.3448 | 2643441.4459 | 1217212.6802
5 | 2643528.137 | 1217199.0236 | 2643513.9656 | 1217427.6448
6 | 2643528.137 | 1217199.0236 | 2643533.2736 | 1217199.3613 | 2643534.2883 | 1217182.0362
7 | 2643501.233 | 1216962.2056 | 2643518.5941 | 1216965.1708 | 2643525.8406 | 1216964.7834
8 | 2643542.9638 | 1216962.9028 | 2643530.3046 | 1216964.5447 | 2643525.8406 | 1216964.7834
9 | 2643534.2883 | 1217182.0362 | 2643547.8104 | 1216962.449 | 2643542.9638 | 1216962.9028
10 | 2643504.0643 | 1217677.6656 | 2643501.1835 | 1217725.2055
11 | 2643504.0643 | 1217677.6656 | 2643507.051 | 1217628.2802 | 2643511.2997 | 1217560.0312
12 | 2643512.3737 | 1217542.7794 | 2643511.2997 | 1217560.0312
13 | 2643012.8596 | 1216565.5638 | 2643017.5763 | 1216563.2083
14 | 2642985.808 | 1216577.9561 | 2642998.1736 | 1216572.8978 | 2643012.8596 | 1216565.5638
15 | 2643034.8225 | 1216554.5957 | 2643017.5763 | 1216563.2083
16 | 2642985.808 | 1216577.9561 | 2642689.2775 | 1216919.4288
17 | 2643034.8225 | 1216554.5957 | 2643037.5072 | 1216560.2517
18 | 2642689.2775 | 1216919.4288 | 2642694.4769 | 1216926.9594 | 2642694.5639 | 1216931.7628 | 2642665.2589 | 1216998.904 | 2642662.1994 | 1217012.7237 | 2642662.3004 | 1217027.2552 | 2642670.5994 | 1217090.641 | 2642675.142 | 1217110.363 | 2642675.6752 | 1217120.7173 | 2642672.1222 | 1217133.4884 | 2642660.9856 | 1217153.6985 | 2642657.8688 | 1217162.8149 | 2642658.5881 | 1217175.8055 | 2642661.5553 | 1217187.6004 | 2642669.3557 | 1217206.6689
19 | 2643037.5072 | 1216560.2517 | 2643052.5907 | 1216592.0127 | 2643053.2023 | 1216595.1609
20 | 2643057.1181 | 1216622.6043 | 2643056.3091 | 1216611.1509 | 2643053.2023 | 1216595.1609
21 | 2643057.1181 | 1216622.6043 | 2643058.4924 | 1216642.0627 | 2643061.5613 | 1216652.3243 | 2643062.7171 | 1216657.177
22 | 2644132.8736 | 1217445.5836 | 2643062.7171 | 1216657.177
23 | 2644089.5289 | 1217545.7311 | 2644090.0844 | 1217545.468 | 2644088.3519 | 1217503.6414 | 2644089.3457 | 1217480.1125 | 2644093.3864 | 1217456.1837 | 2644097.3055 | 1217449.72 | 2644103.0344 | 1217445.9045 | 2644110.3727 | 1217445.1472 | 2644132.8736 | 1217445.5836
24 | 2644156.6259 | 1217445.7229 | 2644138.1888 | 1217445.6866 | 2644132.8736 | 1217445.5836
25 | 2642816.6979 | 1217463.9314 | 2642793.9178 | 1217469.2291
26 | 2642816.6979 | 1217463.9314 | 2642819.3496 | 1217448.7859 | 2642818.969 | 1217439.4332
27 | 2642816.6979 | 1217463.9314 | 2642846.8775 | 1217474.6545 | 2642859.5589 | 1217477.1359 | 2642862.467 | 1217477.6127
28 | 2642796.6897 | 1217404.5016 | 2642797.1843 | 1217409.7148 | 2642799.1045 | 1217415.0428 | 2642803.3983 | 1217420.6881 | 2642813.3987 | 1217429.7319 | 2642818.969 | 1217439.4332 | 2642818.969 | 1217439.4332
29 | 2642862.467 | 1217477.6127 | 2642863.5253 | 1217477.7862
30 | 2642796.6897 | 1217404.5016 | 2642673.9621 | 1217217.9293
31 | 2642924.4174 | 1217526.187 | 2642903.549 | 1217495.8411 | 2642893.5872 | 1217486.7307 | 2642881.7583 | 1217480.7754 | 2642863.5253 | 1217477.7862
32 | 2642673.9621 | 1217217.9293 | 2642669.3557 | 1217206.6689
33 | 2642924.4174 | 1217526.187 | 2642940.3095 | 1217521.2874 | 2642955.5062 | 1217511.7689 | 2643005.6695 | 1217472.2514 | 2643048.3065 | 1217440.718 | 2643060.0744 | 1217427.8064 | 2643072.0766 | 1217409.7713
34 | 2643406.1566 | 1217409.5485 | 2643419.9305 | 1217419.3879 | 2643428.8664 | 1217422.2992 | 2643513.9656 | 1217427.6448
35 | 2643512.3737 | 1217542.7794 | 2643519.2085 | 1217427.961 | 2643513.9656 | 1217427.6448
36 | 2643729.8666 | 1217469.8436 | 2643728.0298 | 1217470.5136 | 2643727.8547 | 1217470.6282
37 | 2643740.4587 | 1217465.9798 | 2643729.8666 | 1217469.8436
38 | 2643727.8547 | 1217470.6282 | 2643721.7959 | 1217474.5949
39 | 2644089.5289 | 1217545.7311 | 2643740.4587 | 1217465.9798
40 | 2643706.4721 | 1217485.8506 | 2643708.16 | 1217483.609 | 2643718.2058 | 1217476.9454 | 2643721.7959 | 1217474.5949
41 | 2643512.3737 | 1217542.7794 | 2643570.7715 | 1217537.1579 | 2643636.7295 | 1217529.4911 | 2643641.406 | 1217528.3691 | 2643647.5044 | 1217526.9017 | 2643673.2822 | 1217520.6978 | 2643682.9002 | 1217516.4657 | 2643687.1877 | 1217511.4608 | 2643706.4721 | 1217485.8506
42 | 2643744.4784 | 1217186.2885 | 2643766.5815 | 1217187.3445
43 | 2643534.2883 | 1217182.0362 | 2643716.7868 | 1217184.9949 | 2643720.4988 | 1217184.9999 | 2643726.3105 | 1217185.4205 | 2643744.4784 | 1217186.2885
44 | 2643769.2002 | 1217187.4696 | 2643766.5815 | 1217187.3445

## bus_geodata
| x | y | coords
0 | 2643317.2012 | 1217085.6384
1 | 2643326.7538 | 1217091.4269
2 | 2643424.0051 | 1217194.5286
3 | 2643424.0791 | 1217184.3786
4 | 2643441.4459 | 1217212.6802
5 | 2643528.137 | 1217199.0236
6 | 2643501.233 | 1216962.2056
7 | 2643525.8406 | 1216964.7834
8 | 2643542.9638 | 1216962.9028
9 | 2643501.1835 | 1217725.2055
10 | 2643504.0643 | 1217677.6656
11 | 2643511.2997 | 1217560.0312
12 | 2643012.8596 | 1216565.5638
13 | 2643017.5763 | 1216563.2083
14 | 2642985.808 | 1216577.9561
15 | 2643034.8225 | 1216554.5957
16 | 2642689.2775 | 1216919.4288
17 | 2643037.5072 | 1216560.2517
18 | 2643057.1181 | 1216622.6043
19 | 2643053.2023 | 1216595.1609
20 | 2643062.7171 | 1216657.177
21 | 2644132.8736 | 1217445.5836
22 | 2642793.9178 | 1217469.2291
23 | 2642816.6979 | 1217463.9314
24 | 2642818.969 | 1217439.4332
25 | 2642862.467 | 1217477.6127
26 | 2642796.6897 | 1217404.5016
27 | 2642863.5253 | 1217477.7862
28 | 2642673.9621 | 1217217.9293
29 | 2642924.4174 | 1217526.187
30 | 2643072.0766 | 1217409.7713
31 | 2642669.3557 | 1217206.6689
32 | 2643406.1566 | 1217409.5485
33 | 2643513.9656 | 1217427.6448
34 | 2643729.8666 | 1217469.8436
35 | 2643727.8547 | 1217470.6282
36 | 2643740.4587 | 1217465.9798
37 | 2643721.7959 | 1217474.5949
38 | 2644089.5289 | 1217545.7311
39 | 2643706.4721 | 1217485.8506
40 | 2644156.6259 | 1217445.7229
41 | 2643744.4784 | 1217186.2885
42 | 2643766.5815 | 1217187.3445
43 | 2643534.2883 | 1217182.0362
44 | 2643769.2002 | 1217187.4696
45 | 2643512.3737 | 1217542.7794
46 | 2643441.4459 | 1217212.6802

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99962 | -0.0026917 | 9.5219e-05 | 2.3864e-05
1 | 0.99962 | -0.0026809 | 0 | 0
2 | 0.99964 | -0.0025318 | 0 | 0
3 | 0.99951 | -0.0034545 | 0.0090979 | 0.0022801
4 | 1 | 0 | -0.041256 | -0.010056
5 | 0.99865 | -0.0096601 | 0 | 0
6 | 0.99835 | -0.011808 | 7.8803e-05 | 1.975e-05
7 | 0.99835 | -0.011788 | 0.00037055 | 9.287e-05
8 | 0.99836 | -0.01171 | 0 | 0
9 | 0.99372 | -0.045016 | 0.0031397 | 0.00078689
10 | 0.99394 | -0.043504 | 0 | 0
11 | 0.99447 | -0.039756 | 0.00083615 | 0.00020956
12 | 0.98265 | -0.12591 | 0.00062063 | 0.00015554
13 | 0.98267 | -0.12577 | 0.00034366 | 8.6129e-05
14 | 0.9825 | -0.12703 | 0 | 0
15 | 0.98275 | -0.12522 | 0 | 0
16 | 0.97774 | -0.1612 | 0 | 0
17 | 0.98277 | -0.12504 | 0 | 0
18 | 0.98304 | -0.12312 | 0.0019339 | 0.00048468
19 | 0.98293 | -0.12394 | 0.00031484 | 7.8906e-05
20 | 0.98322 | -0.12184 | 8.6424e-05 | 2.166e-05
21 | 0.98998 | -0.072667 | 0.00015892 | 3.9829e-05
22 | 0.9717 | -0.20489 | 0.0019114 | 0.00047905
23 | 0.97176 | -0.20441 | 0 | 0
24 | 0.97197 | -0.20289 | 0.00028819 | 7.2228e-05
25 | 0.97149 | -0.2064 | 0.0005374 | 0.00013469
26 | 0.97236 | -0.20012 | 0.00028084 | 7.0384e-05
27 | 0.97148 | -0.20644 | 0.00028604 | 7.1688e-05
28 | 0.97445 | -0.185 | 0.00057481 | 0.00014406
29 | 0.97111 | -0.20913 | 0 | 0
30 | 0.97025 | -0.21534 | 0.0030754 | 0.00077076
31 | 0.97457 | -0.18411 | 0.00020888 | 5.235e-05
32 | 0.99471 | -0.03781 | 0.0064044 | 0.0016051
33 | 0.99573 | -0.030622 | 0 | 0
34 | 0.99271 | -0.052572 | 0.0020616 | 0.00051669
35 | 0.99273 | -0.052468 | 0.00094197 | 0.00023608
36 | 0.99265 | -0.053039 | 0.00030076 | 7.5376e-05
37 | 0.99278 | -0.052094 | 0.00047162 | 0.0001182
38 | 0.99069 | -0.067465 | 0.00044709 | 0.00011205
39 | 0.99292 | -0.051076 | 0.001061 | 0.0002659
40 | 0.98998 | -0.072714 | 0.00019486 | 4.8837e-05
41 | 0.99732 | -0.019034 | 0.0006251 | 0.00015667
42 | 0.99721 | -0.019775 | 0.0018013 | 0.00045145
43 | 0.99851 | -0.010664 | 0 | 0
44 | 0.99721 | -0.019815 | 0.001533 | 0.00038421
45 | 0.99457 | -0.039059 | 0 | 0
46 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -9.5219e-05 | -2.3864e-05 | 9.5219e-05 | 2.3716e-05 | 1.4115e-10 | -1.476e-07 | 0.00014174 | 0.00014169 | 0.00014174 | 0.99962 | -0.0026917 | 0.99962 | -0.0026809 | 0.052497
1 | -9.5219e-05 | -2.3716e-05 | 9.5221e-05 | 2.1824e-05 | 1.8007e-09 | -1.8924e-06 | 0.00014169 | 0.00014105 | 0.00014169 | 0.99962 | -0.0026809 | 0.99964 | -0.0025318 | 0.052478
2 | 0.009099 | 0.0022805 | -0.0090979 | -0.0022801 | 1.1621e-06 | 3.139e-07 | 0.013544 | 0.013544 | 0.013544 | 0.99964 | -0.0025318 | 0.99951 | -0.0034545 | 5.0165
3 | -0.0091943 | -0.0023023 | 0.0091975 | 0.0023032 | 3.2177e-06 | 8.7649e-07 | 0.013685 | 0.013685 | 0.013685 | 0.99964 | -0.0025318 | 1 | 0 | 5.0687
4 | 0.031259 | 0.0077525 | -0.031218 | -0.0077404 | 4.0916e-05 | 1.2159e-05 | 0.046485 | 0.046487 | 0.046487 | 1 | 0 | 0.99865 | -0.0096601 | 5.7391
5 | 0.026804 | 0.0066401 | -0.026728 | -0.0066199 | 7.5912e-05 | 2.0231e-05 | 0.039911 | 0.039914 | 0.039914 | 0.99865 | -0.0096601 | 0.99573 | -0.030622 | 4.9277
6 | 0.0044144 | 0.0011002 | -0.0044138 | -0.0011003 | 6.0712e-07 | -6.0872e-08 | 0.0065754 | 0.0065755 | 0.0065755 | 0.99865 | -0.0096601 | 0.99851 | -0.010664 | 2.4354
7 | -7.8803e-05 | -1.975e-05 | 7.8803e-05 | 1.9425e-05 | 2.1388e-10 | -3.2511e-07 | 0.00011745 | 0.00011734 | 0.00011745 | 0.99835 | -0.011808 | 0.99835 | -0.011788 | 0.043502
8 | -0.00044936 | -0.00011229 | 0.00044936 | 0.00011207 | 4.8222e-09 | -2.2352e-07 | 0.00066964 | 0.00066956 | 0.00066964 | 0.99835 | -0.011788 | 0.99836 | -0.01171 | 0.24802
9 | -0.00044936 | -0.00011207 | 0.00044943 | 0.00010915 | 6.2811e-08 | -2.9168e-06 | 0.00066956 | 0.00066855 | 0.00066956 | 0.99836 | -0.01171 | 0.99851 | -0.010664 | 0.24799
10 | -0.0031397 | -0.00078689 | 0.0031404 | 0.00078653 | 6.5689e-07 | -3.645e-07 | 0.0047015 | 0.0047013 | 0.0047015 | 0.99372 | -0.045016 | 0.99394 | -0.043504 | 1.7413
11 | -0.0031404 | -0.00078653 | 0.003142 | 0.00078563 | 1.6253e-06 | -9.0322e-07 | 0.0047013 | 0.0047007 | 0.0047013 | 0.99394 | -0.043504 | 0.99447 | -0.039756 | 1.7412
12 | -0.0039782 | -0.00099519 | 0.0039786 | 0.00099511 | 3.8209e-07 | -7.7334e-08 | 0.0059519 | 0.0059518 | 0.0059519 | 0.99447 | -0.039756 | 0.99457 | -0.039059 | 2.2044
13 | -0.007864 | -0.0019634 | 0.0078642 | 0.0019633 | 1.5544e-07 | -1.4058e-07 | 0.011906 | 0.011906 | 0.011906 | 0.98265 | -0.12591 | 0.98267 | -0.12577 | 1.4698
14 | 0.0072434 | 0.0018079 | -0.0072423 | -0.0018082 | 1.1172e-06 | -3.246e-07 | 0.010966 | 0.010966 | 0.010966 | 0.98265 | -0.12591 | 0.9825 | -0.12703 | 2.0308
15 | -0.0082078 | -0.0020494 | 0.0082084 | 0.0020489 | 6.191e-07 | -4.9458e-07 | 0.012426 | 0.012426 | 0.012426 | 0.98267 | -0.12577 | 0.98275 | -0.12522 | 1.5341
16 | 0.0072423 | 0.0018082 | -0.0072083 | -0.0018009 | 3.3944e-05 | 7.3555e-06 | 0.010966 | 0.010968 | 0.010968 | 0.9825 | -0.12703 | 0.97774 | -0.1612 | 4.0623
17 | -0.0082084 | -0.0020489 | 0.0082086 | 0.0020488 | 2.0097e-07 | -1.6058e-07 | 0.012426 | 0.012426 | 0.012426 | 0.98275 | -0.12522 | 0.98277 | -0.12504 | 1.534
18 | 0.0072083 | 0.0018009 | -0.0071856 | -0.0017959 | 2.2686e-05 | 4.948e-06 | 0.010968 | 0.01097 | 0.01097 | 0.97774 | -0.1612 | 0.97457 | -0.18411 | 4.0628
19 | -0.0082086 | -0.0020488 | 0.0082099 | 0.0020478 | 1.2321e-06 | -9.8483e-07 | 0.012426 | 0.012425 | 0.012426 | 0.98277 | -0.12504 | 0.98293 | -0.12394 | 1.534
20 | 0.0085257 | 0.002126 | -0.0085247 | -0.0021267 | 9.6148e-07 | -6.8632e-07 | 0.012901 | 0.012902 | 0.012902 | 0.98304 | -0.12312 | 0.98293 | -0.12394 | 1.5928
21 | -0.01046 | -0.0026107 | 0.010461 | 0.00261 | 1.8347e-06 | -6.3363e-07 | 0.015829 | 0.015828 | 0.015829 | 0.98304 | -0.12312 | 0.98322 | -0.12184 | 1.9542
22 | -0.010548 | -0.0026317 | 0.010618 | 0.0026078 | 7.0337e-05 | -2.387e-05 | 0.015959 | 0.015941 | 0.015959 | 0.98322 | -0.12184 | 0.98998 | -0.072667 | 1.9703
23 | -0.010972 | -0.0026962 | 0.01098 | 0.0026939 | 7.5973e-06 | -2.2744e-06 | 0.016473 | 0.016471 | 0.016473 | 0.98998 | -0.072667 | 0.99069 | -0.067465 | 2.0337
24 | 0.00019486 | 4.8532e-05 | -0.00019486 | -4.8837e-05 | 1.2711e-09 | -3.0493e-07 | 0.00029279 | 0.00029289 | 0.00029289 | 0.98998 | -0.072667 | 0.98998 | -0.072714 | 0.10848
25 | -0.0019114 | -0.00047905 | 0.0019115 | 0.0004788 | 1.2503e-07 | -2.4164e-07 | 0.0029271 | 0.002927 | 0.0029271 | 0.9717 | -0.20489 | 0.97176 | -0.20441 | 1.0841
26 | -0.0058152 | -0.0014538 | 0.0058164 | 0.001454 | 1.2235e-06 | 1.6406e-07 | 0.0089032 | 0.0089031 | 0.0089032 | 0.97176 | -0.20441 | 0.97197 | -0.20289 | 3.2975
27 | 0.0039037 | 0.00097503 | -0.0039026 | -0.00097521 | 1.0675e-06 | -1.8264e-07 | 0.0059763 | 0.0059765 | 0.0059765 | 0.97176 | -0.20441 | 0.97149 | -0.2064 | 2.2135
28 | -0.0061046 | -0.0015262 | 0.0061069 | 0.0015266 | 2.3245e-06 | 3.6504e-07 | 0.0093443 | 0.0093441 | 0.0093443 | 0.97197 | -0.20289 | 0.97236 | -0.20012 | 3.4609
29 | 0.0033652 | 0.00084052 | -0.0033652 | -0.00084053 | 1.7772e-08 | -6.4431e-09 | 0.0051534 | 0.0051534 | 0.0051534 | 0.97149 | -0.2064 | 0.97148 | -0.20644 | 1.9087
30 | -0.0063878 | -0.001597 | 0.0064011 | 0.0015993 | 1.3311e-05 | 2.3435e-06 | 0.0097739 | 0.0097729 | 0.0097739 | 0.97236 | -0.20012 | 0.97445 | -0.185 | 3.62
31 | 0.0030791 | 0.00076884 | -0.003078 | -0.00076942 | 1.1384e-06 | -5.7766e-07 | 0.0047153 | 0.0047156 | 0.0047156 | 0.97148 | -0.20644 | 0.97111 | -0.20913 | 1.7465
32 | -0.0069759 | -0.0017434 | 0.0069768 | 0.0017436 | 8.6118e-07 | 1.7964e-07 | 0.010651 | 0.010651 | 0.010651 | 0.97445 | -0.185 | 0.97457 | -0.18411 | 3.9447
33 | 0.003078 | 0.00076942 | -0.0030754 | -0.00077076 | 2.6406e-06 | -1.3363e-06 | 0.0047156 | 0.0047165 | 0.0047165 | 0.97111 | -0.20913 | 0.97025 | -0.21534 | 1.7468
34 | -0.0064044 | -0.0016051 | 0.0064108 | 0.0016061 | 6.3736e-06 | 1.0053e-06 | 0.0095805 | 0.00958 | 0.0095805 | 0.99471 | -0.03781 | 0.99573 | -0.030622 | 3.5483
35 | 0.020317 | 0.0050138 | -0.020294 | -0.0050096 | 2.3021e-05 | 4.1663e-06 | 0.030334 | 0.030336 | 0.030336 | 0.99573 | -0.030622 | 0.99457 | -0.039059 | 3.7452
36 | -0.013812 | -0.0033924 | 0.013812 | 0.0033924 | 1.9251e-07 | -9.9109e-09 | 0.020679 | 0.020679 | 0.020679 | 0.99271 | -0.052572 | 0.99273 | -0.052468 | 2.5529
37 | 0.01175 | 0.0028757 | -0.011749 | -0.0028759 | 7.2549e-07 | -1.5825e-07 | 0.017588 | 0.017589 | 0.017589 | 0.99271 | -0.052572 | 0.99265 | -0.053039 | 2.1714
38 | -0.014754 | -0.0036285 | 0.014755 | 0.0036285 | 7.3504e-07 | 1.8058e-09 | 0.02209 | 0.02209 | 0.02209 | 0.99273 | -0.052468 | 0.99278 | -0.052094 | 2.7272
39 | 0.011449 | 0.0028005 | -0.011427 | -0.002806 | 2.188e-05 | -5.4434e-06 | 0.017138 | 0.017142 | 0.017142 | 0.99265 | -0.053039 | 0.99069 | -0.067465 | 2.1164
40 | -0.015226 | -0.0037467 | 0.015228 | 0.0037468 | 2.0703e-06 | 5.3237e-08 | 0.022797 | 0.022797 | 0.022797 | 0.99278 | -0.052094 | 0.99292 | -0.051076 | 2.8145
41 | -0.016289 | -0.0040127 | 0.016315 | 0.0040145 | 2.62e-05 | 1.844e-06 | 0.024387 | 0.024384 | 0.024387 | 0.99292 | -0.051076 | 0.99457 | -0.039059 | 3.0107
42 | 0.0033347 | 0.00083547 | -0.0033343 | -0.00083563 | 3.4181e-07 | -1.5726e-07 | 0.0049753 | 0.0049754 | 0.0049754 | 0.99732 | -0.019034 | 0.99721 | -0.019775 | 1.8427
43 | -0.0039598 | -0.00099214 | 0.0039644 | 0.00099115 | 4.5785e-06 | -9.8586e-07 | 0.005908 | 0.005907 | 0.005908 | 0.99732 | -0.019034 | 0.99851 | -0.010664 | 2.1881
44 | 0.001533 | 0.00038418 | -0.001533 | -0.00038421 | 8.5607e-09 | -3.0911e-08 | 0.0022875 | 0.0022875 | 0.0022875 | 0.99721 | -0.019775 | 0.99721 | -0.019815 | 0.84724

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.050383 | 0.012343

## res_load
| p_mw | q_mvar
0 | 9.5219e-05 | 2.3864e-05
1 | 0.0090979 | 0.0022801
2 | 0.0091265 | 0.0022873
3 | 7.8803e-05 | 1.975e-05
4 | 0.00037055 | 9.287e-05
5 | 0.0031397 | 0.00078689
6 | 0.00083615 | 0.00020956
7 | 0.00062063 | 0.00015554
8 | 0.00034366 | 8.6129e-05
9 | 0.0019339 | 0.00048468
10 | 0.00031484 | 7.8906e-05
11 | 8.6424e-05 | 2.166e-05
12 | 0.00015892 | 3.9829e-05
13 | 0.0019114 | 0.00047905
14 | 0.00028819 | 7.2228e-05
15 | 0.0005374 | 0.00013469
16 | 0.00028084 | 7.0384e-05
17 | 0.00028604 | 7.1688e-05
18 | 0.00057481 | 0.00014406
19 | 0.0030754 | 0.00077076
20 | 0.00020888 | 5.235e-05
21 | 0.0064044 | 0.0016051
22 | 0.0020616 | 0.00051669
23 | 0.00094197 | 0.00023608
24 | 0.00030076 | 7.5376e-05
25 | 0.00047162 | 0.0001182
26 | 0.00044709 | 0.00011205
27 | 0.001061 | 0.0002659
28 | 0.00019486 | 4.8837e-05
29 | 0.0006251 | 0.00015667
30 | 0.0018013 | 0.00045145
31 | 0.001533 | 0.00038421

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1