## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1151-37_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1151-37_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1151-37_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1151-37_0_3_node_24 | 0.4 | n |  | TRUE
4 | bus_LV_1151-37_0_3_node_22 | 0.4 | n |  | TRUE
5 | bus_LV_1151-37_0_3_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_1151-37_0_3_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1151-37_0_3_node_3 | 0.4 | n |  | TRUE
8 | bus_LV_1151-37_0_3_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1151-37_0_3_node_34 | 0.4 | n |  | TRUE
10 | bus_LV_1151-37_0_3_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1151-37_0_3_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1151-37_0_3_node_12 | 0.4 | n |  | TRUE
13 | bus_LV_1151-37_0_3_node_13 | 0.4 | n |  | TRUE
14 | bus_LV_1151-37_0_3_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1151-37_0_3_node_29 | 0.4 | n |  | TRUE
16 | bus_LV_1151-37_0_3_node_30 | 0.4 | n |  | TRUE
17 | bus_LV_1151-37_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1151-37_0_3_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1151-37_0_3_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1151-37_0_3_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1151-37_0_3_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_1151-37_0_3_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_1151-37_0_3_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_1151-37_0_3_node_26 | 0.4 | n |  | TRUE
25 | bus_LV_1151-37_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1151-37_0_3_node_17 | 0.4 | n |  | TRUE
27 | bus_LV_1151-37_0_3_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_1151-37_0_3_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1151-37_0_3_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_1151-37_0_3_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1151-37_0_3_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_1151-37_0_3_node_27 | 0.4 | n |  | TRUE
33 | bus_MV_128_0_node_192 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1151-37_0_3_load_0 | 0 | 0.0028355 | 0.00071064 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1151-37_0_3_load_1 | 1 | 0.0039371 | 0.00098673 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1151-37_0_3_load_24 | 3 | 0.0018987 | 0.00047587 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1151-37_0_3_load_22 | 4 | 0.00068391 | 0.0001714 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1151-37_0_3_load_6 | 5 | 0.002666 | 0.00066816 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1151-37_0_3_load_4 | 6 | 0.0028441 | 0.0007128 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1151-37_0_3_load_3 | 7 | 0.0021039 | 0.00052729 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1151-37_0_3_load_5 | 8 | 0.0062234 | 0.0015597 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1151-37_0_3_load_34 | 9 | 0.002669 | 0.00066892 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1151-37_0_3_load_12 | 12 | 0.0074675 | 0.0018715 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1151-37_0_3_load_8 | 14 | 0.002862 | 0.00071728 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1151-37_0_3_load_29 | 15 | 0.0016029 | 0.00040173 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1151-37_0_3_load_30 | 16 | 0.0028115 | 0.00070464 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1151-37_0_3_load_9 | 17 | 0.0069568 | 0.0017435 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1151-37_0_3_load_11 | 18 | 0.006508 | 0.0016311 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1151-37_0_3_load_21 | 19 | 0.0065441 | 0.0016401 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1151-37_0_3_load_14 | 20 | 0.0078359 | 0.0019639 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1151-37_0_3_load_20 | 21 | 0.0069567 | 0.0017435 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1151-37_0_3_load_15 | 22 | 0.0094968 | 0.0023801 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1151-37_0_3_load_28 | 23 | 0.0017678 | 0.00044306 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1151-37_0_3_load_26 | 24 | 0.0018472 | 0.00046294 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1151-37_0_3_load_16 | 25 | 0.009477 | 0.0023752 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1151-37_0_3_load_17 | 26 | 0.01016 | 0.0025464 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1151-37_0_3_load_18 | 27 | 0.012032 | 0.0030155 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1151-37_0_3_load_31 | 28 | 0.00592 | 0.0014837 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1151-37_0_3_load_19 | 29 | 0.002894 | 0.00072531 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1151-37_0_3_load_25 | 31 | 0.0015716 | 0.00039389 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1151-37_0_3_load_27 | 32 | 0.0087171 | 0.0021847 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1151-37_0_3_line_0 | NAYY 4x150 SE | 0 | 1 | 0.01001 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1151-37_0_3_line_1 | NAYY 4x150 SE | 0 | 2 | 0.017071 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1151-37_0_3_line_2 | NAYY 4x150 SE | 2 | 3 | 0.084679 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1151-37_0_3_line_3 | NAYY 4x150 SE | 3 | 4 | 0.0091642 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1151-37_0_3_line_4 | NAYY 4x150 SE | 4 | 30 | 0.0082888 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1151-37_0_3_line_5 | NAYY 4x150 SE | 5 | 6 | 0.0034102 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1151-37_0_3_line_6 | NAYY 4x150 SE | 6 | 7 | 0.018339 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1151-37_0_3_line_7 | NAYY 4x150 SE | 7 | 8 | 0.011787 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1151-37_0_3_line_8 | NAYY 4x150 SE | 7 | 9 | 0.025371 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1151-37_0_3_line_9 | NAYY 4x150 SE | 8 | 10 | 0.026811 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1151-37_0_3_line_10 | NAYY 4x150 SE | 10 | 11 | 0.038502 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1151-37_0_3_line_11 | NAYY 4x150 SE | 11 | 12 | 0.034949 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1151-37_0_3_line_12 | NAYY 4x150 SE | 11 | 13 | 0.030588 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1151-37_0_3_line_13 | NAYY 4x150 SE | 11 | 14 | 0.021947 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
14 | LV_1151-37_0_3_line_14 | NAYY 4x150 SE | 12 | 20 | 0.024505 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1151-37_0_3_line_15 | NAYY 4x150 SE | 13 | 15 | 0.024103 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1151-37_0_3_line_16 | NAYY 4x150 SE | 13 | 16 | 0.021437 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1151-37_0_3_line_17 | NAYY 4x150 SE | 14 | 17 | 0.026008 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1151-37_0_3_line_18 | NAYY 4x150 SE | 15 | 23 | 0.0063221 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1151-37_0_3_line_19 | NAYY 4x150 SE | 16 | 24 | 0.0011268 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1151-37_0_3_line_20 | NAYY 4x150 SE | 17 | 18 | 0.010244 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1151-37_0_3_line_21 | NAYY 4x150 SE | 18 | 19 | 0.0215 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1151-37_0_3_line_22 | NAYY 4x150 SE | 19 | 21 | 0.0035976 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1151-37_0_3_line_23 | NAYY 4x150 SE | 20 | 22 | 0.0076544 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1151-37_0_3_line_24 | NAYY 4x150 SE | 21 | 29 | 0.021336 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1151-37_0_3_line_25 | NAYY 4x150 SE | 22 | 25 | 0.022727 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1151-37_0_3_line_26 | NAYY 4x150 SE | 23 | 32 | 0.021629 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1151-37_0_3_line_27 | NAYY 4x150 SE | 24 | 30 | 0.020353 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1151-37_0_3_line_28 | NAYY 4x150 SE | 25 | 26 | 0.073905 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1151-37_0_3_line_29 | NAYY 4x150 SE | 26 | 27 | 0.036729 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1151-37_0_3_line_30 | NAYY 4x150 SE | 27 | 28 | 0.023436 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1151-37_0_3_line_31 | NAYY 4x150 SE | 30 | 31 | 0.014334 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1151-37_0_3_trafo_8 | 0.25 MVA 20/0.4 kV | 33 | 14 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2642404.0287 | 1218716.9066 | 2642407.2337 | 1218726.3894
1 | 2642398.5629 | 1218700.7347 | 2642404.0287 | 1218716.9066
2 | 2642315.5266 | 1218684.135 | 2642398.5629 | 1218700.7347
3 | 2642315.5266 | 1218684.135 | 2642309.6512 | 1218682.2033 | 2642308.4938 | 1218680.6053 | 2642308.423 | 1218679.6016
4 | 2642309.2877 | 1218671.3943 | 2642308.2938 | 1218677.7688 | 2642308.423 | 1218679.6016
5 | 2642308.1693 | 1218709.2089 | 2642304.7598 | 1218709.277
6 | 2642304.7598 | 1218709.277 | 2642286.4243 | 1218709.6436
7 | 2642274.6401 | 1218709.8792 | 2642286.4243 | 1218709.6436
8 | 2642286.4243 | 1218709.6436 | 2642294.4717 | 1218733.7041
9 | 2642247.8349 | 1218710.4152 | 2642274.6401 | 1218709.8792
10 | 2642247.8349 | 1218710.4152 | 2642243.6527 | 1218710.4967 | 2642254.7515 | 1218682.1696 | 2642250.9712 | 1218681.2312
11 | 2642250.9712 | 1218681.2312 | 2642217.0482 | 1218672.8243
12 | 2642250.9712 | 1218681.2312 | 2642254.7515 | 1218682.1696 | 2642263.5593 | 1218661.2084 | 2642265.9678 | 1218661.9037 | 2642267.3614 | 1218662.3027
13 | 2642250.9712 | 1218681.2312 | 2642259.6033 | 1218661.0533
14 | 2642217.0482 | 1218672.8243 | 2642193.263 | 1218666.9298
15 | 2642267.3614 | 1218662.3027 | 2642277.0071 | 1218640.2141
16 | 2642267.3614 | 1218662.3027 | 2642270.9286 | 1218663.3286 | 2642287.6025 | 1218666.4598 | 2642288.3436 | 1218666.6284
17 | 2642269.833 | 1218637.1415 | 2642259.6033 | 1218661.0533
18 | 2642279.5371 | 1218634.4203 | 2642277.0071 | 1218640.2141
19 | 2642289.4423 | 1218666.8784 | 2642288.3436 | 1218666.6284
20 | 2642273.8622 | 1218627.7231 | 2642269.833 | 1218637.1415
21 | 2642273.8622 | 1218627.7231 | 2642282.3185 | 1218607.9564
22 | 2642283.7335 | 1218604.6488 | 2642282.3185 | 1218607.9564
23 | 2642185.8334 | 1218665.0885 | 2642193.263 | 1218666.9298
24 | 2642283.7335 | 1218604.6488 | 2642286.7246 | 1218597.6571 | 2642292.2409 | 1218585.0824
25 | 2642185.8334 | 1218665.0885 | 2642163.774 | 1218659.6217
26 | 2642279.5371 | 1218634.4203 | 2642288.1928 | 1218614.5989
27 | 2642309.2877 | 1218671.3943 | 2642289.4423 | 1218666.8784
28 | 2642152.4614 | 1218601.5089 | 2642141.3426 | 1218640.9093 | 2642141.3456 | 1218644.7783 | 2642142.6745 | 1218648.9568 | 2642145.0091 | 1218652.5866 | 2642147.731 | 1218655.0962 | 2642151.6818 | 1218656.625 | 2642163.774 | 1218659.6217
29 | 2642162.4368 | 1218566.1605 | 2642152.4614 | 1218601.5089
30 | 2642162.4368 | 1218566.1605 | 2642164.2441 | 1218559.7562 | 2642165.8528 | 1218556.5657 | 2642168.6201 | 1218552.6718 | 2642174.2287 | 1218546.3764
31 | 2642309.2877 | 1218671.3943 | 2642311.7179 | 1218657.2698

## bus_geodata
| x | y | coords
0 | 2642404.0287 | 1218716.9066
1 | 2642407.2337 | 1218726.3894
2 | 2642398.5629 | 1218700.7347
3 | 2642315.5266 | 1218684.135
4 | 2642308.423 | 1218679.6016
5 | 2642308.1693 | 1218709.2089
6 | 2642304.7598 | 1218709.277
7 | 2642286.4243 | 1218709.6436
8 | 2642274.6401 | 1218709.8792
9 | 2642294.4717 | 1218733.7041
10 | 2642247.8349 | 1218710.4152
11 | 2642250.9712 | 1218681.2312
12 | 2642217.0482 | 1218672.8243
13 | 2642267.3614 | 1218662.3027
14 | 2642259.6033 | 1218661.0533
15 | 2642277.0071 | 1218640.2141
16 | 2642288.3436 | 1218666.6284
17 | 2642269.833 | 1218637.1415
18 | 2642273.8622 | 1218627.7231
19 | 2642282.3185 | 1218607.9564
20 | 2642193.263 | 1218666.9298
21 | 2642283.7335 | 1218604.6488
22 | 2642185.8334 | 1218665.0885
23 | 2642279.5371 | 1218634.4203
24 | 2642289.4423 | 1218666.8784
25 | 2642163.774 | 1218659.6217
26 | 2642152.4614 | 1218601.5089
27 | 2642162.4368 | 1218566.1605
28 | 2642174.2287 | 1218546.3764
29 | 2642292.2409 | 1218585.0824
30 | 2642309.2877 | 1218671.3943
31 | 2642311.7179 | 1218657.2698
32 | 2642288.1928 | 1218614.5989
33 | 2642250.9712 | 1218681.2312

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99508 | -0.03446 | 0.0028355 | 0.00071064
1 | 0.99502 | -0.034858 | 0.0039371 | 0.00098673
2 | 0.99525 | -0.033295 | 0 | 0
3 | 0.99607 | -0.027515 | 0.0018987 | 0.00047587
4 | 0.99618 | -0.026715 | 0.00068391 | 0.0001714
5 | 0.99645 | -0.024841 | 0.002666 | 0.00066816
6 | 0.99646 | -0.02475 | 0.0028441 | 0.0007128
7 | 0.99661 | -0.023734 | 0.0021039 | 0.00052729
8 | 0.99678 | -0.022516 | 0.0062234 | 0.0015597
9 | 0.99651 | -0.024415 | 0.002669 | 0.00066892
10 | 0.99741 | -0.018071 | 0 | 0
11 | 0.99832 | -0.011698 | 0 | 0
12 | 0.99518 | -0.033608 | 0.0074675 | 0.0018715
13 | 0.99711 | -0.020192 | 0 | 0
14 | 1 | 0 | -0.13801 | -0.034481
15 | 0.99669 | -0.023119 | 0.0016029 | 0.00040173
16 | 0.99663 | -0.023551 | 0.0028115 | 0.00070464
17 | 0.99889 | -0.007761 | 0.0069568 | 0.0017435
18 | 0.99856 | -0.010109 | 0.006508 | 0.0016311
19 | 0.99805 | -0.01364 | 0.0065441 | 0.0016401
20 | 0.99325 | -0.047201 | 0.0078359 | 0.0019639
21 | 0.998 | -0.013995 | 0.0069567 | 0.0017435
22 | 0.99273 | -0.05085 | 0.0094968 | 0.0023801
23 | 0.9966 | -0.023785 | 0.0017678 | 0.00044306
24 | 0.99661 | -0.023696 | 0.0018472 | 0.00046294
25 | 0.9915 | -0.059516 | 0.009477 | 0.0023752
26 | 0.9885 | -0.080679 | 0.01016 | 0.0025464
27 | 0.98755 | -0.087422 | 0.012032 | 0.0030155
28 | 0.98735 | -0.088842 | 0.00592 | 0.0014837
29 | 0.99791 | -0.014614 | 0.002894 | 0.00072531
30 | 0.99629 | -0.025934 | 0 | 0
31 | 0.99626 | -0.026161 | 0.0015716 | 0.00039389
32 | 0.99633 | -0.02568 | 0.0087171 | 0.0021847
33 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0039373 | 0.00098668 | -0.0039371 | -0.00098673 | 2.1652e-07 | -4.6747e-08 | 0.0058877 | 0.0058878 | 0.0058878 | 0.99508 | -0.03446 | 0.99502 | -0.034858 | 2.1806
1 | -0.0067728 | -0.0016973 | 0.0067739 | 0.0016975 | 1.0926e-06 | 1.9844e-07 | 0.010128 | 0.010128 | 0.010128 | 0.99508 | -0.03446 | 0.99525 | -0.033295 | 3.751
2 | -0.0067739 | -0.0016975 | 0.0067793 | 0.0016985 | 5.4196e-06 | 9.8317e-07 | 0.010128 | 0.010127 | 0.010128 | 0.99525 | -0.033295 | 0.99607 | -0.027515 | 3.751
3 | -0.0086781 | -0.0021744 | 0.008679 | 0.0021746 | 9.6105e-07 | 2.5034e-07 | 0.012964 | 0.012964 | 0.012964 | 0.99607 | -0.027515 | 0.99618 | -0.026715 | 4.8014
4 | -0.0093629 | -0.002346 | 0.0093639 | 0.0023463 | 1.0116e-06 | 2.8117e-07 | 0.013985 | 0.013985 | 0.013985 | 0.99618 | -0.026715 | 0.99629 | -0.025934 | 5.1798
5 | -0.002666 | -0.00066816 | 0.002666 | 0.00066813 | 3.3727e-08 | -3.1451e-08 | 0.0039812 | 0.0039811 | 0.0039812 | 0.99645 | -0.024841 | 0.99646 | -0.02475 | 1.4745
6 | -0.0055101 | -0.0013809 | 0.0055109 | 0.001381 | 7.7477e-07 | 5.9058e-08 | 0.0082283 | 0.0082282 | 0.0082283 | 0.99646 | -0.02475 | 0.99661 | -0.023734 | 3.0475
7 | -0.010284 | -0.002577 | 0.010286 | 0.0025775 | 1.734e-06 | 5.1332e-07 | 0.015355 | 0.015355 | 0.015355 | 0.99661 | -0.023734 | 0.99678 | -0.022516 | 5.687
8 | 0.0026693 | 0.00066868 | -0.002669 | -0.00066892 | 2.5145e-07 | -2.3384e-07 | 0.0039853 | 0.0039854 | 0.0039854 | 0.99661 | -0.023734 | 0.99651 | -0.024415 | 1.4761
9 | -0.016509 | -0.0041372 | 0.016519 | 0.0041408 | 1.0161e-05 | 3.5585e-06 | 0.024645 | 0.024645 | 0.024645 | 0.99678 | -0.022516 | 0.99741 | -0.018071 | 9.1278
10 | -0.016519 | -0.0041408 | 0.016534 | 0.0041459 | 1.4592e-05 | 5.1094e-06 | 0.024645 | 0.024645 | 0.024645 | 0.99741 | -0.018071 | 0.99832 | -0.011698 | 9.1278
11 | 0.062855 | 0.015812 | -0.062664 | -0.015739 | 0.0001915 | 7.3199e-05 | 0.093708 | 0.093708 | 0.093708 | 0.99832 | -0.011698 | 0.99518 | -0.033608 | 34.7066
12 | 0.027734 | 0.0069554 | -0.027701 | -0.0069432 | 3.2619e-05 | 1.2146e-05 | 0.041339 | 0.04134 | 0.04134 | 0.99832 | -0.011698 | 0.99711 | -0.020192 | 15.311
13 | -0.10712 | -0.026914 | 0.1073 | 0.02698 | 0.00017462 | 6.6586e-05 | 0.15969 | 0.15969 | 0.15969 | 0.99832 | -0.011698 | 1 | 0 | 29.5726
14 | 0.055196 | 0.013868 | -0.055092 | -0.013828 | 0.00010418 | 3.9752e-05 | 0.082542 | 0.082542 | 0.082542 | 0.99518 | -0.033608 | 0.99325 | -0.047201 | 30.5712
15 | 0.012096 | 0.003032 | -0.012091 | -0.0030304 | 4.9009e-06 | 1.5707e-06 | 0.018051 | 0.018051 | 0.018051 | 0.99711 | -0.020192 | 0.99669 | -0.023119 | 6.6857
16 | 0.015605 | 0.0039112 | -0.015598 | -0.0039087 | 7.2548e-06 | 2.5108e-06 | 0.023288 | 0.023288 | 0.023288 | 0.99711 | -0.020192 | 0.99663 | -0.023551 | 8.6253
17 | 0.029908 | 0.007501 | -0.029876 | -0.007489 | 3.2146e-05 | 1.2023e-05 | 0.044505 | 0.044506 | 0.044506 | 1 | 0 | 0.99889 | -0.007761 | 16.4835
18 | 0.010488 | 0.0026287 | -0.010487 | -0.0026284 | 9.6726e-07 | 2.8964e-07 | 0.015658 | 0.015658 | 0.015658 | 0.99669 | -0.023119 | 0.9966 | -0.023785 | 5.7994
19 | 0.012786 | 0.0032041 | -0.012786 | -0.003204 | 2.5626e-07 | 8.3877e-08 | 0.019091 | 0.019091 | 0.019091 | 0.99663 | -0.023551 | 0.99661 | -0.023696 | 7.0706
20 | 0.022919 | 0.0057455 | -0.022912 | -0.0057427 | 7.4515e-06 | 2.7319e-06 | 0.034142 | 0.034142 | 0.034142 | 0.99889 | -0.007761 | 0.99856 | -0.010109 | 12.6453
21 | 0.016404 | 0.0041117 | -0.016396 | -0.0041089 | 8.0162e-06 | 2.8021e-06 | 0.024444 | 0.024444 | 0.024444 | 0.99856 | -0.010109 | 0.99805 | -0.01364 | 9.0535
22 | 0.0098514 | 0.0024688 | -0.0098509 | -0.0024686 | 4.8428e-07 | 1.3925e-07 | 0.014688 | 0.014688 | 0.014688 | 0.99805 | -0.01364 | 0.998 | -0.013995 | 5.4399
23 | 0.047256 | 0.011864 | -0.047232 | -0.011855 | 2.3944e-05 | 9.1103e-06 | 0.070803 | 0.070803 | 0.070803 | 0.99325 | -0.047201 | 0.99273 | -0.05085 | 26.2234
24 | 0.0028943 | 0.00072512 | -0.002894 | -0.00072531 | 2.4792e-07 | -1.8342e-07 | 0.0043152 | 0.0043153 | 0.0043153 | 0.998 | -0.013995 | 0.99791 | -0.014614 | 1.5983
25 | 0.037735 | 0.0094749 | -0.03769 | -0.0094577 | 4.538e-05 | 1.716e-05 | 0.056568 | 0.056568 | 0.056568 | 0.99273 | -0.05085 | 0.9915 | -0.059516 | 20.9513
26 | 0.0087194 | 0.0021853 | -0.0087171 | -0.0021847 | 2.2876e-06 | 5.9808e-07 | 0.013019 | 0.013019 | 0.013019 | 0.9966 | -0.023785 | 0.99633 | -0.02568 | 4.8219
27 | 0.010939 | 0.0027411 | -0.010936 | -0.00274 | 3.3878e-06 | 1.0379e-06 | 0.016333 | 0.016333 | 0.016333 | 0.99661 | -0.023696 | 0.99629 | -0.025934 | 6.0491
28 | 0.028213 | 0.0070826 | -0.02813 | -0.0070517 | 8.2695e-05 | 3.0855e-05 | 0.042345 | 0.042346 | 0.042346 | 0.9915 | -0.059516 | 0.9885 | -0.080679 | 15.6836
29 | 0.01797 | 0.0045053 | -0.017953 | -0.0044993 | 1.6771e-05 | 5.9801e-06 | 0.027051 | 0.027051 | 0.027051 | 0.9885 | -0.080679 | 0.98755 | -0.087422 | 10.019
30 | 0.0059211 | 0.0014838 | -0.00592 | -0.0014837 | 1.1641e-06 | 1.4793e-07 | 0.0089218 | 0.0089219 | 0.0089219 | 0.98755 | -0.087422 | 0.98735 | -0.088842 | 3.3044
31 | 0.0015717 | 0.00039372 | -0.0015716 | -0.00039389 | 4.9285e-08 | -1.677e-07 | 0.0023473 | 0.0023474 | 0.0023474 | 0.99629 | -0.025934 | 0.99626 | -0.026161 | 0.86941

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.14087 | 0.035199

## res_load
| p_mw | q_mvar
0 | 0.0028355 | 0.00071064
1 | 0.0039371 | 0.00098673
2 | 0.0018987 | 0.00047587
3 | 0.00068391 | 0.0001714
4 | 0.002666 | 0.00066816
5 | 0.0028441 | 0.0007128
6 | 0.0021039 | 0.00052729
7 | 0.0062234 | 0.0015597
8 | 0.002669 | 0.00066892
9 | 0.0074675 | 0.0018715
10 | 0.002862 | 0.00071728
11 | 0.0016029 | 0.00040173
12 | 0.0028115 | 0.00070464
13 | 0.0069568 | 0.0017435
14 | 0.006508 | 0.0016311
15 | 0.0065441 | 0.0016401
16 | 0.0078359 | 0.0019639
17 | 0.0069567 | 0.0017435
18 | 0.0094968 | 0.0023801
19 | 0.0017678 | 0.00044306
20 | 0.0018472 | 0.00046294
21 | 0.009477 | 0.0023752
22 | 0.01016 | 0.0025464
23 | 0.012032 | 0.0030155
24 | 0.00592 | 0.0014837
25 | 0.002894 | 0.00072531
26 | 0.0015716 | 0.00039389
27 | 0.0087171 | 0.0021847

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1