## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1151-4_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1151-4_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1151-4_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1151-4_0_2_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_1151-4_0_2_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_1151-4_0_2_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_1151-4_0_2_node_9 | 0.4 | n |  | TRUE
7 | bus_LV_1151-4_0_2_node_8 | 0.4 | n |  | TRUE
8 | bus_LV_1151-4_0_2_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_1151-4_0_2_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_1151-4_0_2_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_1151-4_0_2_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_1151-4_0_2_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_1151-4_0_2_node_11 | 0.4 | n |  | TRUE
14 | bus_LV_1151-4_0_2_node_14 | 0.4 | n |  | TRUE
15 | bus_LV_1151-4_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1151-4_0_2_node_22 | 0.4 | n |  | TRUE
17 | bus_LV_1151-4_0_2_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1151-4_0_2_node_34 | 0.4 | n |  | TRUE
19 | bus_LV_1151-4_0_2_node_27 | 0.4 | n |  | TRUE
20 | bus_LV_1151-4_0_2_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1151-4_0_2_node_29 | 0.4 | n |  | TRUE
22 | bus_LV_1151-4_0_2_node_26 | 0.4 | n |  | TRUE
23 | bus_LV_1151-4_0_2_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_1151-4_0_2_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_1151-4_0_2_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1151-4_0_2_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1151-4_0_2_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1151-4_0_2_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1151-4_0_2_node_28 | 0.4 | n |  | TRUE
30 | bus_LV_1151-4_0_2_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_1151-4_0_2_node_30 | 0.4 | n |  | TRUE
32 | bus_MV_128_0_node_281 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1151-4_0_2_load_0 | 0 | 0.02576 | 0.0064562 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1151-4_0_2_load_1 | 1 | 0.023074 | 0.0057829 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1151-4_0_2_load_4 | 3 | 0.020149 | 0.0050499 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1151-4_0_2_load_5 | 4 | 0.025398 | 0.0063653 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1151-4_0_2_load_7 | 5 | 0.0081405 | 0.0020402 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1151-4_0_2_load_8 | 7 | 0.016904 | 0.0042365 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1151-4_0_2_load_15 | 9 | 0.0012991 | 0.00032559 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1151-4_0_2_load_16 | 10 | 0.001329 | 0.00033308 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1151-4_0_2_load_12 | 15 | 0.030292 | 0.007592 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1151-4_0_2_load_22 | 16 | 0.0010228 | 0.00025633 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1151-4_0_2_load_19 | 17 | 0.0012173 | 0.00030508 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1151-4_0_2_load_34 | 18 | 0.017824 | 0.0044671 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1151-4_0_2_load_27 | 19 | 0.0025478 | 0.00063853 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1151-4_0_2_load_20 | 20 | 0.0015699 | 0.00039347 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1151-4_0_2_load_29 | 21 | 0.00035828 | 8.9792e-05 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1151-4_0_2_load_26 | 22 | 0.0081773 | 0.0020494 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1151-4_0_2_load_33 | 23 | 0.0050992 | 0.001278 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1151-4_0_2_load_25 | 24 | 0.0014291 | 0.00035816 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1151-4_0_2_load_23 | 25 | 0.0012535 | 0.00031415 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1151-4_0_2_load_24 | 27 | 0.0016584 | 0.00041564 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1151-4_0_2_load_28 | 29 | 0.0073693 | 0.0018469 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1151-4_0_2_load_32 | 30 | 0.0011546 | 0.00028937 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1151-4_0_2_load_30 | 31 | 0.0037972 | 0.00095166 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1151-4_0_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.021285 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1151-4_0_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.022988 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1151-4_0_2_line_2 | NAYY 4x150 SE | 2 | 3 | 0.0057851 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
3 | LV_1151-4_0_2_line_3 | NAYY 4x150 SE | 2 | 4 | 0.016153 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1151-4_0_2_line_4 | NAYY 4x150 SE | 3 | 5 | 0.034584 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
5 | LV_1151-4_0_2_line_5 | NAYY 4x150 SE | 4 | 6 | 0.029847 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1151-4_0_2_line_6 | NAYY 4x150 SE | 5 | 7 | 0.045264 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
7 | LV_1151-4_0_2_line_7 | NAYY 4x150 SE | 6 | 8 | 0.00632 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1151-4_0_2_line_8 | NAYY 4x150 SE | 7 | 13 | 0.020708 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
9 | LV_1151-4_0_2_line_9 | NAYY 4x150 SE | 8 | 15 | 0.06981 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1151-4_0_2_line_10 | NAYY 4x150 SE | 9 | 10 | 0.0042741 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1151-4_0_2_line_11 | NAYY 4x150 SE | 9 | 11 | 0.020235 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1151-4_0_2_line_12 | NAYY 4x150 SE | 11 | 12 | 0.1062 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1151-4_0_2_line_13 | NAYY 4x150 SE | 12 | 21 | 0.1093 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1151-4_0_2_line_14 | NAYY 4x150 SE | 12 | 22 | 0.047118 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1151-4_0_2_line_15 | NAYY 4x150 SE | 13 | 14 | 0.063447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
16 | LV_1151-4_0_2_line_16 | NAYY 4x150 SE | 14 | 16 | 0.023026 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1151-4_0_2_line_17 | NAYY 4x150 SE | 14 | 17 | 0.0077205 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1151-4_0_2_line_18 | NAYY 4x150 SE | 14 | 18 | 0.039313 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 2 | cs | TRUE
19 | LV_1151-4_0_2_line_19 | NAYY 4x150 SE | 16 | 19 | 0.028083 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1151-4_0_2_line_20 | NAYY 4x150 SE | 17 | 20 | 0.034168 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1151-4_0_2_line_21 | NAYY 4x150 SE | 19 | 29 | 0.033251 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1151-4_0_2_line_22 | NAYY 4x150 SE | 20 | 26 | 0.043956 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1151-4_0_2_line_23 | NAYY 4x150 SE | 21 | 23 | 0.00055822 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1151-4_0_2_line_24 | NAYY 4x150 SE | 22 | 24 | 0.049201 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1151-4_0_2_line_25 | NAYY 4x150 SE | 24 | 30 | 0.069162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1151-4_0_2_line_26 | NAYY 4x150 SE | 25 | 26 | 0.0052232 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1151-4_0_2_line_27 | NAYY 4x150 SE | 26 | 27 | 0.063619 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1151-4_0_2_line_28 | NAYY 4x150 SE | 27 | 28 | 0.028791 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1151-4_0_2_line_29 | NAYY 4x150 SE | 28 | 30 | 0.064113 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1151-4_0_2_line_30 | NAYY 4x150 SE | 28 | 31 | 0.03447 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1151-4_0_2_trafo_34 | 0.25 MVA 20/0.4 kV | 32 | 18 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2641993.8858 | 1218504.5635 | 2641972.7419 | 1218502.1168
1 | 2642016.7218 | 1218507.206 | 2641993.8858 | 1218504.5635
2 | 2642016.7218 | 1218507.206 | 2642022.4686 | 1218507.8705
3 | 2642016.7218 | 1218507.206 | 2642014.929 | 1218523.2589
4 | 2642022.4686 | 1218507.8705 | 2642056.824 | 1218511.8431
5 | 2642011.4969 | 1218552.9075 | 2642012.5905 | 1218544.1989 | 2642014.929 | 1218523.2589
6 | 2642056.824 | 1218511.8431 | 2642071.5027 | 1218513.5404 | 2642072.9631 | 1218506.6355 | 2642073.8331 | 1218500.5714 | 2642083.3956 | 1218501.6617 | 2642091.0205 | 1218502.5757
7 | 2642011.4969 | 1218552.9075 | 2642014.5531 | 1218553.2403 | 2642014.2949 | 1218556.4849
8 | 2642111.5815 | 1218505.0405 | 2642091.0205 | 1218502.5757
9 | 2642014.2949 | 1218556.4849 | 2642083.3588 | 1218566.6648
10 | 2641917.7358 | 1218362.164 | 2641921.868 | 1218361.0721
11 | 2641939.4316 | 1218351.892 | 2641930.7542 | 1218358.7239 | 2641921.868 | 1218361.0721
12 | 2641939.4316 | 1218351.892 | 2641959.0721 | 1218318.6548 | 2641973.5414 | 1218300.9127 | 2641980.4572 | 1218287.7536 | 2641984.0567 | 1218273.4593 | 2641986.3552 | 1218258.5444
13 | 2641986.3552 | 1218258.5444 | 2641981.148 | 1218255.4059 | 2641977.6106 | 1218249.0217 | 2641976.3129 | 1218241.4636 | 2641978.2302 | 1218200.9197 | 2641981.4326 | 1218153.3644
14 | 2641986.3552 | 1218258.5444 | 2641991.9196 | 1218260.5292 | 2642000.5182 | 1218259.5225 | 2642010.4095 | 1218256.0234 | 2642029.7538 | 1218245.4178
15 | 2642104.9994 | 1218441.9454 | 2642111.5815 | 1218505.0405
16 | 2642104.9994 | 1218441.9454 | 2642127.5321 | 1218437.204
17 | 2642104.9994 | 1218441.9454 | 2642104.1977 | 1218434.2666
18 | 2642104.9994 | 1218441.9454 | 2642072.4595 | 1218464.0066
19 | 2642155.0135 | 1218431.4212 | 2642127.5321 | 1218437.204
20 | 2642100.6497 | 1218400.2838 | 2642104.1977 | 1218434.2666
21 | 2642185.5527 | 1218419.5902 | 2642177.7807 | 1218425.0052 | 2642171.2477 | 1218428.0052 | 2642155.0135 | 1218431.4212
22 | 2642096.0852 | 1218356.5651 | 2642100.6497 | 1218400.2838
23 | 2641981.4701 | 1218152.8074 | 2641981.4326 | 1218153.3644
24 | 2642029.7538 | 1218245.4178 | 2642033.5336 | 1218243.3455 | 2642050.3231 | 1218232.4352 | 2642063.6836 | 1218221.3117 | 2642070.4438 | 1218218.1047
25 | 2642138.7263 | 1218229.0975 | 2642070.4438 | 1218218.1047
26 | 2642096.0852 | 1218356.5651 | 2642095.667 | 1218351.3586
27 | 2642096.0852 | 1218356.5651 | 2642109.1225 | 1218344.9724 | 2642117.3407 | 1218335.4915 | 2642140.1679 | 1218310.8002
28 | 2642158.2176 | 1218288.3745 | 2642141.1951 | 1218309.6891 | 2642140.1679 | 1218310.8002
29 | 2642158.2176 | 1218288.3745 | 2642146.4398 | 1218265.6445 | 2642144.1598 | 1218258.5686 | 2642144.4641 | 1218243.4395 | 2642143.4346 | 1218235.5387 | 2642138.7263 | 1218229.0975
30 | 2642158.2176 | 1218288.3745 | 2642172.9849 | 1218280.0962 | 2642177.5141 | 1218276.0703 | 2642180.7568 | 1218269.3559 | 2642181.9414 | 1218265.5099

## bus_geodata
| x | y | coords
0 | 2641993.8858 | 1218504.5635
1 | 2641972.7419 | 1218502.1168
2 | 2642016.7218 | 1218507.206
3 | 2642022.4686 | 1218507.8705
4 | 2642014.929 | 1218523.2589
5 | 2642056.824 | 1218511.8431
6 | 2642011.4969 | 1218552.9075
7 | 2642091.0205 | 1218502.5757
8 | 2642014.2949 | 1218556.4849
9 | 2641921.868 | 1218361.0721
10 | 2641917.7358 | 1218362.164
11 | 2641939.4316 | 1218351.892
12 | 2641986.3552 | 1218258.5444
13 | 2642111.5815 | 1218505.0405
14 | 2642104.9994 | 1218441.9454
15 | 2642083.3588 | 1218566.6648
16 | 2642127.5321 | 1218437.204
17 | 2642104.1977 | 1218434.2666
18 | 2642072.4595 | 1218464.0066
19 | 2642155.0135 | 1218431.4212
20 | 2642100.6497 | 1218400.2838
21 | 2641981.4326 | 1218153.3644
22 | 2642029.7538 | 1218245.4178
23 | 2641981.4701 | 1218152.8074
24 | 2642070.4438 | 1218218.1047
25 | 2642095.667 | 1218351.3586
26 | 2642096.0852 | 1218356.5651
27 | 2642140.1679 | 1218310.8002
28 | 2642158.2176 | 1218288.3745
29 | 2642185.5527 | 1218419.5902
30 | 2642138.7263 | 1218229.0975
31 | 2642181.9414 | 1218265.5099
32 | 2641927.3513 | 1218481.0393

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97576 | -0.16986 | 0.02576 | 0.0064562
1 | 0.97505 | -0.17501 | 0.023074 | 0.0057829
2 | 0.9774 | -0.15811 | 0 | 0
3 | 0.97785 | -0.15495 | 0.020149 | 0.0050499
4 | 0.97609 | -0.16752 | 0.025398 | 0.0063653
5 | 0.981 | -0.13252 | 0.0081405 | 0.0020402
6 | 0.97476 | -0.17701 | 0 | 0
7 | 0.98539 | -0.10147 | 0.016904 | 0.0042365
8 | 0.97448 | -0.17902 | 0 | 0
9 | 0.9824 | -0.12342 | 0.0012991 | 0.00032559
10 | 0.98239 | -0.12348 | 0.001329 | 0.00033308
11 | 0.98248 | -0.12287 | 0 | 0
12 | 0.98288 | -0.11998 | 0 | 0
13 | 0.98765 | -0.085574 | 0 | 0
14 | 0.99459 | -0.037305 | 0 | 0
15 | 0.97138 | -0.20132 | 0.030292 | 0.007592
16 | 0.99423 | -0.039849 | 0.0010228 | 0.00025633
17 | 0.99427 | -0.039518 | 0.0012173 | 0.00030508
18 | 1 | 0 | -0.19377 | -0.048878
19 | 0.99383 | -0.042663 | 0.0025478 | 0.00063853
20 | 0.99293 | -0.04891 | 0.0015699 | 0.00039347
21 | 0.98202 | -0.12615 | 0.00035828 | 8.9792e-05
22 | 0.98344 | -0.11603 | 0.0081773 | 0.0020494
23 | 0.98201 | -0.12618 | 0.0050992 | 0.001278
24 | 0.9846 | -0.10777 | 0.0014291 | 0.00035816
25 | 0.9913 | -0.060393 | 0.0012535 | 0.00031415
26 | 0.99131 | -0.060326 | 0 | 0
27 | 0.98907 | -0.076099 | 0.0016584 | 0.00041564
28 | 0.98812 | -0.082771 | 0 | 0
29 | 0.99348 | -0.045141 | 0.0073693 | 0.0018469
30 | 0.98637 | -0.095171 | 0.0011546 | 0.00028937
31 | 0.98793 | -0.084109 | 0.0037972 | 0.00095166
32 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.023091 | 0.005789 | -0.023074 | -0.0057829 | 1.6469e-05 | 6.0687e-06 | 0.035213 | 0.035214 | 0.035214 | 0.97576 | -0.16986 | 0.97505 | -0.17501 | 13.0421
1 | -0.048851 | -0.012245 | 0.048931 | 0.012276 | 7.9612e-05 | 3.0332e-05 | 0.074497 | 0.074497 | 0.074497 | 0.97576 | -0.16986 | 0.9774 | -0.15811 | 27.5917
2 | -0.10484 | -0.026314 | 0.10488 | 0.026332 | 4.5987e-05 | 1.7542e-05 | 0.15962 | 0.15962 | 0.15962 | 0.9774 | -0.15811 | 0.97785 | -0.15495 | 29.559
3 | 0.055906 | 0.014039 | -0.055832 | -0.014011 | 7.3031e-05 | 2.7887e-05 | 0.085121 | 0.085121 | 0.085121 | 0.9774 | -0.15811 | 0.97609 | -0.16752 | 31.5265
4 | -0.12503 | -0.031382 | 0.12542 | 0.031531 | 0.00039068 | 0.00014939 | 0.19028 | 0.19028 | 0.19028 | 0.97785 | -0.15495 | 0.981 | -0.13252 | 35.2372
5 | 0.030435 | 0.0076454 | -0.030395 | -0.0076304 | 4.0104e-05 | 1.5052e-05 | 0.046403 | 0.046403 | 0.046403 | 0.97609 | -0.16752 | 0.97476 | -0.17701 | 17.1864
6 | -0.13356 | -0.033571 | 0.13414 | 0.033793 | 0.00057984 | 0.00022187 | 0.20263 | 0.20263 | 0.20263 | 0.981 | -0.13252 | 0.98539 | -0.10147 | 37.5237
7 | 0.030395 | 0.0076304 | -0.030386 | -0.0076272 | 8.4918e-06 | 3.1873e-06 | 0.046403 | 0.046403 | 0.046403 | 0.97476 | -0.17701 | 0.97448 | -0.17902 | 17.1864
8 | -0.15105 | -0.03803 | 0.15138 | 0.038158 | 0.00033632 | 0.00012882 | 0.22815 | 0.22815 | 0.22815 | 0.98539 | -0.10147 | 0.98765 | -0.085574 | 42.2507
9 | 0.030386 | 0.0076272 | -0.030292 | -0.007592 | 9.3801e-05 | 3.521e-05 | 0.046403 | 0.046404 | 0.046404 | 0.97448 | -0.17902 | 0.97138 | -0.20132 | 17.1866
10 | 0.001329 | 0.00033303 | -0.001329 | -0.00033308 | 1.0808e-08 | -4.9959e-08 | 0.002013 | 0.002013 | 0.002013 | 0.9824 | -0.12342 | 0.98239 | -0.12348 | 0.74557
11 | -0.0026282 | -0.00065863 | 0.0026284 | 0.00065845 | 2.0009e-07 | -1.7927e-07 | 0.0039808 | 0.0039807 | 0.0039808 | 0.9824 | -0.12342 | 0.98248 | -0.12287 | 1.4744
12 | -0.0026284 | -0.00065845 | 0.0026294 | 0.00065751 | 1.0499e-06 | -9.4157e-07 | 0.0039807 | 0.0039802 | 0.0039807 | 0.98248 | -0.12287 | 0.98288 | -0.11998 | 1.4743
13 | 0.0054621 | 0.0013682 | -0.0054575 | -0.0013678 | 4.6638e-06 | 4.0972e-07 | 0.008269 | 0.0082695 | 0.0082695 | 0.98288 | -0.11998 | 0.98202 | -0.12615 | 3.0628
14 | -0.0080916 | -0.0020257 | 0.008096 | 0.0020268 | 4.4115e-06 | 1.0992e-06 | 0.012249 | 0.012249 | 0.012249 | 0.98288 | -0.11998 | 0.98344 | -0.11603 | 4.5368
15 | -0.15138 | -0.038158 | 0.15241 | 0.038553 | 0.0010304 | 0.00039469 | 0.22815 | 0.22815 | 0.22815 | 0.98765 | -0.085574 | 0.99459 | -0.037305 | 42.2507
16 | 0.01095 | 0.0027446 | -0.010946 | -0.0027434 | 3.8563e-06 | 1.1845e-06 | 0.016383 | 0.016383 | 0.016383 | 0.99459 | -0.037305 | 0.99423 | -0.039849 | 6.0677
17 | 0.028596 | 0.0071921 | -0.028587 | -0.0071888 | 8.8218e-06 | 3.2929e-06 | 0.042792 | 0.042792 | 0.042792 | 0.99459 | -0.037305 | 0.99427 | -0.039518 | 15.849
18 | -0.19196 | -0.04849 | 0.19297 | 0.048878 | 0.0010126 | 0.00038845 | 0.28733 | 0.28733 | 0.28733 | 0.99459 | -0.037305 | 1 | 0 | 53.2089
19 | 0.0099234 | 0.0024871 | -0.0099196 | -0.002486 | 3.8655e-06 | 1.1227e-06 | 0.014852 | 0.014852 | 0.014852 | 0.99423 | -0.039849 | 0.99383 | -0.042663 | 5.5008
20 | 0.02737 | 0.0068837 | -0.027334 | -0.0068704 | 3.5788e-05 | 1.3322e-05 | 0.04097 | 0.040971 | 0.040971 | 0.99427 | -0.039518 | 0.99293 | -0.04891 | 15.1743
21 | 0.0073718 | 0.0018475 | -0.0073693 | -0.0018469 | 2.5277e-06 | 5.415e-07 | 0.011037 | 0.011038 | 0.011038 | 0.99383 | -0.042663 | 0.99348 | -0.045141 | 4.088
22 | 0.025764 | 0.0064769 | -0.025724 | -0.0064617 | 4.0906e-05 | 1.5165e-05 | 0.038618 | 0.038618 | 0.038618 | 0.99293 | -0.04891 | 0.99131 | -0.060326 | 14.303
23 | 0.0050992 | 0.001278 | -0.0050992 | -0.001278 | 2.0795e-08 | 9.3596e-10 | 0.0077266 | 0.0077266 | 0.0077266 | 0.98202 | -0.12615 | 0.98201 | -0.12618 | 2.8617
24 | -0.016273 | -0.0040762 | 0.016292 | 0.0040828 | 1.8612e-05 | 6.5336e-06 | 0.024622 | 0.024622 | 0.024622 | 0.98344 | -0.11603 | 0.9846 | -0.10777 | 9.1193
25 | -0.017721 | -0.0044409 | 0.017752 | 0.0044519 | 3.0954e-05 | 1.1024e-05 | 0.026782 | 0.026781 | 0.026782 | 0.9846 | -0.10777 | 0.98637 | -0.095171 | 9.9191
26 | -0.0012535 | -0.00031415 | 0.0012535 | 0.00031409 | 1.1539e-08 | -6.2899e-08 | 0.0018816 | 0.0018816 | 0.0018816 | 0.9913 | -0.060393 | 0.99131 | -0.060326 | 0.69688
27 | 0.02447 | 0.0061477 | -0.024416 | -0.0061279 | 5.3576e-05 | 1.9788e-05 | 0.036736 | 0.036737 | 0.036737 | 0.99131 | -0.060326 | 0.98907 | -0.076099 | 13.6062
28 | 0.022758 | 0.0057122 | -0.022737 | -0.0057045 | 2.1065e-05 | 7.7326e-06 | 0.034242 | 0.034242 | 0.034242 | 0.98907 | -0.076099 | 0.98812 | -0.082771 | 12.6822
29 | 0.018939 | 0.004753 | -0.018907 | -0.0047413 | 3.2547e-05 | 1.1698e-05 | 0.028523 | 0.028523 | 0.028523 | 0.98812 | -0.082771 | 0.98637 | -0.095171 | 10.5641
30 | 0.0037979 | 0.00095149 | -0.0037972 | -0.00095166 | 7.0355e-07 | -1.7086e-07 | 0.0057191 | 0.0057193 | 0.0057193 | 0.98812 | -0.082771 | 0.98793 | -0.084109 | 2.1182

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | 2.5187e-16 | 8.8016e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.6429e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.2116 | 0.053345

## res_load
| p_mw | q_mvar
0 | 0.02576 | 0.0064562
1 | 0.023074 | 0.0057829
2 | 0.020149 | 0.0050499
3 | 0.025398 | 0.0063653
4 | 0.0081405 | 0.0020402
5 | 0.016904 | 0.0042365
6 | 0.0012991 | 0.00032559
7 | 0.001329 | 0.00033308
8 | 0.030292 | 0.007592
9 | 0.0010228 | 0.00025633
10 | 0.0012173 | 0.00030508
11 | 0.017824 | 0.0044671
12 | 0.0025478 | 0.00063853
13 | 0.0015699 | 0.00039347
14 | 0.00035828 | 8.9792e-05
15 | 0.0081773 | 0.0020494
16 | 0.0050992 | 0.001278
17 | 0.0014291 | 0.00035816
18 | 0.0012535 | 0.00031415
19 | 0.0016584 | 0.00041564
20 | 0.0073693 | 0.0018469
21 | 0.0011546 | 0.00028937
22 | 0.0037972 | 0.00095166

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1