## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1151-55_1_2_node_24 | 0.4 | n |  | TRUE
1 | bus_LV_1151-55_1_2_node_30 | 0.4 | n |  | TRUE
2 | bus_LV_1151-55_1_2_node_23 | 0.4 | n |  | TRUE
3 | bus_LV_1151-55_1_2_node_8 | 0.4 | n |  | TRUE
4 | bus_LV_1151-55_1_2_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_1151-55_1_2_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_1151-55_1_2_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_1151-55_1_2_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_1151-55_1_2_node_18 | 0.4 | n |  | TRUE
9 | bus_LV_1151-55_1_2_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_1151-55_1_2_node_17 | 0.4 | n |  | TRUE
11 | bus_LV_1151-55_1_2_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_1151-55_1_2_node_34 | 0.4 | n |  | TRUE
13 | bus_LV_1151-55_1_2_node_14 | 0.4 | n |  | TRUE
14 | bus_LV_1151-55_1_2_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_1151-55_1_2_node_43 | 0.4 | n |  | TRUE
16 | bus_LV_1151-55_1_2_node_25 | 0.4 | n |  | TRUE
17 | bus_LV_1151-55_1_2_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_1151-55_1_2_node_45 | 0.4 | n |  | TRUE
19 | bus_LV_1151-55_1_2_node_21 | 0.4 | n |  | TRUE
20 | bus_LV_1151-55_1_2_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_1151-55_1_2_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_1151-55_1_2_node_38 | 0.4 | n |  | TRUE
23 | bus_LV_1151-55_1_2_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_1151-55_1_2_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_1151-55_1_2_node_44 | 0.4 | n |  | TRUE
26 | bus_LV_1151-55_1_2_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_1151-55_1_2_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1151-55_1_2_node_27 | 0.4 | n |  | TRUE
29 | bus_LV_1151-55_1_2_node_29 | 0.4 | n |  | TRUE
30 | bus_LV_1151-55_1_2_node_32 | 0.4 | n |  | TRUE
31 | bus_LV_1151-55_1_2_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_1151-55_1_2_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_1151-55_1_2_node_35 | 0.4 | n |  | TRUE
34 | bus_LV_1151-55_1_2_node_37 | 0.4 | n |  | TRUE
35 | bus_LV_1151-55_1_2_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_1151-55_1_2_node_42 | 0.4 | n |  | TRUE
37 | bus_MV_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1151-55_1_2_load_30 | 1 | 0.00028166 | 7.059e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1151-55_1_2_load_23 | 2 | 0.00087405 | 0.00021906 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1151-55_1_2_load_8 | 3 | 0.00036586 | 9.1693e-05 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1151-55_1_2_load_9 | 4 | 0.00033799 | 8.4708e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1151-55_1_2_load_10 | 5 | 0.0016505 | 0.00041365 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1151-55_1_2_load_11 | 6 | 0.0030165 | 0.000756 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1151-55_1_2_load_18 | 8 | 0.00038277 | 9.5931e-05 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1151-55_1_2_load_20 | 9 | 0.00080827 | 0.00020257 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1151-55_1_2_load_17 | 10 | 0.00013957 | 3.498e-05 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1151-55_1_2_load_14 | 13 | 0.0014472 | 0.00036271 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1151-55_1_2_load_15 | 14 | 0.0033693 | 0.00084441 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1151-55_1_2_load_43 | 15 | 0.0018912 | 0.00047397 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1151-55_1_2_load_25 | 16 | 0.0010104 | 0.00025323 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1151-55_1_2_load_45 | 18 | 0.0027185 | 0.00068132 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1151-55_1_2_load_22 | 20 | 0.0013322 | 0.00033388 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1151-55_1_2_load_40 | 21 | 0.002496 | 0.00062555 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1151-55_1_2_load_38 | 22 | 0.0013804 | 0.00034597 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1151-55_1_2_load_41 | 23 | 0.0095053 | 0.0023822 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1151-55_1_2_load_36 | 24 | 0.0011077 | 0.00027762 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1151-55_1_2_load_44 | 25 | 0.0017403 | 0.00043616 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1151-55_1_2_load_26 | 27 | 0.00059211 | 0.0001484 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1151-55_1_2_load_27 | 28 | 0.0072168 | 0.0018087 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1151-55_1_2_load_32 | 30 | 0.00026791 | 6.7145e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1151-55_1_2_load_31 | 31 | 0.00010105 | 2.5324e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1151-55_1_2_load_33 | 32 | 0.000968 | 0.0002426 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1151-55_1_2_load_35 | 33 | 0.0017516 | 0.00043898 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1151-55_1_2_load_37 | 34 | 0.00024925 | 6.2468e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1151-55_1_2_load_39 | 35 | 0.0005238 | 0.00013128 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1151-55_1_2_load_42 | 36 | 0.00060286 | 0.00015109 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 8 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1151-55_1_2_line_0 | NAYY 4x150 SE | 0 | 1 | 0.046172 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
1 | LV_1151-55_1_2_line_1 | NAYY 4x150 SE | 0 | 2 | 0.16425 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
2 | LV_1151-55_1_2_line_2 | NAYY 4x150 SE | 1 | 26 | 0.06534 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
3 | LV_1151-55_1_2_line_3 | NAYY 4x150 SE | 2 | 15 | 0.07224 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
4 | LV_1151-55_1_2_line_4 | NAYY 4x150 SE | 2 | 9 | 0.034712 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
5 | LV_1151-55_1_2_line_5 | NAYY 4x150 SE | 3 | 4 | 0.044057 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
6 | LV_1151-55_1_2_line_6 | NAYY 4x150 SE | 3 | 5 | 0.0042772 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
7 | LV_1151-55_1_2_line_7 | NAYY 4x150 SE | 4 | 6 | 0.010753 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
8 | LV_1151-55_1_2_line_8 | NAYY 4x150 SE | 5 | 7 | 0.12946 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
9 | LV_1151-55_1_2_line_9 | NAYY 4x150 SE | 6 | 11 | 0.099889 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
10 | LV_1151-55_1_2_line_10 | NAYY 4x150 SE | 7 | 12 | 0.1162 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
11 | LV_1151-55_1_2_line_11 | NAYY 4x150 SE | 8 | 9 | 0.024145 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
12 | LV_1151-55_1_2_line_12 | NAYY 4x150 SE | 8 | 10 | 0.044357 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
13 | LV_1151-55_1_2_line_13 | NAYY 4x150 SE | 10 | 17 | 0.12147 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
14 | LV_1151-55_1_2_line_14 | NAYY 4x150 SE | 10 | 18 | 0.08214 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
15 | LV_1151-55_1_2_line_15 | NAYY 4x150 SE | 11 | 13 | 0.0381 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
16 | LV_1151-55_1_2_line_16 | NAYY 4x150 SE | 11 | 14 | 0.066445 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
17 | LV_1151-55_1_2_line_17 | NAYY 4x150 SE | 12 | 15 | 0.038077 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
18 | LV_1151-55_1_2_line_18 | NAYY 4x150 SE | 13 | 16 | 0.0095718 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
19 | LV_1151-55_1_2_line_19 | NAYY 4x150 SE | 15 | 25 | 0.057272 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
20 | LV_1151-55_1_2_line_20 | NAYY 4x150 SE | 17 | 19 | 0.049136 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
21 | LV_1151-55_1_2_line_21 | NAYY 4x150 SE | 17 | 20 | 0.047864 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
22 | LV_1151-55_1_2_line_22 | NAYY 4x150 SE | 19 | 21 | 0.025567 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
23 | LV_1151-55_1_2_line_23 | NAYY 4x150 SE | 20 | 22 | 0.0087236 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
24 | LV_1151-55_1_2_line_24 | NAYY 4x150 SE | 21 | 23 | 0.025554 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
25 | LV_1151-55_1_2_line_25 | NAYY 4x150 SE | 22 | 24 | 0.042595 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
26 | LV_1151-55_1_2_line_26 | NAYY 4x150 SE | 24 | 33 | 0.0095429 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
27 | LV_1151-55_1_2_line_27 | NAYY 4x150 SE | 26 | 29 | 0.026643 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
28 | LV_1151-55_1_2_line_28 | NAYY 4x150 SE | 26 | 27 | 0.030725 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
29 | LV_1151-55_1_2_line_29 | NAYY 4x150 SE | 27 | 28 | 0.021291 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
30 | LV_1151-55_1_2_line_30 | NAYY 4x150 SE | 29 | 30 | 0.027869 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
31 | LV_1151-55_1_2_line_31 | NAYY 4x150 SE | 30 | 31 | 0.01846 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
32 | LV_1151-55_1_2_line_32 | NAYY 4x150 SE | 31 | 32 | 0.011096 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
33 | LV_1151-55_1_2_line_33 | NAYY 4x150 SE | 33 | 34 | 0.026289 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
34 | LV_1151-55_1_2_line_34 | NAYY 4x150 SE | 34 | 35 | 0.0018125 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE
35 | LV_1151-55_1_2_line_35 | NAYY 4x150 SE | 35 | 36 | 0.012774 | 0.208 | 0.08 | 261 | 0 | 0.27 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1151-55_1_2_trafo_18 | 0.25 MVA 20/0.4 kV | 37 | 8 | 0.25 | 20 | 0.4 | 6 | 1.44 | 0.8 | 0.32 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2641460.1416 | 1221486.3664 | 2641441.6337 | 1221528.6672
1 | 2641460.1416 | 1221486.3664 | 2641438.4849 | 1221483.0917 | 2641393.2906 | 1221481.9325 | 2641296.4302 | 1221489.2132
2 | 2641415.4427 | 1221588.5281 | 2641441.6337 | 1221528.6672
3 | 2641296.4302 | 1221489.2132 | 2641291.6847 | 1221417.1291
4 | 2641261.8159 | 1221491.8151 | 2641296.4302 | 1221489.2132
5 | 2641201.8847 | 1221182.2364 | 2641191.4877 | 1221169.8365 | 2641184.3996 | 1221165.8629 | 2641167.2139 | 1221161.9641 | 2641165.4577 | 1221160.7642
6 | 2641204.6328 | 1221185.5139 | 2641201.8847 | 1221182.2364
7 | 2641158.0127 | 1221153.1515 | 2641162.4799 | 1221158.7295 | 2641165.4577 | 1221160.7642
8 | 2641235.3095 | 1221303.8864 | 2641240.1272 | 1221300.4955 | 2641242.7568 | 1221295.3995 | 2641242.1449 | 1221289.5474 | 2641232.9263 | 1221250.3601 | 2641224.4857 | 1221219.3054 | 2641218.4783 | 1221204.9663 | 2641213.1189 | 1221195.6348 | 2641204.6328 | 1221185.5139
9 | 2641095.5713 | 1221075.1845 | 2641158.0127 | 1221153.1515
10 | 2641235.3095 | 1221303.8864 | 2641253.3348 | 1221373.7864 | 2641253.7223 | 1221378.0694 | 2641253.8635 | 1221379.5935 | 2641253.9734 | 1221385.6312 | 2641253.8044 | 1221389.2322 | 2641253.6143 | 1221417.7702
11 | 2641261.8159 | 1221491.8151 | 2641237.7386 | 1221493.6249
12 | 2641237.7386 | 1221493.6249 | 2641213.3205 | 1221495.4603 | 2641202.586 | 1221498.8882 | 2641195.5409 | 1221503.8227
13 | 2641130.3407 | 1221605.5532 | 2641133.3726 | 1221598.1919 | 2641172.0204 | 1221538.901 | 2641183.8575 | 1221516.4137 | 2641191.6935 | 1221506.5175 | 2641195.5409 | 1221503.8227
14 | 2641195.5409 | 1221503.8227 | 2641191.6665 | 1221421.7744
15 | 2641095.5713 | 1221075.1845 | 2641081.8783 | 1221057.6019 | 2641074.8755 | 1221043.4229
16 | 2641095.5713 | 1221075.1845 | 2641032.0694 | 1221094.7393
17 | 2641253.6143 | 1221417.7702 | 2641274.5371 | 1221417.5371 | 2641291.6847 | 1221417.1291
18 | 2641074.8755 | 1221043.4229 | 2641074.8755 | 1221043.4229 | 2641072.6306 | 1221034.118
19 | 2641291.6847 | 1221417.1291 | 2641330.6195 | 1221416.2027 | 2641344.7609 | 1221417.0346 | 2641348.7974 | 1221418.0427
20 | 2641130.3407 | 1221605.5532 | 2641129.8386 | 1221612.3538 | 2641130.665 | 1221619.008 | 2641144.3647 | 1221651.8889
21 | 2641130.3407 | 1221605.5532 | 2641178.0558 | 1221601.7819
22 | 2641144.3647 | 1221651.8889 | 2641169.7322 | 1221648.7002
23 | 2641178.0558 | 1221601.7819 | 2641186.7523 | 1221601.0946
24 | 2641195.0865 | 1221645.5132 | 2641169.7322 | 1221648.7002
25 | 2641229.2144 | 1221597.7385 | 2641186.7523 | 1221601.0946
26 | 2641238.7276 | 1221596.9865 | 2641229.2144 | 1221597.7385
27 | 2641415.4427 | 1221588.5281 | 2641406.2318 | 1221609.5879 | 2641405.5393 | 1221613.1852
28 | 2641415.4427 | 1221588.5281 | 2641410.4758 | 1221588.3157 | 2641384.8758 | 1221591.1218
29 | 2641384.8758 | 1221591.1218 | 2641363.7111 | 1221593.4418
30 | 2641405.5393 | 1221613.1852 | 2641398.7066 | 1221615.1167 | 2641382.4296 | 1221628.0158
31 | 2641367.9617 | 1221639.4812 | 2641382.4296 | 1221628.0158
32 | 2641359.2655 | 1221646.3728 | 2641367.9617 | 1221639.4812
33 | 2641238.7276 | 1221596.9865 | 2641264.9348 | 1221594.9152
34 | 2641266.7417 | 1221594.7724 | 2641264.9348 | 1221594.9152
35 | 2641279.4756 | 1221593.7659 | 2641266.7417 | 1221594.7724

## bus_geodata
| x | y | coords
0 | 2641460.1416 | 1221486.3664
1 | 2641441.6337 | 1221528.6672
2 | 2641296.4302 | 1221489.2132
3 | 2641201.8847 | 1221182.2364
4 | 2641165.4577 | 1221160.7642
5 | 2641204.6328 | 1221185.5139
6 | 2641158.0127 | 1221153.1515
7 | 2641235.3095 | 1221303.8864
8 | 2641237.7386 | 1221493.6249
9 | 2641261.8159 | 1221491.8151
10 | 2641195.5409 | 1221503.8227
11 | 2641095.5713 | 1221075.1845
12 | 2641253.6143 | 1221417.7702
13 | 2641074.8755 | 1221043.4229
14 | 2641032.0694 | 1221094.7393
15 | 2641291.6847 | 1221417.1291
16 | 2641072.6306 | 1221034.118
17 | 2641130.3407 | 1221605.5532
18 | 2641191.6665 | 1221421.7744
19 | 2641144.3647 | 1221651.8889
20 | 2641178.0558 | 1221601.7819
21 | 2641169.7322 | 1221648.7002
22 | 2641186.7523 | 1221601.0946
23 | 2641195.0865 | 1221645.5132
24 | 2641229.2144 | 1221597.7384
25 | 2641348.7974 | 1221418.0427
26 | 2641415.4427 | 1221588.5281
27 | 2641384.8758 | 1221591.1218
28 | 2641363.7111 | 1221593.4418
29 | 2641405.5393 | 1221613.1852
30 | 2641382.4296 | 1221628.0158
31 | 2641367.9617 | 1221639.4812
32 | 2641359.2655 | 1221646.3728
33 | 2641238.7276 | 1221596.9865
34 | 2641264.9348 | 1221594.9152
35 | 2641266.7417 | 1221594.7724
36 | 2641279.4756 | 1221593.7659
37 | 2641237.7386 | 1221493.6249

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99563 | -0.030661 | 0 | 0
1 | 0.995 | -0.035057 | 0.00028166 | 7.059e-05
2 | 0.99785 | -0.015053 | 0.00087405 | 0.00021906
3 | 0.99168 | -0.058475 | 0.00036586 | 9.1693e-05
4 | 0.9911 | -0.062593 | 0.00033799 | 8.4708e-05
5 | 0.99174 | -0.05806 | 0.0016505 | 0.00041365
6 | 0.99096 | -0.063562 | 0.0030165 | 0.000756
7 | 0.99382 | -0.043338 | 0 | 0
8 | 1 | 0 | -0.048838 | -0.012057
9 | 0.9991 | -0.006283 | 0.00080827 | 0.00020257
10 | 0.99861 | -0.0096878 | 0.00013957 | 3.498e-05
11 | 0.99012 | -0.069498 | 0 | 0
12 | 0.9957 | -0.030162 | 0 | 0
13 | 0.98999 | -0.070453 | 0.0014472 | 0.00036271
14 | 0.9898 | -0.07178 | 0.0033693 | 0.00084441
15 | 0.99631 | -0.025853 | 0.0018912 | 0.00047397
16 | 0.98997 | -0.070551 | 0.0010104 | 0.00025323
17 | 0.99531 | -0.032837 | 0 | 0
18 | 0.9983 | -0.011927 | 0.0027185 | 0.00068132
19 | 0.99447 | -0.038786 | 0 | 0
20 | 0.99484 | -0.036194 | 0.0013322 | 0.00033388
21 | 0.99403 | -0.041885 | 0.002496 | 0.00062555
22 | 0.99477 | -0.036689 | 0.0013804 | 0.00034597
23 | 0.99368 | -0.04434 | 0.0095053 | 0.0023822
24 | 0.99451 | -0.038512 | 0.0011077 | 0.00027762
25 | 0.99617 | -0.026857 | 0.0017403 | 0.00043616
26 | 0.99415 | -0.041097 | 0 | 0
27 | 0.9938 | -0.043522 | 0.00059211 | 0.0001484
28 | 0.99358 | -0.045075 | 0.0072168 | 0.0018087
29 | 0.9941 | -0.041458 | 0 | 0
30 | 0.99404 | -0.041836 | 0.00026791 | 6.7145e-05
31 | 0.99401 | -0.042035 | 0.00010105 | 2.5324e-05
32 | 0.994 | -0.042144 | 0.000968 | 0.0002426
33 | 0.99447 | -0.038814 | 0.0017516 | 0.00043898
34 | 0.99441 | -0.03918 | 0.00024925 | 6.2468e-05
35 | 0.99441 | -0.0392 | 0.0005238 | 0.00013128
36 | 0.9944 | -0.039278 | 0.00060286 | 0.00015109
37 | 0.99998 | 149.9947 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0094453 | 0.0023664 | -0.0094395 | -0.0023648 | 5.7412e-06 | 1.6081e-06 | 0.014116 | 0.014116 | 0.014116 | 0.99563 | -0.030661 | 0.995 | -0.035057 | 5.2283
1 | -0.0094453 | -0.0023664 | 0.0094657 | 0.0023721 | 2.0421e-05 | 5.7136e-06 | 0.014116 | 0.014115 | 0.014116 | 0.99563 | -0.030661 | 0.99785 | -0.015053 | 5.2282
2 | 0.0091579 | 0.0022942 | -0.0091502 | -0.0022921 | 7.6472e-06 | 2.0933e-06 | 0.013695 | 0.013695 | 0.013695 | 0.995 | -0.035057 | 0.99415 | -0.041097 | 5.0724
3 | 0.014915 | 0.0037406 | -0.014893 | -0.003733 | 2.2301e-05 | 7.6352e-06 | 0.022242 | 0.022243 | 0.022243 | 0.99785 | -0.015053 | 0.99631 | -0.025853 | 8.238
4 | -0.025255 | -0.0063318 | 0.025285 | 0.0063431 | 3.0722e-05 | 1.1362e-05 | 0.037661 | 0.037661 | 0.037661 | 0.99785 | -0.015053 | 0.9991 | -0.006283 | 13.9486
5 | 0.0091939 | 0.0023024 | -0.0091887 | -0.002301 | 5.2317e-06 | 1.4441e-06 | 0.013795 | 0.013795 | 0.013795 | 0.99168 | -0.058475 | 0.9911 | -0.062593 | 5.1093
6 | -0.0095598 | -0.0023941 | 0.0095603 | 0.0023943 | 5.4913e-07 | 1.5602e-07 | 0.014344 | 0.014344 | 0.014344 | 0.99168 | -0.058475 | 0.99174 | -0.05806 | 5.3125
7 | 0.0088507 | 0.0022163 | -0.0088495 | -0.002216 | 1.1847e-06 | 3.171e-07 | 0.013288 | 0.013288 | 0.013288 | 0.9911 | -0.062593 | 0.99096 | -0.063562 | 4.9214
8 | -0.011211 | -0.0028079 | 0.011234 | 0.002815 | 2.2855e-05 | 7.1163e-06 | 0.01682 | 0.01682 | 0.01682 | 0.99174 | -0.05806 | 0.99382 | -0.043338 | 6.2297
9 | 0.005833 | 0.00146 | -0.0058283 | -0.0014594 | 4.7813e-06 | 5.5318e-07 | 0.0087582 | 0.0087586 | 0.0087586 | 0.99096 | -0.063562 | 0.99012 | -0.069498 | 3.2439
10 | -0.011234 | -0.002815 | 0.011254 | 0.0028214 | 2.0512e-05 | 6.3807e-06 | 0.01682 | 0.016819 | 0.01682 | 0.99382 | -0.043338 | 0.9957 | -0.030162 | 6.2295
11 | 0.026116 | 0.0065541 | -0.026094 | -0.0065457 | 2.2758e-05 | 8.4364e-06 | 0.038865 | 0.038865 | 0.038865 | 1 | 0 | 0.9991 | -0.006283 | 14.3944
12 | 0.021922 | 0.0055029 | -0.021892 | -0.0054922 | 2.9457e-05 | 1.0749e-05 | 0.032623 | 0.032623 | 0.032623 | 1 | 0 | 0.99861 | -0.0096878 | 12.0826
13 | 0.019033 | 0.0047766 | -0.018972 | -0.0047548 | 6.0978e-05 | 2.1869e-05 | 0.028363 | 0.028364 | 0.028364 | 0.99861 | -0.0096878 | 0.99531 | -0.032837 | 10.5052
14 | 0.0027193 | 0.00068057 | -0.0027185 | -0.00068132 | 8.4149e-07 | -7.5064e-07 | 0.0040517 | 0.0040521 | 0.0040521 | 0.99861 | -0.0096878 | 0.9983 | -0.011927 | 1.5008
15 | 0.002458 | 0.00061545 | -0.0024576 | -0.00061582 | 3.2439e-07 | -3.6518e-07 | 0.0036938 | 0.0036939 | 0.0036939 | 0.99012 | -0.069498 | 0.98999 | -0.070453 | 1.3681
16 | 0.0033703 | 0.00084397 | -0.0033693 | -0.00084441 | 1.0637e-06 | -4.4519e-07 | 0.0050649 | 0.0050652 | 0.0050652 | 0.99012 | -0.069498 | 0.9898 | -0.07178 | 1.876
17 | -0.011254 | -0.0028214 | 0.011261 | 0.0028235 | 6.7211e-06 | 2.0895e-06 | 0.016819 | 0.016819 | 0.016819 | 0.9957 | -0.030162 | 0.99631 | -0.025853 | 6.2293
18 | 0.0010104 | 0.00025311 | -0.0010104 | -0.00025323 | 1.3776e-08 | -1.1777e-07 | 0.0015187 | 0.0015187 | 0.0015187 | 0.98999 | -0.070453 | 0.98997 | -0.070551 | 0.56248
19 | 0.0017405 | 0.00043551 | -0.0017403 | -0.00043616 | 2.4148e-07 | -6.5285e-07 | 0.0025993 | 0.0025996 | 0.0025996 | 0.99631 | -0.025853 | 0.99617 | -0.026857 | 0.9628
20 | 0.01202 | 0.0030135 | -0.01201 | -0.0030104 | 9.9011e-06 | 3.17e-06 | 0.01797 | 0.01797 | 0.01797 | 0.99531 | -0.032837 | 0.99447 | -0.038786 | 6.6556
21 | 0.0069527 | 0.0017412 | -0.0069495 | -0.0017406 | 3.2268e-06 | 6.193e-07 | 0.010394 | 0.010394 | 0.010394 | 0.99531 | -0.032837 | 0.99484 | -0.036194 | 3.8497
22 | 0.01201 | 0.0030104 | -0.012005 | -0.0030087 | 5.152e-06 | 1.6499e-06 | 0.01797 | 0.01797 | 0.01797 | 0.99447 | -0.038786 | 0.99403 | -0.041885 | 6.6556
23 | 0.0056173 | 0.0014067 | -0.0056169 | -0.0014067 | 3.8424e-07 | 3.4526e-08 | 0.0084016 | 0.0084017 | 0.0084017 | 0.99484 | -0.036194 | 0.99477 | -0.036689 | 3.1117
24 | 0.0095085 | 0.0023832 | -0.0095053 | -0.0023822 | 3.2306e-06 | 9.1142e-07 | 0.014234 | 0.014234 | 0.014234 | 0.99403 | -0.041885 | 0.99368 | -0.04434 | 5.2718
25 | 0.0042365 | 0.0010607 | -0.0042354 | -0.0010609 | 1.0673e-06 | -1.4234e-07 | 0.0063367 | 0.0063369 | 0.0063369 | 0.99477 | -0.036689 | 0.99451 | -0.038512 | 2.347
26 | 0.0031277 | 0.00078324 | -0.0031275 | -0.00078332 | 1.304e-07 | -7.3666e-08 | 0.0046795 | 0.0046796 | 0.0046796 | 0.99451 | -0.038512 | 0.99447 | -0.038814 | 1.7332
27 | 0.0013371 | 0.00033405 | -0.0013371 | -0.00033437 | 6.6572e-08 | -3.1983e-07 | 0.002001 | 0.0020011 | 0.0020011 | 0.99415 | -0.041097 | 0.9941 | -0.041458 | 0.74116
28 | 0.0078131 | 0.001958 | -0.0078105 | -0.0019574 | 2.622e-06 | 6.1022e-07 | 0.011694 | 0.011695 | 0.011695 | 0.99415 | -0.041097 | 0.9938 | -0.043522 | 4.3313
29 | 0.0072183 | 0.001809 | -0.0072168 | -0.0018087 | 1.552e-06 | 3.2109e-07 | 0.010808 | 0.010808 | 0.010808 | 0.9938 | -0.043522 | 0.99358 | -0.045075 | 4.003
30 | 0.0013371 | 0.00033437 | -0.001337 | -0.00033471 | 6.9644e-08 | -3.3451e-07 | 0.0020011 | 0.0020013 | 0.0020013 | 0.9941 | -0.041458 | 0.99404 | -0.041836 | 0.74121
31 | 0.0010691 | 0.00026756 | -0.0010691 | -0.00026779 | 2.9498e-08 | -2.2795e-07 | 0.0016002 | 0.0016003 | 0.0016003 | 0.99404 | -0.041836 | 0.99401 | -0.042035 | 0.5927
32 | 0.00096801 | 0.00024246 | -0.000968 | -0.0002426 | 1.4539e-08 | -1.3824e-07 | 0.001449 | 0.0014491 | 0.0014491 | 0.99401 | -0.042035 | 0.994 | -0.042144 | 0.5367
33 | 0.001376 | 0.00034434 | -0.0013759 | -0.00034465 | 6.953e-08 | -3.1432e-07 | 0.0020587 | 0.0020588 | 0.0020588 | 0.99447 | -0.038814 | 0.99441 | -0.03918 | 0.76253
34 | 0.0011267 | 0.00028218 | -0.0011267 | -0.0002822 | 3.2145e-09 | -2.2277e-08 | 0.0016859 | 0.0016859 | 0.0016859 | 0.99441 | -0.03918 | 0.99441 | -0.0392 | 0.62439
35 | 0.00060286 | 0.00015093 | -0.00060286 | -0.00015109 | 6.4862e-09 | -1.6322e-07 | 0.00090205 | 0.00090211 | 0.00090211 | 0.99441 | -0.0392 | 0.9944 | -0.039278 | 0.33412

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -4.4415e-16 | -7.6913e-16 | 0.00079998 | 7.4552e-08 | 0.00079998 | 7.4552e-08 | 2.564e-17 | 0.0011547 | 0.99998 | 149.9947 | 1 | 0 | 0.31999

## res_ext_grid
| p_mw | q_mvar
0 | 0.049221 | 0.012153

## res_load
| p_mw | q_mvar
0 | 0.00028166 | 7.059e-05
1 | 0.00087405 | 0.00021906
2 | 0.00036586 | 9.1693e-05
3 | 0.00033799 | 8.4708e-05
4 | 0.0016505 | 0.00041365
5 | 0.0030165 | 0.000756
6 | 0.00038277 | 9.5931e-05
7 | 0.00080827 | 0.00020257
8 | 0.00013957 | 3.498e-05
9 | 0.0014472 | 0.00036271
10 | 0.0033693 | 0.00084441
11 | 0.0018912 | 0.00047397
12 | 0.0010104 | 0.00025323
13 | 0.0027185 | 0.00068132
14 | 0.0013322 | 0.00033388
15 | 0.002496 | 0.00062555
16 | 0.0013804 | 0.00034597
17 | 0.0095053 | 0.0023822
18 | 0.0011077 | 0.00027762
19 | 0.0017403 | 0.00043616
20 | 0.00059211 | 0.0001484
21 | 0.0072168 | 0.0018087
22 | 0.00026791 | 6.7145e-05
23 | 0.00010105 | 2.5324e-05
24 | 0.000968 | 0.0002426
25 | 0.0017516 | 0.00043898
26 | 0.00024925 | 6.2468e-05
27 | 0.0005238 | 0.00013128
28 | 0.00060286 | 0.00015109

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1